## Download Transaksi
Experimental Data of Practice 1: Introduction of Reactor Operation
No | Time | Power NP1000 [kW] | Power NLW2 [kW] | Safety Rod [%] | Compensation Rod [%] | Regulator Rod [%] | Reactor Tank Temp. [°C] | Reactor Tank Level [cm] | Reactor pH [-] | Fuel Element Temp. [°C] | Primary Inlet HE Tube Temp. [°C] | Primary Inlet HE Plat Temp. [°C] | Primary Outlet Temp. [°C] | Primary Flowrate [lpm] | Secondary Inlet HE Tube Temp. [°C] | Secondary Outlet HE Tube Temp. [°C] | Secondary HE Tube Flowrate [lpm] | Secondary Inlet HE Plat Temp. [°C] | Secondary Outlet HE Plat Temp. [°C] | Secondary HE Plat Flowrate [lpm] | Reactor Deck Area [MicroSv/h] | SubCritic Area [MicroSv/h] | Demineralizer Area [MicroSv/h] | Column Thermal Area [MicroSv/h] | Bulkshielding Area [MicroSv/h] | Main Control Room Area [MicroSv/h]
1 | 30/07/2025 09:18:20.677 | 0 | 0.00032 | 100 | 0 | 0 | 27.35 | 9.549 | 7.063 | 27.045 | 28.318 | 28.046 | 27.344 | 605.417 | 25.636 | 26.345 | 1296.588 | 26.951 | 27.161 | 38.374 | 0 | 0.6 | 0.6 | 0 | 0 | 0.1
2 | 30/07/2025 09:18:22.311 | 0 | 0.00031 | 100 | 0 | 1 | 29.697 | 9.5 | 7.064 | 27.498 | 28.301 | 28.026 | 27.36 | 605.41 | 25.621 | 26.373 | 1310.259 | 26.936 | 27.143 | 38.238 | 0 | 0 | 1.5 | 0.6 | 0 | 0.1
3 | 30/07/2025 09:18:23.949 | 0 | 0.00033 | 100 | 3 | 0 | 28.533 | 9.736 | 7.07 | 27.083 | 28.308 | 28.045 | 27.383 | 605.653 | 25.625 | 26.338 | 1318.807 | 26.912 | 27.135 | 38.539 | 0 | 0 | 1.5 | 0.6 | 0 | 0.1
4 | 30/07/2025 09:18:25.583 | 0 | 0.00031 | 100 | 5 | 0 | 25.763 | 9.713 | 7.065 | 27.188 | 28.285 | 28.04 | 27.352 | 605.383 | 25.632 | 26.331 | 1313.109 | 26.933 | 27.181 | 38.383 | 0 | 0 | 0.6 | 0.6 | 0 | 0.1
5 | 30/07/2025 09:18:27.221 | 0 | 0.00032 | 100 | 8 | 0 | 28.848 | 9.589 | 7.062 | 27.237 | 28.308 | 28.055 | 27.353 | 605.361 | 25.646 | 26.345 | 1309.056 | 26.923 | 27.158 | 38.377 | 0 | 0 | 1.5 | 0 | 0 | 0.2
6 | 30/07/2025 09:18:28.859 | 0 | 0.00041 | 100 | 10 | 1 | 25.772 | 9.69 | 7.066 | 27.193 | 28.295 | 28.037 | 27.338 | 605.246 | 25.637 | 26.345 | 1308.932 | 26.958 | 27.169 | 38.372 | 0 | 0 | 1.3 | 0 | 0 | 0.2
7 | 30/07/2025 09:18:30.493 | 0 | 0.00037 | 100 | 9 | 0 | 28.017 | 9.569 | 7.071 | 27.108 | 28.312 | 28.027 | 27.376 | 605.573 | 25.669 | 26.34 | 1311.302 | 26.919 | 27.133 | 38.138 | 0 | 0.7 | 0.9 | 0.6 | 0.8 | 0.2
8 | 30/07/2025 09:18:32.128 | 0 | 0.00042 | 100 | 10 | 0 | 29.803 | 9.557 | 7.074 | 26.986 | 28.29 | 28.049 | 27.357 | 605.475 | 25.635 | 26.352 | 1312.926 | 26.905 | 27.157 | 38.381 | 0 | 0.7 | 0.9 | 0.6 | 0.8 | 0.2
9 | 30/07/2025 09:18:33.761 | 0 | 0.0004 | 100 | 10 | 0 | 27.846 | 9.57 | 7.075 | 27.522 | 28.3 | 28.037 | 27.361 | 605.415 | 25.643 | 26.366 | 1318.759 | 26.919 | 27.166 | 38.584 | 0 | 0.7 | 0.7 | 0.6 | 0.8 | 0.2
10 | 30/07/2025 09:18:35.396 | 0 | 0.0004 | 100 | 13 | 0 | 25.913 | 9.764 | 7.073 | 27.314 | 28.285 | 28.054 | 27.348 | 605.435 | 25.659 | 26.365 | 1314.073 | 26.932 | 27.168 | 38.342 | 0 | 0 | 0.6 | 0.6 | 0 | 0.2
11 | 30/07/2025 09:18:37.033 | 0 | 0.00039 | 100 | 15 | 0 | 29.389 | 9.803 | 7.074 | 27.219 | 28.282 | 28.023 | 27.356 | 604.185 | 25.647 | 26.372 | 1310.962 | 26.954 | 27.155 | 38.154 | 0 | 0 | 1.4 | 0.6 | 0 | 0.2
12 | 30/07/2025 09:18:38.668 | 0 | 0.00041 | 100 | 18 | 1 | 25.764 | 9.728 | 7.071 | 27.097 | 28.278 | 28.028 | 27.384 | 604.38 | 25.634 | 26.36 | 1315.452 | 26.924 | 27.134 | 38.081 | 0 | 0 | 1.3 | 0 | 0.5 | 0.2
13 | 30/07/2025 09:18:40.302 | 0 | 0.00041 | 100 | 21 | 1 | 28.587 | 9.571 | 7.103 | 27.02 | 28.262 | 28.039 | 27.362 | 604.191 | 25.636 | 26.377 | 1322.546 | 26.92 | 27.169 | 38.647 | 0 | 0 | 1.1 | 0 | 0.5 | 0.2
14 | 30/07/2025 09:18:41.935 | 0 | 0.0004 | 100 | 24 | 1 | 29.842 | 9.571 | 7.09 | 27.378 | 28.281 | 28.042 | 27.36 | 604.242 | 25.666 | 26.369 | 1328.961 | 26.927 | 27.161 | 38.372 | 0 | 0 | 1.1 | 0 | 0.5 | 0.2
15 | 30/07/2025 09:18:43.584 | 0 | 0.00041 | 100 | 27 | 0 | 27.178 | 9.801 | 7.074 | 27.217 | 28.277 | 28.036 | 27.34 | 604.171 | 25.635 | 26.368 | 1321.587 | 26.941 | 27.166 | 38.354 | 0 | 0.6 | 1.1 | 0.6 | 0 | 0.2
16 | 30/07/2025 09:18:45.220 | 0 | 0.0004 | 100 | 30 | 0 | 26.358 | 9.799 | 7.103 | 27.227 | 28.279 | 28.023 | 27.367 | 604.299 | 25.648 | 26.383 | 1318.758 | 26.936 | 27.14 | 38.067 | 0 | 0.6 | 1 | 0.6 | 0 | 0.2
17 | 30/07/2025 09:18:46.863 | 0 | 0.00041 | 100 | 32 | 1 | 29.492 | 9.571 | 7.089 | 27.051 | 28.291 | 28.05 | 27.379 | 605.608 | 25.633 | 26.343 | 1308.513 | 26.896 | 27.168 | 38.532 | 0 | 0 | 0.2 | 0 | 0.5 | 0.2
18 | 30/07/2025 09:18:48.498 | 0 | 0.00041 | 100 | 35 | 0 | 25.751 | 9.795 | 7.075 | 27.233 | 28.294 | 28.043 | 27.356 | 605.424 | 25.647 | 26.365 | 1308.507 | 26.9 | 27.159 | 38.597 | 0 | 0 | 0.9 | 0 | 0.5 | 0.2
19 | 30/07/2025 09:18:50.134 | 0 | 0.00039 | 100 | 38 | 0 | 28.872 | 9.865 | 7.073 | 27.281 | 28.285 | 28.047 | 27.366 | 605.553 | 25.636 | 26.368 | 1304.812 | 26.947 | 27.159 | 38.251 | 0 | 0 | 0.9 | 0 | 0.5 | 0.2
20 | 30/07/2025 09:18:51.771 | 0 | 0.00041 | 100 | 41 | 0 | 29.863 | 9.723 | 7.075 | 27.164 | 28.302 | 28.034 | 27.345 | 605.281 | 25.639 | 26.369 | 1310.545 | 26.95 | 27.163 | 38.344 | 0 | 0 | 0.7 | 0 | 0 | 0.2
21 | 30/07/2025 09:18:53.413 | 0 | 0.00042 | 100 | 42 | 0 | 26.794 | 9.802 | 7.07 | 27.062 | 28.319 | 28.021 | 27.363 | 604.351 | 25.653 | 26.354 | 1310.313 | 26.922 | 27.135 | 38.338 | 0 | 0 | 0.7 | 0 | 0 | 0.2
22 | 30/07/2025 09:18:55.051 | 0 | 0.00042 | 100 | 46 | 0 | 26.903 | 9.58 | 7.066 | 27.071 | 28.305 | 28.061 | 27.361 | 604.278 | 25.628 | 26.346 | 1315.488 | 26.912 | 27.175 | 38.64 | 0 | 0.6 | 0.9 | 0 | 0 | 0.2
23 | 30/07/2025 09:18:56.686 | 0 | 0.00043 | 100 | 49 | 0 | 27.926 | 9.758 | 7.026 | 27.15 | 28.318 | 28.049 | 27.369 | 604.355 | 25.635 | 26.331 | 1319.14 | 26.916 | 27.164 | 38.46 | 0 | 0.6 | 0.7 | 0 | 0 | 0.2
24 | 30/07/2025 09:18:58.323 | 0 | 0.00042 | 100 | 52 | 0 | 26.013 | 9.799 | 7.025 | 27.122 | 28.286 | 28.066 | 27.338 | 604.148 | 25.624 | 26.339 | 1318.999 | 26.956 | 27.178 | 38.316 | 0 | 0 | 0.3 | 0 | 1.3 | 0.2
25 | 30/07/2025 09:18:59.958 | 0 | 0.00042 | 100 | 55 | 0 | 29.333 | 9.797 | 7.024 | 27.427 | 28.304 | 28.021 | 27.358 | 604.213 | 25.63 | 26.347 | 1319.171 | 26.929 | 27.152 | 38.303 | 0 | 0 | 0.3 | 0 | 1.3 | 0.2
26 | 30/07/2025 09:19:01.589 | 0 | 0.00041 | 100 | 57 | 0 | 29.726 | 9.567 | 7.022 | 27.07 | 28.309 | 28.035 | 27.368 | 604.269 | 25.628 | 26.329 | 1320.81 | 26.916 | 27.152 | 38.276 | 0 | 0 | 0.6 | 0 | 1.3 | 0.2
27 | 30/07/2025 09:19:03.224 | 0 | 0.00041 | 100 | 59 | 1 | 26.289 | 9.724 | 7.027 | 27.143 | 28.283 | 28.042 | 27.352 | 604.087 | 25.637 | 26.343 | 1321.384 | 26.922 | 27.178 | 38.458 | 0 | 0.2 | 0.9 | 0 | 0 | 0.2
28 | 30/07/2025 09:19:04.866 | 0 | 0.00039 | 100 | 61 | 1 | 29.843 | 9.799 | 7.025 | 27.293 | 28.277 | 28.045 | 27.353 | 604.212 | 25.629 | 26.344 | 1318.889 | 26.922 | 27.168 | 38.323 | 0 | 0.2 | 1 | 0 | 0 | 0.2
29 | 30/07/2025 09:19:06.500 | 0 | 0.0004 | 100 | 64 | 1 | 27.215 | 9.574 | 7.025 | 27.296 | 28.295 | 28.042 | 27.33 | 604.048 | 25.664 | 26.36 | 1313.573 | 26.965 | 27.145 | 38.429 | 0 | 0 | 1.6 | 0 | 0 | 0.2
30 | 30/07/2025 09:19:08.135 | 0 | 0.00042 | 100 | 66 | 0 | 26.359 | 9.56 | 7.073 | 27.074 | 28.324 | 28.023 | 27.381 | 604.345 | 25.65 | 26.349 | 1308.957 | 26.926 | 27.14 | 37.911 | 0 | 0 | 1.6 | 0 | 0 | 0.2
31 | 30/07/2025 09:19:09.771 | 0 | 0.00043 | 100 | 69 | 1 | 29.499 | 9.557 | 7.026 | 26.657 | 28.284 | 28.059 | 27.366 | 604.297 | 25.642 | 26.367 | 1301.401 | 26.909 | 27.161 | 38.484 | 0 | 0 | 1.3 | 0 | 0 | 0.2
32 | 30/07/2025 09:19:11.407 | 0 | 0.00039 | 100 | 69 | 0 | 29.469 | 9.799 | 7.024 | 27.455 | 28.274 | 28.038 | 27.359 | 603.107 | 25.651 | 26.371 | 1298.943 | 26.915 | 27.166 | 38.601 | 0 | 0 | 0.6 | 0.9 | 0.2 | 0.1
33 | 30/07/2025 09:19:13.041 | 0 | 0.00041 | 100 | 69 | 0 | 25.834 | 9.717 | 7.025 | 27.147 | 28.274 | 28.045 | 27.349 | 603.036 | 25.659 | 26.362 | 1298.687 | 26.934 | 27.165 | 38.287 | 0 | 0 | 0.3 | 0.9 | 0.2 | 0.1
34 | 30/07/2025 09:19:14.676 | 0 | 0.00042 | 100 | 70 | 0 | 29.822 | 9.507 | 7.025 | 27.227 | 28.277 | 28.037 | 27.333 | 602.905 | 25.648 | 26.359 | 1301.292 | 26.939 | 27.164 | 38.356 | 0 | 0 | 0.6 | 1.3 | 0 | 0.1
35 | 30/07/2025 09:19:16.311 | 0 | 0.00041 | 100 | 71 | 1 | 26.812 | 9.573 | 7.023 | 26.976 | 28.27 | 28.033 | 27.373 | 603.131 | 25.641 | 26.367 | 1298.886 | 26.929 | 27.141 | 38.03 | 0 | 0 | 0 | 1.3 | 0 | 0.1
36 | 30/07/2025 09:19:17.946 | 0 | 0.00042 | 100 | 70 | 0 | 26.809 | 9.571 | 7.026 | 26.823 | 28.263 | 28.044 | 27.365 | 604.238 | 25.647 | 26.383 | 1307.734 | 26.909 | 27.16 | 38.482 | 0 | 0 | 0 | 1.3 | 0 | 0.1
37 | 30/07/2025 09:19:19.582 | 0 | 0.00041 | 100 | 70 | 0 | 29.615 | 9.564 | 7.025 | 27.4 | 28.304 | 28.046 | 27.351 | 604.261 | 25.673 | 26.351 | 1308.907 | 26.931 | 27.164 | 38.487 | 0 | 0.6 | 0.6 | 0 | 0.5 | 0.1
38 | 30/07/2025 09:19:21.217 | 0 | 0.00039 | 100 | 70 | 3 | 28.925 | 9.577 | 7.024 | 27.102 | 28.298 | 28.055 | 27.333 | 604.1 | 25.638 | 26.362 | 1321.399 | 26.946 | 27.176 | 38.338 | 0 | 0.6 | 1.5 | 0 | 0.5 | 0.1
39 | 30/07/2025 09:19:22.852 | 0 | 0.00037 | 100 | 70 | 5 | 29.329 | 9.73 | 7.024 | 27.155 | 28.297 | 28.037 | 27.362 | 604.225 | 25.651 | 26.349 | 1320.83 | 26.93 | 27.145 | 38.261 | 0 | 0.6 | 1.2 | 0 | 1 | 0.1
40 | 30/07/2025 09:19:24.486 | 0 | 0.00039 | 100 | 71 | 7 | 29.758 | 9.729 | 7.074 | 26.983 | 28.295 | 28.047 | 27.364 | 604.226 | 25.642 | 26.358 | 1320.271 | 26.938 | 27.156 | 38.413 | 0 | 0.6 | 1.2 | 0 | 1 | 0.1
41 | 30/07/2025 09:19:26.120 | 0 | 0.00039 | 100 | 71 | 8 | 26.166 | 9.493 | 7.064 | 27.109 | 28.308 | 28.05 | 27.369 | 604.188 | 25.639 | 26.359 | 1327.837 | 26.902 | 27.163 | 38.441 | 0 | 0.6 | 1.2 | 0 | 1 | 0.1
42 | 30/07/2025 09:19:27.754 | 0 | 0.00038 | 100 | 70 | 8 | 27.364 | 9.705 | 7.063 | 27.123 | 28.303 | 28.046 | 27.372 | 604.267 | 25.628 | 26.348 | 1338.62 | 26.93 | 27.163 | 38.414 | 0 | 0 | 0.6 | 0 | 0.5 | 0.1
43 | 30/07/2025 09:19:29.388 | 0 | 0.0004 | 100 | 70 | 7 | 29.635 | 9.573 | 7.076 | 27.195 | 28.299 | 28.032 | 27.338 | 604.013 | 25.622 | 26.365 | 1338.508 | 26.955 | 27.162 | 38.202 | 0 | 0 | 1 | 0 | 0.5 | 0.1
44 | 30/07/2025 09:19:31.024 | 0 | 0.00041 | 100 | 71 | 10 | 28.537 | 9.583 | 7.061 | 27.053 | 28.317 | 28.024 | 27.364 | 604.361 | 25.626 | 26.328 | 1351.741 | 26.924 | 27.137 | 38.339 | 0 | 0 | 1.7 | 0 | 0.6 | 0.1
45 | 30/07/2025 09:19:32.661 | 0 | 0.00039 | 100 | 70 | 10 | 29.458 | 9.698 | 7.062 | 27.216 | 28.311 | 28.042 | 27.371 | 604.23 | 25.609 | 26.348 | 1350.764 | 26.919 | 27.154 | 38.388 | 0 | 0 | 0.6 | 0 | 0.6 | 0.1
46 | 30/07/2025 09:19:34.297 | 0 | 0.0004 | 100 | 70 | 12 | 29.447 | 9.798 | 7.027 | 27.246 | 28.291 | 28.053 | 27.366 | 604.339 | 25.632 | 26.34 | 1338.495 | 26.912 | 27.16 | 38.58 | 0 | 0 | 0.1 | 0 | 0.2 | 0.2
47 | 30/07/2025 09:19:35.931 | 0 | 0.00042 | 100 | 71 | 15 | 25.848 | 9.736 | 7.025 | 27.137 | 28.294 | 28.058 | 27.335 | 604.167 | 25.629 | 26.327 | 1335.665 | 26.946 | 27.195 | 38.628 | 0 | 0 | 0.1 | 0 | 0.2 | 0.2
48 | 30/07/2025 09:19:37.568 | 0 | 0.00041 | 100 | 70 | 16 | 27.891 | 9.569 | 7.023 | 27.253 | 28.301 | 28.023 | 27.358 | 604.254 | 25.634 | 26.335 | 1326.645 | 26.922 | 27.146 | 38.295 | 0 | 0 | 0.6 | 0 | 0.2 | 0.2
49 | 30/07/2025 09:19:39.206 | 0 | 0.0004 | 100 | 71 | 18 | 29.746 | 9.578 | 6.992 | 26.987 | 28.291 | 28.038 | 27.349 | 605.516 | 25.641 | 26.345 | 1332.782 | 26.919 | 27.144 | 38.272 | 0 | 0.7 | 0.9 | 0.6 | 0 | 0.2
50 | 30/07/2025 09:19:40.842 | 0 | 0.0004 | 100 | 70 | 21 | 27.83 | 9.794 | 6.991 | 26.945 | 28.294 | 28.049 | 27.358 | 605.346 | 25.643 | 26.379 | 1343.207 | 26.915 | 27.162 | 38.481 | 0 | 0.7 | 1 | 0.6 | 0 | 0.2
51 | 30/07/2025 09:19:42.477 | 0 | 0.00039 | 100 | 70 | 20 | 29.54 | 9.873 | 7.008 | 27.176 | 28.281 | 28.05 | 27.351 | 605.464 | 25.645 | 26.366 | 1343.978 | 26.921 | 27.179 | 38.426 | 0 | 0.6 | 1 | 0 | 0.1 | 0.2
52 | 30/07/2025 09:19:44.112 | 0 | 0.0004 | 100 | 70 | 21 | 28.906 | 9.523 | 7.027 | 27.296 | 28.273 | 28.043 | 27.322 | 605.234 | 25.636 | 26.384 | 1328.795 | 26.94 | 27.166 | 38.46 | 0 | 0.6 | 1 | 0 | 0.1 | 0.2
53 | 30/07/2025 09:19:45.748 | 0 | 0.00041 | 100 | 71 | 22 | 25.672 | 9.571 | 7.006 | 27.141 | 28.287 | 28.021 | 27.37 | 605.558 | 25.655 | 26.369 | 1324.466 | 26.924 | 27.147 | 38.204 | 0 | 0.6 | 1.5 | 0 | 0.1 | 0.2
54 | 30/07/2025 09:19:47.386 | 0 | 0.00042 | 99 | 70 | 23 | 28.433 | 9.571 | 7.007 | 26.779 | 28.27 | 28.058 | 27.357 | 605.376 | 25.644 | 26.366 | 1324.854 | 26.923 | 27.172 | 38.512 | 0 | 0 | 0.6 | 0 | 0 | 0.2
55 | 30/07/2025 09:19:49.021 | 0 | 0.00041 | 100 | 70 | 26 | 29.793 | 9.794 | 7.024 | 27.333 | 28.288 | 28.051 | 27.359 | 605.412 | 25.646 | 26.367 | 1311.269 | 26.901 | 27.173 | 38.746 | 0 | 0 | 0.1 | 0 | 0 | 0.2
56 | 30/07/2025 09:19:50.658 | 0 | 0.00042 | 100 | 71 | 28 | 27.347 | 9.872 | 7.036 | 27.171 | 28.254 | 28.066 | 27.338 | 605.375 | 25.637 | 26.371 | 1317.064 | 26.957 | 27.184 | 38.416 | 0 | 0 | 0.6 | 0.2 | 0.8 | 0.3
57 | 30/07/2025 09:19:52.300 | 0 | 0.00038 | 100 | 70 | 29 | 29.58 | 9.769 | 7.062 | 27.146 | 28.282 | 28.045 | 27.336 | 605.276 | 25.66 | 26.358 | 1328.648 | 26.927 | 27.155 | 38.392 | 0 | 0 | 0.3 | 0.2 | 0.8 | 0.3
58 | 30/07/2025 09:19:53.934 | 0 | 0.00043 | 100 | 70 | 31 | 28.539 | 9.688 | 7.024 | 27.246 | 28.268 | 28.026 | 27.367 | 605.404 | 25.631 | 26.352 | 1318.715 | 26.931 | 27.137 | 37.997 | 0 | 0 | 0.3 | 0.2 | 0.8 | 0.3
59 | 30/07/2025 09:19:55.568 | 0 | 0.00043 | 100 | 71 | 31 | 25.671 | 9.477 | 7.035 | 26.826 | 28.275 | 28.053 | 27.361 | 605.469 | 25.639 | 26.36 | 1318.6 | 26.896 | 27.159 | 38.448 | 0 | 0.1 | 0.9 | 0 | 0.5 | 0.3
60 | 30/07/2025 09:19:57.204 | 0 | 0.00043 | 100 | 70 | 32 | 28.883 | 9.568 | 7.064 | 27.284 | 28.317 | 28.052 | 27.37 | 605.483 | 25.644 | 26.354 | 1323.635 | 26.923 | 27.161 | 38.574 | 0 | 0.1 | 1.1 | 0 | 0.5 | 0.3
61 | 30/07/2025 09:19:58.838 | 0 | 0.00042 | 100 | 70 | 32 | 29.804 | 9.571 | 7.064 | 27.061 | 28.285 | 28.064 | 27.331 | 604.101 | 25.632 | 26.354 | 1318.858 | 26.949 | 27.178 | 38.535 | 0 | 0.3 | 0.3 | 0.7 | 0 | 0.2
62 | 30/07/2025 09:20:00.474 | 0 | 0.00041 | 100 | 71 | 33 | 27.866 | 9.573 | 7.062 | 27.241 | 28.293 | 28.04 | 27.356 | 604.28 | 25.636 | 26.349 | 1322.905 | 26.924 | 27.158 | 38.307 | 0 | 0.3 | 2 | 0.7 | 0 | 0.2
63 | 30/07/2025 09:20:02.112 | 0 | 0.00041 | 100 | 70 | 35 | 29.746 | 9.723 | 7.074 | 27.026 | 28.295 | 28.036 | 27.371 | 604.199 | 25.625 | 26.358 | 1321.014 | 26.937 | 27.153 | 38.258 | 0 | 0.3 | 2 | 0.7 | 0 | 0.2
64 | 30/07/2025 09:20:03.750 | 0 | 0.00042 | 100 | 71 | 37 | 27.88 | 9.495 | 7.063 | 26.971 | 28.312 | 28.056 | 27.358 | 604.169 | 25.646 | 26.354 | 1321.204 | 26.888 | 27.164 | 38.613 | 0 | 0 | 1.1 | 0 | 0.6 | 0.2
65 | 30/07/2025 09:20:05.388 | 0 | 0.00042 | 100 | 70 | 38 | 25.863 | 9.439 | 7.064 | 27.186 | 28.278 | 28.058 | 27.347 | 604.201 | 25.602 | 26.355 | 1308.773 | 26.938 | 27.175 | 38.402 | 0 | 0 | 0.9 | 0 | 0.6 | 0.2
66 | 30/07/2025 09:20:07.023 | 0 | 0.00041 | 100 | 70 | 40 | 28.843 | 9.548 | 7.013 | 27.213 | 28.32 | 28.045 | 27.32 | 604.147 | 25.639 | 26.338 | 1310.967 | 26.93 | 27.165 | 38.453 | 0 | 0.3 | 0.8 | 0 | 0 | 0.2
67 | 30/07/2025 09:20:08.658 | 0 | 0.00042 | 100 | 70 | 40 | 25.703 | 9.522 | 7.008 | 27.293 | 28.282 | 28.032 | 27.352 | 604.172 | 25.622 | 26.324 | 1311.338 | 26.935 | 27.163 | 38.328 | 0 | 0.3 | 1 | 0 | 0 | 0.2
68 | 30/07/2025 09:20:10.292 | 0 | 0.00045 | 100 | 70 | 43 | 28.4 | 9.764 | 7.023 | 27.037 | 28.296 | 28.046 | 27.361 | 604.14 | 25.634 | 26.348 | 1293.76 | 26.922 | 27.151 | 38.443 | 0 | 0 | 1.1 | 0.6 | 0.6 | 0.1
69 | 30/07/2025 09:20:11.926 | 0 | 0.00048 | 100 | 70 | 42 | 29.737 | 9.547 | 7.025 | 26.984 | 28.289 | 28.053 | 27.377 | 604.288 | 25.635 | 26.345 | 1297.999 | 26.894 | 27.167 | 38.345 | 0 | 0 | 1.1 | 0.6 | 0.6 | 0.1
70 | 30/07/2025 09:20:13.561 | 0 | 0.00045 | 100 | 71 | 45 | 27.185 | 9.573 | 7.027 | 27.133 | 28.278 | 28.044 | 27.329 | 603.998 | 25.631 | 26.352 | 1308.473 | 26.954 | 27.173 | 38.563 | 0 | 0 | 0.8 | 0.6 | 0.6 | 0.1
71 | 30/07/2025 09:20:15.195 | 0 | 0.00049 | 100 | 70 | 45 | 26.307 | 9.499 | 7.023 | 27.052 | 28.307 | 28.031 | 27.342 | 605.318 | 25.654 | 26.357 | 1306.678 | 26.92 | 27.154 | 38.331 | 0 | 1.1 | 0.7 | 0 | 0.5 | 0.1
72 | 30/07/2025 09:20:16.831 | 0 | 0.00048 | 99 | 71 | 46 | 28.521 | 9.736 | 7.024 | 27.147 | 28.282 | 28.008 | 27.349 | 604.157 | 25.639 | 26.388 | 1307.807 | 26.94 | 27.144 | 38.263 | 0 | 1.1 | 0.6 | 0 | 0.5 | 0.1
73 | 30/07/2025 09:20:18.464 | 0 | 0.00052 | 100 | 70 | 47 | 25.679 | 9.506 | 7.006 | 26.977 | 28.302 | 28.05 | 27.362 | 604.213 | 25.661 | 26.363 | 1308.488 | 26.901 | 27.158 | 38.523 | 0 | 0.1 | 0.3 | 1 | 0.5 | 0.1
74 | 30/07/2025 09:20:20.102 | 0 | 0.00055 | 100 | 70 | 48 | 28.987 | 9.498 | 7.014 | 27.15 | 28.273 | 28.058 | 27.347 | 604.172 | 25.626 | 26.35 | 1310.99 | 26.925 | 27.174 | 38.214 | 0 | 0.1 | 0.3 | 1 | 0.5 | 0.1
75 | 30/07/2025 09:20:21.735 | 0 | 0.00055 | 100 | 70 | 48 | 29.772 | 9.708 | 7.064 | 27.383 | 28.278 | 28.046 | 27.318 | 604.083 | 25.637 | 26.387 | 1322.817 | 26.936 | 27.169 | 38.312 | 0 | 0.1 | 0 | 1 | 0.5 | 0.1
76 | 30/07/2025 09:20:23.370 | 0 | 0.00062 | 100 | 71 | 48 | 26.805 | 9.801 | 7.071 | 27.063 | 28.265 | 28.028 | 27.371 | 605.529 | 25.64 | 26.364 | 1328.567 | 26.923 | 27.151 | 38.169 | 0 | 0.6 | 0.6 | 0 | 0.5 | 0.1
77 | 30/07/2025 09:20:25.004 | 0 | 0.00057 | 100 | 71 | 47 | 26.689 | 9.574 | 7.063 | 26.944 | 28.276 | 28.048 | 27.352 | 605.26 | 25.643 | 26.372 | 1333.615 | 26.926 | 27.168 | 38.382 | 0 | 0.6 | 0.6 | 0 | 0.5 | 0.1
78 | 30/07/2025 09:20:26.638 | 0 | 0.00061 | 100 | 70 | 47 | 27.917 | 9.685 | 7.063 | 27.076 | 28.279 | 28.066 | 27.361 | 605.423 | 25.629 | 26.347 | 1330.627 | 26.897 | 27.166 | 38.455 | 0 | 0.6 | 0.9 | 0 | 0.5 | 0.1
79 | 30/07/2025 09:20:28.273 | 0 | 0.00069 | 100 | 70 | 47 | 25.83 | 9.571 | 7.041 | 27.226 | 28.279 | 28.043 | 27.345 | 605.271 | 25.64 | 26.366 | 1331.077 | 26.949 | 27.172 | 38.369 | 0 | 0.6 | 0.9 | 0 | 0.5 | 0.1
80 | 30/07/2025 09:20:29.909 | 0 | 0.00074 | 100 | 70 | 47 | 29.171 | 9.798 | 7.025 | 27.228 | 28.299 | 28.051 | 27.316 | 605.232 | 25.655 | 26.355 | 1337.639 | 26.931 | 27.159 | 38.476 | 0 | 0.6 | 0.9 | 0 | 0.5 | 0.1
81 | 30/07/2025 09:20:31.542 | 0 | 0.00077 | 100 | 71 | 48 | 29.687 | 9.695 | 7.061 | 27.179 | 28.284 | 28.024 | 27.362 | 605.472 | 25.632 | 26.356 | 1338.367 | 26.931 | 27.144 | 38.227 | 0 | 0.1 | 0.7 | 0 | 0.8 | 0.1
82 | 30/07/2025 09:20:33.177 | 0 | 0.00085 | 100 | 70 | 47 | 26.097 | 9.715 | 7.062 | 26.878 | 28.304 | 28.053 | 27.351 | 605.402 | 25.623 | 26.372 | 1328.969 | 26.907 | 27.157 | 38.68 | 0 | 0.1 | 1.9 | 0 | 0.8 | 0.1
83 | 30/07/2025 09:20:34.812 | 0 | 0.00094 | 100 | 70 | 47 | 29.777 | 9.572 | 7.074 | 27.045 | 28.29 | 28.059 | 27.351 | 605.378 | 25.626 | 26.349 | 1330.919 | 26.912 | 27.183 | 38.565 | 0 | 0 | 1.3 | 0 | 0.6 | 0.1
84 | 30/07/2025 09:20:36.447 | 0 | 0.001 | 100 | 70 | 47 | 27.219 | 9.711 | 7.074 | 27.276 | 28.157 | 28.052 | 27.335 | 605.228 | 25.64 | 26.347 | 1324.917 | 26.944 | 27.163 | 38.53 | 0 | 0 | 2.2 | 0 | 0.6 | 0.1
85 | 30/07/2025 09:20:38.081 | 0 | 0.0012 | 100 | 70 | 47 | 26.262 | 9.536 | 7.073 | 27.203 | 28.313 | 28.045 | 27.359 | 605.194 | 25.604 | 26.345 | 1318.82 | 26.929 | 27.158 | 38.252 | 0 | 0 | 2.2 | 0 | 0.6 | 0.1
86 | 30/07/2025 09:20:39.718 | 0 | 0.0013 | 100 | 70 | 47 | 29.452 | 9.561 | 7.073 | 27.142 | 28.14 | 28.025 | 27.358 | 605.377 | 25.622 | 26.359 | 1303.843 | 26.949 | 27.143 | 38.311 | 0 | 0 | 0.9 | 0.6 | 1 | 0.2
87 | 30/07/2025 09:20:41.353 | 0 | 0.0014 | 100 | 70 | 47 | 29.431 | 9.629 | 7.073 | 27.056 | 28.146 | 28.052 | 27.358 | 605.399 | 25.639 | 26.337 | 1303.618 | 26.892 | 27.169 | 38.605 | 0 | 0 | 0.6 | 0.6 | 1 | 0.2
88 | 30/07/2025 09:20:42.988 | 0 | 0.0016 | 100 | 71 | 47 | 28.973 | 9.434 | 7.076 | 27.215 | 28.148 | 28.048 | 27.353 | 605.177 | 25.621 | 26.341 | 1303.537 | 26.921 | 27.167 | 38.383 | 0 | 0 | 1.6 | 0.6 | 0 | 0.2
89 | 30/07/2025 09:20:44.620 | 0 | 0.0019 | 100 | 70 | 47 | 29.754 | 9.804 | 7.069 | 27.182 | 28.139 | 28.047 | 27.335 | 605.234 | 25.656 | 26.347 | 1300.552 | 26.933 | 27.161 | 38.51 | 0 | 0 | 0.2 | 0.6 | 0 | 0.2
90 | 30/07/2025 09:20:46.257 | 0 | 0.0021 | 100 | 71 | 48 | 26.834 | 9.504 | 7.024 | 27.043 | 28.127 | 28.05 | 27.346 | 604.115 | 25.631 | 26.345 | 1288.928 | 26.939 | 27.168 | 38.285 | 0 | 0 | 2 | 0 | 0 | 0.2
91 | 30/07/2025 09:20:47.891 | 0 | 0.0025 | 100 | 70 | 47 | 26.665 | 9.855 | 6.901 | 27.018 | 28.145 | 28.039 | 27.359 | 604.272 | 25.644 | 26.36 | 1281.005 | 26.907 | 27.141 | 38.421 | 0 | 0 | 2 | 0 | 0 | 0.2
92 | 30/07/2025 09:20:49.524 | 0 | 0.0027 | 100 | 70 | 46 | 29.517 | 9.769 | 6.902 | 26.992 | 28.142 | 28.056 | 27.378 | 604.292 | 25.624 | 26.363 | 1280.949 | 26.9 | 27.17 | 38.392 | 0 | 0 | 0.8 | 0 | 0 | 0.2
93 | 30/07/2025 09:20:51.159 | 0 | 0.0029 | 100 | 70 | 45 | 28.891 | 9.793 | 6.905 | 27.091 | 28.123 | 28.046 | 27.332 | 603.97 | 25.635 | 26.391 | 1288.321 | 26.961 | 27.166 | 38.334 | 0 | 0.6 | 2.5 | 0 | 0.8 | 0.2
94 | 30/07/2025 09:20:52.797 | 0 | 0.0031 | 100 | 70 | 46 | 29.121 | 9.73 | 6.902 | 27.453 | 28.119 | 28.049 | 27.332 | 604.015 | 25.633 | 26.365 | 1291.136 | 26.936 | 27.164 | 38.405 | 0 | 0.6 | 1.2 | 0 | 0.8 | 0.2
95 | 30/07/2025 09:20:54.438 | 0 | 0.0035 | 100 | 70 | 45 | 29.651 | 9.602 | 6.904 | 27.194 | 28.122 | 28.024 | 27.354 | 604.087 | 25.643 | 26.38 | 1290.533 | 26.931 | 27.149 | 38.02 | 0 | 0.6 | 1 | 0 | 0 | 0.3
96 | 30/07/2025 09:20:56.074 | 0 | 0.0039 | 100 | 70 | 45 | 26.101 | 9.495 | 6.828 | 26.877 | 28.128 | 28.053 | 27.345 | 604.19 | 25.657 | 26.363 | 1292.714 | 26.904 | 27.159 | 38.661 | 0 | 0.6 | 1 | 0 | 0 | 0.3
97 | 30/07/2025 09:20:57.711 | 0 | 0.0043 | 100 | 70 | 45 | 27.387 | 9.797 | 6.83 | 27.16 | 28.109 | 28.064 | 27.343 | 604.166 | 25.634 | 26.368 | 1300.199 | 26.915 | 27.183 | 38.579 | 0 | 0.6 | 0.2 | 0 | 0 | 0.3
98 | 30/07/2025 09:20:59.345 | 0 | 0.0048 | 100 | 71 | 44 | 29.552 | 9.727 | 6.868 | 27.176 | 28.132 | 28.049 | 27.316 | 604.014 | 25.651 | 26.363 | 1301.085 | 26.929 | 27.147 | 38.415 | 0 | 1.3 | 0.9 | 0 | 0.9 | 0.3
99 | 30/07/2025 09:21:00.983 | 0 | 0.0055 | 100 | 70 | 46 | 28.486 | 9.523 | 6.865 | 27.037 | 28.124 | 28.033 | 27.381 | 604.226 | 25.631 | 26.357 | 1301.144 | 26.926 | 27.144 | 38.151 | 0 | 1.3 | 0.2 | 0 | 0.9 | 0.3
100 | 30/07/2025 09:21:02.619 | 0 | 0.0064 | 100 | 70 | 45 | 29.409 | 9.571 | 6.866 | 27.086 | 28.146 | 28.031 | 27.356 | 604.142 | 25.636 | 26.367 | 1298.447 | 26.92 | 27.132 | 38.258 | 0 | 0 | 0.7 | 0 | 0.6 | 0.3
101 | 30/07/2025 09:21:04.255 | 0 | 0.0068 | 100 | 71 | 42 | 29.418 | 9.786 | 6.867 | 26.97 | 28.135 | 28.073 | 27.358 | 604.194 | 25.636 | 26.348 | 1298.135 | 26.898 | 27.172 | 38.478 | 0 | 0 | 0.7 | 0 | 0.6 | 0.3
102 | 30/07/2025 09:21:05.888 | 0 | 0.0075 | 100 | 71 | 43 | 25.869 | 9.51 | 6.869 | 27.047 | 28.141 | 28.048 | 27.342 | 604.008 | 25.622 | 26.38 | 1298.608 | 26.945 | 27.153 | 38.36 | 0 | 0 | 0.7 | 0 | 0.6 | 0.3
103 | 30/07/2025 09:21:07.523 | 0 | 0.0085 | 100 | 72 | 43 | 27.824 | 9.425 | 6.901 | 27.265 | 28.144 | 28.048 | 27.33 | 604.104 | 25.645 | 26.342 | 1302.969 | 26.924 | 27.164 | 38.541 | 0 | 0.6 | 0.6 | 0 | 0 | 0.3
104 | 30/07/2025 09:21:09.159 | 0 | 0.0096 | 100 | 70 | 43 | 29.693 | 9.458 | 6.901 | 27.186 | 28.146 | 28.037 | 27.366 | 604.151 | 25.616 | 26.349 | 1311.786 | 26.935 | 27.148 | 38.11 | 0 | 0.6 | 0.7 | 0 | 0 | 0.3
105 | 30/07/2025 09:21:10.793 | 0 | 0.01 | 100 | 71 | 42 | 26.667 | 9.427 | 6.899 | 27.147 | 28.149 | 28.035 | 27.373 | 604.24 | 25.614 | 26.358 | 1310.768 | 26.909 | 27.138 | 38.333 | 0 | 0.3 | 1.2 | 0.6 | 0.5 | 0.2
106 | 30/07/2025 09:21:12.429 | 0 | 0.012 | 100 | 70 | 42 | 29.48 | 9.799 | 6.926 | 26.866 | 28.14 | 28.078 | 27.348 | 604.085 | 25.614 | 26.353 | 1313.375 | 26.901 | 27.183 | 38.528 | 0 | 0.3 | 0.3 | 0.6 | 0.5 | 0.2
107 | 30/07/2025 09:21:14.064 | 0 | 0.013 | 100 | 70 | 43 | 28.922 | 9.658 | 6.937 | 27.309 | 28.141 | 28.053 | 27.325 | 604.058 | 25.631 | 26.342 | 1307.651 | 26.935 | 27.154 | 38.435 | 0 | 0.3 | 0.3 | 0.6 | 0.5 | 0.2
108 | 30/07/2025 09:21:15.700 | 0 | 0.015 | 100 | 71 | 43 | 25.537 | 9.75 | 6.989 | 27.16 | 28.142 | 28.055 | 27.35 | 604.068 | 25.62 | 26.327 | 1311.957 | 26.937 | 27.161 | 38.293 | 0 | 0.6 | 0 | 0.6 | 0.5 | 0.2
109 | 30/07/2025 09:21:17.335 | 0 | 0.016 | 100 | 70 | 43 | 28.341 | 9.427 | 6.986 | 27.11 | 28.132 | 28.033 | 27.358 | 604.126 | 25.623 | 26.34 | 1312.202 | 26.949 | 27.144 | 38.186 | 0 | 0.6 | 0.9 | 0.6 | 0.5 | 0.2
110 | 30/07/2025 09:21:18.970 | 0 | 0.019 | 100 | 71 | 43 | 29.69 | 9.72 | 6.988 | 26.957 | 28.163 | 28.061 | 27.362 | 604.207 | 25.653 | 26.325 | 1318.133 | 26.899 | 27.162 | 38.63 | 0 | 0.3 | 1.5 | 0 | 0 | 0.2
111 | 30/07/2025 09:21:20.607 | 0 | 0.02 | 100 | 70 | 43 | 27.29 | 9.791 | 7.013 | 27.067 | 28.131 | 28.047 | 27.344 | 604.064 | 25.63 | 26.365 | 1320.354 | 26.907 | 27.162 | 38.538 | 0 | 0.3 | 1.2 | 0 | 0 | 0.2
112 | 30/07/2025 09:21:22.241 | 0 | 0.023 | 100 | 70 | 45 | 29.534 | 9.8 | 7.024 | 27.287 | 28.159 | 28.058 | 27.351 | 604.097 | 25.645 | 26.352 | 1328.654 | 26.929 | 27.16 | 38.411 | 0 | 0.2 | 0.6 | 0 | 0.8 | 0.2
113 | 30/07/2025 09:21:23.878 | 0 | 0.026 | 100 | 71 | 44 | 28.495 | 9.691 | 7.025 | 27.157 | 28.126 | 28.039 | 27.335 | 604.028 | 25.64 | 26.358 | 1330.896 | 26.939 | 27.171 | 38.37 | 0 | 0.2 | 0.6 | 0 | 0.8 | 0.2
114 | 30/07/2025 09:21:25.515 | 0 | 0.029 | 100 | 70 | 44 | 25.66 | 9.296 | 7.03 | 26.909 | 28.135 | 28.041 | 27.354 | 604.169 | 25.636 | 26.365 | 1326.079 | 26.916 | 27.141 | 38.48 | 0 | 0.2 | 0 | 0 | 0.8 | 0.2
115 | 30/07/2025 09:21:27.153 | 0.048 | 0.032 | 100 | 70 | 44 | 28.911 | 9.573 | 7.025 | 27.065 | 28.13 | 28.073 | 27.35 | 604.144 | 25.63 | 26.372 | 1329.586 | 26.908 | 27.172 | 38.365 | 0 | 0.6 | 1.2 | 0.1 | 0.5 | 0.2
116 | 30/07/2025 09:21:28.787 | 0 | 0.036 | 100 | 70 | 42 | 25.847 | 9.766 | 7.026 | 27.282 | 28.134 | 28.061 | 27.349 | 604.094 | 25.649 | 26.371 | 1333.439 | 26.91 | 27.175 | 38.627 | 0 | 0.6 | 1.2 | 0.1 | 0.5 | 0.2
117 | 30/07/2025 09:21:30.422 | 0 | 0.04 | 100 | 71 | 44 | 27.785 | 9.702 | 7.024 | 27.279 | 28.096 | 28.055 | 27.333 | 603.963 | 25.639 | 26.222 | 1328.173 | 26.944 | 27.166 | 38.325 | 0 | 0 | 1.2 | 0 | 0.5 | 0.1
118 | 30/07/2025 09:21:32.057 | 0 | 0.044 | 100 | 71 | 44 | 29.645 | 9.513 | 7.028 | 27.19 | 28.119 | 28.022 | 27.347 | 604.05 | 25.635 | 26.303 | 1317.093 | 26.936 | 27.147 | 38.195 | 0 | 0 | 1.2 | 0 | 0.5 | 0.1
119 | 30/07/2025 09:21:33.692 | 0 | 0.049 | 100 | 70 | 43 | 27.896 | 9.368 | 7.027 | 26.967 | 28.126 | 28.056 | 27.372 | 603.057 | 25.639 | 26.35 | 1308.398 | 26.903 | 27.148 | 38.53 | 0 | 0 | 0.6 | 0 | 0.5 | 0.1
120 | 30/07/2025 09:21:35.328 | 0 | 0.055 | 100 | 70 | 41 | 25.821 | 9.551 | 7.037 | 27.138 | 28.123 | 28.057 | 27.348 | 602.923 | 25.632 | 26.366 | 1308.321 | 26.92 | 27.183 | 38.386 | 0 | 1 | 2.2 | 0 | 0.5 | 0.1
121 | 30/07/2025 09:21:36.964 | 0 | 0.062 | 100 | 71 | 43 | 28.904 | 9.505 | 7.036 | 27.444 | 28.135 | 28.053 | 27.363 | 603.029 | 25.641 | 26.359 | 1303.695 | 26.934 | 27.161 | 38.375 | 0 | 1 | 0.7 | 0 | 0.5 | 0.1
122 | 30/07/2025 09:21:38.598 | 0.072 | 0.069 | 100 | 70 | 43 | 25.535 | 9.572 | 7.037 | 27.282 | 28.125 | 28.043 | 27.319 | 602.531 | 25.63 | 26.228 | 1303.418 | 26.952 | 27.168 | 38.392 | 0 | 0 | 1.9 | 0.7 | 0.8 | 0.1
123 | 30/07/2025 09:21:40.235 | 0.072 | 0.074 | 100 | 70 | 43 | 28.27 | 9.558 | 7.031 | 27.162 | 28.156 | 28.032 | 27.345 | 602.893 | 25.636 | 26.219 | 1301.157 | 26.917 | 27.131 | 38.107 | 0 | 0 | 1.5 | 0.7 | 0.8 | 0.1
124 | 30/07/2025 09:21:41.870 | 0.096 | 0.085 | 100 | 70 | 43 | 29.698 | 9.575 | 7.037 | 26.999 | 28.136 | 28.078 | 27.346 | 602.865 | 25.622 | 26.351 | 1303.302 | 26.91 | 27.172 | 38.519 | 0 | 0 | 1.5 | 0.7 | 0.8 | 0.1
125 | 30/07/2025 09:21:43.504 | 0.12 | 0.092 | 100 | 70 | 43 | 27.203 | 9.867 | 7.065 | 27.108 | 28.147 | 28.056 | 27.348 | 602.831 | 25.611 | 26.366 | 1308.598 | 26.926 | 27.161 | 38.44 | 0 | 1.3 | 1.1 | 0.6 | 1.2 | 0.1
126 | 30/07/2025 09:21:45.140 | 0.192 | 0.1 | 100 | 70 | 43 | 26.167 | 9.437 | 7.073 | 27.224 | 28.156 | 28.052 | 27.337 | 604.061 | 25.624 | 26.344 | 1319.033 | 26.931 | 27.16 | 38.526 | 0 | 1.3 | 1 | 0.6 | 1.2 | 0.1
127 | 30/07/2025 09:21:46.774 | 0.12 | 0.11 | 100 | 70 | 43 | 28.406 | 9.279 | 7.074 | 27.434 | 28.147 | 28.036 | 27.336 | 603.998 | 25.624 | 26.348 | 1325.325 | 26.932 | 27.158 | 38.273 | 0 | 0 | 1.2 | 0 | 0.2 | 0.1
128 | 30/07/2025 09:21:48.410 | 0.216 | 0.13 | 100 | 70 | 44 | 25.572 | 9.546 | 7.032 | 27.019 | 28.157 | 28.041 | 27.37 | 604.284 | 25.622 | 26.276 | 1326.092 | 26.921 | 27.142 | 38.321 | 0 | 0 | 0.7 | 0 | 0.2 | 0.1
129 | 30/07/2025 09:21:50.043 | 0.288 | 0.15 | 100 | 70 | 44 | 28.855 | 9.499 | 7.037 | 26.813 | 28.136 | 28.062 | 27.19 | 604.003 | 25.617 | 26.207 | 1314.99 | 26.927 | 27.187 | 38.522 | 0 | 0 | 0.7 | 0 | 0.2 | 0.1
130 | 30/07/2025 09:21:51.678 | 0.336 | 0.17 | 100 | 71 | 44 | 29.695 | 9.499 | 7.033 | 27.207 | 28.149 | 28.055 | 27.204 | 604.046 | 25.639 | 26.201 | 1306.446 | 26.933 | 27.171 | 38.469 | 0 | 0.6 | 0.1 | 0 | 0.5 | 0.1
131 | 30/07/2025 09:21:53.312 | 0.36 | 0.18 | 100 | 71 | 44 | 26.683 | 9.39 | 7.036 | 27.096 | 28.121 | 28.051 | 27.33 | 602.806 | 25.634 | 26.199 | 1293.772 | 26.934 | 27.164 | 38.207 | 0 | 0.6 | 1.4 | 0 | 0.5 | 0.1
132 | 30/07/2025 09:21:54.949 | 0.408 | 0.21 | 100 | 70 | 43 | 29.561 | 9.536 | 7.033 | 27.142 | 28.153 | 28.029 | 27.347 | 603.016 | 25.632 | 26.266 | 1289.089 | 26.927 | 27.144 | 38.454 | 0 | 0 | 0.8 | 0 | 0.5 | 0.1
133 | 30/07/2025 09:21:56.582 | 0.456 | 0.23 | 100 | 70 | 41 | 27.806 | 9.5 | 7.036 | 26.8 | 28.125 | 28.062 | 27.203 | 602.807 | 25.648 | 26.215 | 1278.587 | 26.925 | 27.154 | 38.468 | 0 | 0 | 0.8 | 0 | 0.5 | 0.1
134 | 30/07/2025 09:21:58.219 | 0.552 | 0.26 | 100 | 71 | 44 | 25.782 | 9.728 | 7.036 | 27.277 | 28.149 | 28.061 | 27.202 | 602.743 | 25.646 | 26.291 | 1279.086 | 26.91 | 27.17 | 38.51 | 0 | 0 | 0.1 | 0.3 | 1.9 | 0.1
135 | 30/07/2025 09:21:59.859 | 0.624 | 0.29 | 100 | 72 | 43 | 29.067 | 9.575 | 7.06 | 27.259 | 28.125 | 28.064 | 27.345 | 603.017 | 25.634 | 26.288 | 1288.8 | 26.931 | 27.165 | 38.403 | 0 | 0 | 0.1 | 0.3 | 1.9 | 0.1
136 | 30/07/2025 09:22:01.495 | 0.672 | 0.33 | 100 | 70 | 44 | 29.561 | 9.778 | 7.036 | 27.101 | 28.105 | 28.036 | 27.327 | 602.745 | 25.626 | 26.235 | 1286.318 | 26.952 | 27.166 | 38.235 | 0 | 0 | 1.8 | 0.3 | 1.9 | 0.1
137 | 30/07/2025 09:22:03.135 | 0.864 | 0.37 | 100 | 71 | 44 | 26.095 | 9.429 | 7.031 | 27.051 | 28.135 | 28.036 | 27.203 | 603.023 | 25.655 | 26.226 | 1286.347 | 26.926 | 27.137 | 38.21 | 0 | 0 | 1 | 0 | 0.4 | 0.1
138 | 30/07/2025 09:22:04.770 | 0.936 | 0.4 | 100 | 72 | 44 | 29.707 | 9.566 | 7.036 | 26.899 | 28.111 | 28.057 | 27.335 | 602.767 | 25.631 | 26.379 | 1286.154 | 26.929 | 27.16 | 38.432 | 0 | 0 | 1.5 | 0 | 0.4 | 0.1
139 | 30/07/2025 09:22:06.407 | 0.984 | 0.46 | 100 | 70 | 44 | 27.209 | 9.577 | 7.011 | 27.259 | 28.132 | 28.055 | 27.208 | 602.953 | 25.655 | 26.218 | 1288.961 | 26.909 | 27.174 | 38.4 | 0 | 0 | 1.1 | 0.6 | 0 | 0.1
140 | 30/07/2025 09:22:08.043 | 1.176 | 0.51 | 100 | 71 | 44 | 26.156 | 9.572 | 7.007 | 27.129 | 28.112 | 28.058 | 27.173 | 602.745 | 25.633 | 26.225 | 1291.067 | 26.951 | 27.176 | 38.372 | 0 | 0 | 1.1 | 0.6 | 0 | 0.1
141 | 30/07/2025 09:22:09.678 | 1.344 | 0.58 | 100 | 71 | 43 | 29.343 | 9.726 | 7.007 | 27.333 | 28.13 | 28.029 | 27.198 | 602.626 | 25.626 | 26.221 | 1298.672 | 26.935 | 27.15 | 38.202 | 0 | 0 | 0.2 | 0.6 | 0 | 0.1
142 | 30/07/2025 09:22:11.314 | 1.488 | 0.66 | 100 | 70 | 44 | 29.309 | 9.872 | 7.004 | 28.558 | 28.133 | 28.047 | 27.22 | 603.11 | 25.642 | 26.326 | 1293.637 | 26.913 | 27.149 | 38.475 | 0 | 0.3 | 0.6 | 0 | 0 | 0.1
143 | 30/07/2025 09:22:12.950 | 1.728 | 0.72 | 100 | 70 | 44 | 28.822 | 9.8 | 7.007 | 28.466 | 28.154 | 28.058 | 27.203 | 602.818 | 25.636 | 26.226 | 1295.887 | 26.902 | 27.151 | 38.726 | 0 | 0.3 | 1.4 | 0 | 0 | 0.1
144 | 30/07/2025 09:22:14.583 | 1.872 | 0.81 | 100 | 70 | 45 | 29.723 | 9.729 | 7.007 | 28.745 | 28.153 | 28.05 | 27.204 | 601.554 | 25.63 | 26.211 | 1291.343 | 26.926 | 27.162 | 38.399 | 0 | 0 | 0.8 | 0.2 | 0.5 | 0
145 | 30/07/2025 09:22:16.220 | 2.064 | 0.89 | 100 | 70 | 45 | 26.659 | 9.498 | 7.038 | 28.696 | 28.138 | 28.05 | 27.172 | 602.674 | 25.616 | 26.224 | 1288.773 | 26.951 | 27.163 | 38.377 | 0 | 0 | 0.8 | 0.2 | 0.5 | 0
146 | 30/07/2025 09:22:17.858 | 2.352 | 1 | 100 | 71 | 44 | 26.622 | 9.868 | 7.07 | 28.579 | 28.157 | 28.04 | 27.218 | 602.98 | 25.643 | 26.209 | 1284.376 | 26.924 | 27.149 | 38.19 | 0 | 0 | 0.8 | 0.2 | 0.5 | 0
147 | 30/07/2025 09:22:19.493 | 2.64 | 1.1 | 100 | 71 | 43 | 29.426 | 9.727 | 7.073 | 28.456 | 28.128 | 28.081 | 27.195 | 602.98 | 25.613 | 26.2 | 1286.065 | 26.908 | 27.182 | 38.304 | 0 | 0.6 | 1.3 | 1.2 | 0.3 | 0
148 | 30/07/2025 09:22:21.130 | 2.952 | 1.3 | 100 | 70 | 44 | 28.984 | 9.572 | 7.075 | 28.875 | 28.143 | 28.054 | 27.196 | 602.766 | 25.617 | 26.214 | 1278.346 | 26.914 | 27.164 | 38.46 | 0 | 0.6 | 0.7 | 1.2 | 0.3 | 0
149 | 30/07/2025 09:22:22.770 | 3.24 | 1.4 | 100 | 70 | 44 | 29.093 | 9.476 | 7.076 | 28.748 | 28.129 | 28.059 | 27.184 | 602.791 | 25.609 | 26.205 | 1278.657 | 26.951 | 27.186 | 38.351 | 0 | 0.6 | 1.9 | 0 | 0.6 | 0
150 | 30/07/2025 09:22:24.405 | 3.6 | 1.6 | 100 | 70 | 44 | 29.569 | 9.662 | 7.073 | 28.762 | 28.15 | 28.045 | 27.184 | 602.652 | 25.626 | 26.19 | 1281.548 | 26.921 | 27.154 | 38.384 | 0 | 0.6 | 1.3 | 0 | 0.6 | 0
151 | 30/07/2025 09:22:26.042 | 4.032 | 1.8 | 100 | 69 | 45 | 26.181 | 9.633 | 7.06 | 28.677 | 28.131 | 28.043 | 27.216 | 602.928 | 25.613 | 26.188 | 1290.344 | 26.928 | 27.138 | 38.261 | 0 | 0.6 | 1.3 | 0 | 0.6 | 0
152 | 30/07/2025 09:22:27.677 | 4.44 | 1.9 | 100 | 70 | 44 | 27.172 | 9.731 | 7.043 | 28.483 | 28.134 | 28.057 | 27.203 | 602.632 | 25.625 | 26.212 | 1303.045 | 26.917 | 27.177 | 38.511 | 0 | 0 | 0.5 | 0 | 0.7 | 0
153 | 30/07/2025 09:22:29.311 | 4.92 | 2.2 | 100 | 71 | 44 | 29.504 | 9.673 | 7.034 | 28.762 | 28.151 | 28.059 | 27.197 | 602.8 | 25.661 | 26.214 | 1308.764 | 26.93 | 27.169 | 38.547 | 0 | 0 | 0.6 | 0 | 0.7 | 0
154 | 30/07/2025 09:22:30.950 | 5.496 | 2.4 | 100 | 70 | 44 | 26.128 | 9.591 | 7.036 | 28.667 | 28.13 | 28.054 | 27.177 | 602.716 | 25.636 | 26.226 | 1308.44 | 26.968 | 27.161 | 38.38 | 0 | 0.6 | 0.6 | 0 | 0 | 0
155 | 30/07/2025 09:22:32.587 | 6.048 | 2.7 | 100 | 70 | 44 | 29.362 | 9.579 | 7.035 | 28.783 | 28.156 | 28.034 | 27.201 | 602.919 | 25.642 | 26.215 | 1308.935 | 26.933 | 27.155 | 38.229 | 0 | 0.6 | 0.7 | 0 | 0 | 0
156 | 30/07/2025 09:22:34.223 | 6.72 | 3 | 100 | 71 | 43 | 29.334 | 9.428 | 7.034 | 29.603 | 28.114 | 28.046 | 27.198 | 602.847 | 25.629 | 26.226 | 1317.86 | 26.935 | 27.159 | 38.364 | 1 | 0.6 | 1.4 | 0 | 0.4 | 0.1
157 | 30/07/2025 09:22:35.869 | 7.416 | 3.3 | 100 | 70 | 43 | 25.78 | 9.538 | 7.036 | 30.286 | 28.116 | 28.055 | 27.197 | 602.821 | 25.639 | 26.233 | 1316.195 | 26.896 | 27.171 | 38.638 | 1 | 0.6 | 1.4 | 0 | 0.4 | 0.1
158 | 30/07/2025 09:22:37.504 | 8.136 | 3.7 | 100 | 70 | 44 | 27.754 | 9.672 | 7.035 | 30.173 | 28.123 | 28.067 | 27.204 | 604.114 | 25.629 | 26.227 | 1310.095 | 26.929 | 27.161 | 38.334 | 1 | 0.6 | 1.7 | 0 | 0.4 | 0.1
159 | 30/07/2025 09:22:39.141 | 8.904 | 4.1 | 100 | 70 | 44 | 29.554 | 9.516 | 7.071 | 30.094 | 28.116 | 28.042 | 27.169 | 603.951 | 25.623 | 26.231 | 1301.786 | 26.953 | 27.17 | 38.382 | 1 | 0.6 | 0.7 | 0.6 | 0 | 0.1
160 | 30/07/2025 09:22:40.776 | 9.744 | 4.5 | 100 | 70 | 45 | 26.704 | 9.481 | 7.072 | 30.311 | 28.098 | 28.032 | 27.216 | 604.077 | 25.623 | 26.222 | 1298.484 | 26.931 | 27.148 | 38.052 | 1 | 0.6 | 0.3 | 0.6 | 0 | 0.1
161 | 30/07/2025 09:22:42.414 | 10.776 | 5 | 100 | 70 | 44 | 29.409 | 9.672 | 7.075 | 30.064 | 28.111 | 28.06 | 27.201 | 603.983 | 25.627 | 26.229 | 1296.678 | 26.923 | 27.146 | 38.52 | 1 | 0.7 | 0 | 0 | 0.5 | 0.2
162 | 30/07/2025 09:22:44.049 | 11.832 | 5.6 | 100 | 71 | 45 | 28.913 | 9.567 | 7.073 | 31.626 | 28.149 | 28.06 | 27.204 | 604.176 | 25.655 | 26.215 | 1296.404 | 26.911 | 27.163 | 38.564 | 1 | 0.7 | 0 | 0 | 0.5 | 0.2
163 | 30/07/2025 09:22:45.685 | 12.888 | 6.2 | 100 | 70 | 44 | 25.507 | 9.506 | 7.103 | 31.717 | 28.144 | 28.075 | 27.177 | 603.952 | 25.625 | 26.222 | 1286.477 | 26.957 | 27.188 | 38.396 | 1 | 0.7 | 1.2 | 0 | 0.5 | 0.2
164 | 30/07/2025 09:22:47.319 | 14.064 | 6.7 | 99 | 70 | 44 | 28.36 | 9.648 | 7.12 | 31.841 | 28.161 | 28.031 | 27.195 | 603.936 | 25.629 | 26.214 | 1298.941 | 26.933 | 27.149 | 38.148 | 1 | 1 | 1.1 | 0.2 | 0.9 | 0.2
165 | 30/07/2025 09:22:48.960 | 15.384 | 7.4 | 100 | 71 | 44 | 26.208 | 9.431 | 7.126 | 31.487 | 28.137 | 28.03 | 27.213 | 604.024 | 25.618 | 26.213 | 1300.84 | 26.949 | 27.157 | 38.208 | 1 | 1 | 1.4 | 0.2 | 0.9 | 0.2
166 | 30/07/2025 09:22:50.596 | 16.92 | 8.2 | 100 | 71 | 44 | 27.11 | 9.279 | 7.103 | 33.206 | 28.166 | 28.062 | 27.199 | 604.083 | 25.635 | 26.207 | 1298.499 | 26.895 | 27.152 | 38.561 | 2 | 0.9 | 1.4 | 0 | 1.1 | 0.2
167 | 30/07/2025 09:22:52.237 | 18.288 | 8.8 | 100 | 70 | 44 | 29.548 | 9.775 | 7.102 | 33.411 | 28.14 | 28.057 | 27.207 | 604.152 | 25.625 | 26.209 | 1304.201 | 26.927 | 27.17 | 38.424 | 3 | 0.9 | 0.7 | 0 | 1.1 | 0.2
168 | 30/07/2025 09:22:53.872 | 19.752 | 9.5 | 100 | 70 | 44 | 28.295 | 9.728 | 7.106 | 33.527 | 28.139 | 28.048 | 27.161 | 603.833 | 25.621 | 26.22 | 1298.753 | 26.943 | 27.166 | 38.461 | 3 | 0.9 | 0.7 | 0 | 1.1 | 0.2
169 | 30/07/2025 09:22:55.508 | 21.528 | 11 | 100 | 70 | 44 | 25.557 | 9.574 | 7.108 | 33.554 | 28.16 | 28.045 | 27.225 | 604.198 | 25.626 | 26.197 | 1308.268 | 26.924 | 27.145 | 38.31 | 2 | 0.1 | 0.7 | 0.6 | 0 | 0.2
170 | 30/07/2025 09:22:57.143 | 23.184 | 11 | 100 | 70 | 44 | 28.746 | 9.672 | 7.123 | 33.602 | 28.124 | 28.075 | 27.195 | 604.078 | 25.608 | 26.183 | 1308.217 | 26.916 | 27.173 | 38.344 | 3 | 0.1 | 0.6 | 0.6 | 0 | 0.2
171 | 30/07/2025 09:22:58.778 | 24.792 | 12 | 100 | 70 | 42 | 25.764 | 9.754 | 7.124 | 34.677 | 28.152 | 28.065 | 27.218 | 604.254 | 25.615 | 26.182 | 1299.498 | 26.9 | 27.16 | 38.513 | 3 | 1 | 1.3 | 0.1 | 0 | 0.2
172 | 30/07/2025 09:23:00.413 | 28.056 | 14 | 100 | 70 | 45 | 27.741 | 9.739 | 7.127 | 34.945 | 28.125 | 28.056 | 27.183 | 603.885 | 25.631 | 26.204 | 1298.512 | 26.952 | 27.187 | 38.503 | 4 | 1 | 0.9 | 0.1 | 0 | 0.2
173 | 30/07/2025 09:23:02.051 | 30.84 | 15 | 100 | 70 | 45 | 29.564 | 9.563 | 7.127 | 36.461 | 28.143 | 28.046 | 27.181 | 603.962 | 25.65 | 26.197 | 1308.299 | 26.925 | 27.158 | 38.306 | 4 | 1 | 0.9 | 0.1 | 0 | 0.2
174 | 30/07/2025 09:23:03.688 | 33.168 | 18 | 100 | 71 | 45 | 27.948 | 9.429 | 7.124 | 37.737 | 28.121 | 28.03 | 27.212 | 604.076 | 25.642 | 26.213 | 1296.2 | 26.928 | 27.139 | 38.173 | 4 | 0.9 | 0.8 | 0 | 0 | 0.2
175 | 30/07/2025 09:23:05.322 | 35.664 | 18 | 100 | 71 | 45 | 25.75 | 9.422 | 7.128 | 37.367 | 28.132 | 28.059 | 27.195 | 603.943 | 25.631 | 26.232 | 1288.268 | 26.92 | 27.169 | 38.519 | 5 | 0.9 | 1.6 | 0 | 0 | 0.2
176 | 30/07/2025 09:23:06.956 | 38.592 | 20 | 100 | 70 | 44 | 28.984 | 9.557 | 7.126 | 39.202 | 28.111 | 28.073 | 27.207 | 603.991 | 25.636 | 26.225 | 1288.641 | 26.912 | 27.177 | 38.516 | 6 | 1.8 | 1.7 | 0 | 0.8 | 0.1
177 | 30/07/2025 09:23:08.594 | 42.864 | 23 | 100 | 72 | 45 | 25.492 | 9.76 | 7.124 | 39.402 | 28.122 | 28.052 | 27.171 | 603.899 | 25.64 | 26.237 | 1290.921 | 26.941 | 27.165 | 38.642 | 5 | 1.8 | 1.5 | 0 | 0.8 | 0.1
178 | 30/07/2025 09:23:10.232 | 46.704 | 25 | 100 | 70 | 46 | 28.352 | 9.726 | 7.102 | 40.772 | 28.136 | 28.036 | 27.197 | 604.164 | 25.633 | 26.234 | 1286.53 | 26.928 | 27.147 | 38.367 | 8 | 2 | 0.8 | 0.3 | 0 | 0.1
179 | 30/07/2025 09:23:11.869 | 50.808 | 28 | 100 | 71 | 46 | 29.647 | 9.728 | 7.103 | 41.73 | 28.109 | 28.049 | 27.189 | 603.992 | 25.622 | 26.222 | 1288.733 | 26.937 | 27.169 | 38.441 | 8 | 2 | 0.8 | 0.3 | 0 | 0.1
180 | 30/07/2025 09:23:13.505 | 54.312 | 31 | 100 | 70 | 46 | 27.244 | 9.571 | 7.104 | 43.611 | 28.123 | 28.064 | 27.192 | 604.088 | 25.638 | 26.223 | 1297.039 | 26.893 | 27.169 | 38.578 | 7 | 2 | 0.7 | 0.3 | 0 | 0.1
181 | 30/07/2025 09:23:15.140 | 58.128 | 33 | 100 | 70 | 46 | 26.055 | 9.504 | 7.102 | 45.35 | 28.132 | 28.061 | 27.203 | 604.082 | 25.627 | 26.22 | 1287.345 | 26.942 | 27.167 | 38.568 | 10 | 2 | 0.3 | 0 | 0.5 | 0.1
182 | 30/07/2025 09:23:16.774 | 60.84 | 34 | 100 | 71 | 45 | 28.359 | 9.556 | 7.104 | 45.208 | 28.144 | 28.054 | 27.178 | 603.996 | 25.657 | 26.221 | 1281.355 | 26.929 | 27.16 | 38.554 | 10 | 2 | 0.9 | 0 | 0.5 | 0.1
183 | 30/07/2025 09:23:18.409 | 64.152 | 36 | 100 | 72 | 46 | 25.546 | 9.735 | 7.102 | 48.093 | 28.114 | 28.023 | 27.204 | 604.081 | 25.626 | 26.22 | 1288.357 | 26.932 | 27.156 | 38.128 | 13 | 2.6 | 0.8 | 0.6 | 0.2 | 0
184 | 30/07/2025 09:23:20.044 | 66.504 | 38 | 100 | 71 | 44 | 28.713 | 9.586 | 7.103 | 49.817 | 28.14 | 28.049 | 27.193 | 603.938 | 25.627 | 26.228 | 1305.417 | 26.911 | 27.154 | 38.474 | 13 | 2.6 | 0.8 | 0.6 | 0.2 | 0
185 | 30/07/2025 09:23:21.683 | 69.288 | 40 | 100 | 71 | 44 | 29.653 | 9.794 | 7.125 | 51.5 | 28.152 | 28.062 | 27.194 | 604.123 | 25.623 | 26.204 | 1316.618 | 26.902 | 27.179 | 38.538 | 14 | 2.6 | 1.6 | 0.6 | 0.2 | 0
186 | 30/07/2025 09:23:23.318 | 71.904 | 42 | 100 | 71 | 46 | 26.578 | 9.87 | 7.104 | 54.225 | 28.129 | 28.074 | 27.176 | 603.895 | 25.617 | 26.213 | 1324.506 | 26.953 | 27.178 | 38.567 | 15 | 3.5 | 2.6 | 0 | 0.6 | 0.1
187 | 30/07/2025 09:23:24.952 | 73.488 | 43 | 100 | 71 | 46 | 29.551 | 9.623 | 7.103 | 55.749 | 28.132 | 28.058 | 27.184 | 603.951 | 25.625 | 26.209 | 1320.455 | 26.929 | 27.161 | 38.338 | 15 | 3.5 | 1.9 | 0 | 0.6 | 0.1
188 | 30/07/2025 09:23:26.587 | 78.648 | 47 | 100 | 70 | 48 | 27.915 | 9.5 | 7.074 | 57.153 | 28.137 | 28.025 | 27.198 | 603.957 | 25.609 | 26.21 | 1317.575 | 26.944 | 27.149 | 38.155 | 17 | 2.5 | 0.7 | 0.3 | 0.5 | 0.1
189 | 30/07/2025 09:23:28.222 | 82.152 | 49 | 100 | 70 | 48 | 25.765 | 9.567 | 7.073 | 59.245 | 28.162 | 28.058 | 27.191 | 604.145 | 25.617 | 26.208 | 1308.306 | 26.9 | 27.164 | 38.742 | 16 | 2.5 | 0.8 | 0.3 | 0.5 | 0.1
190 | 30/07/2025 09:23:29.859 | 84.072 | 51 | 100 | 70 | 47 | 29.139 | 9.429 | 7.072 | 62.042 | 28.13 | 28.066 | 27.205 | 604.085 | 25.607 | 26.187 | 1303.273 | 26.922 | 27.169 | 38.583 | 16 | 2.5 | 0.8 | 0.3 | 0.5 | 0.1
191 | 30/07/2025 09:23:31.498 | 85.824 | 52 | 100 | 70 | 47 | 29.54 | 9.573 | 7.074 | 63.628 | 28.137 | 28.047 | 27.167 | 603.827 | 25.619 | 26.205 | 1313.244 | 26.929 | 27.167 | 38.353 | 20.001 | 2.6 | 1.3 | 0.6 | 0 | 0.2
192 | 30/07/2025 09:23:33.134 | 87.576 | 53 | 100 | 70 | 48 | 26.235 | 9.528 | 7.071 | 67.131 | 28.131 | 28.04 | 27.22 | 604.151 | 25.617 | 26.191 | 1313.602 | 26.927 | 27.142 | 38.252 | 26.001 | 2.6 | 0.1 | 0.6 | 0 | 0.2
193 | 30/07/2025 09:23:34.769 | 88.968 | 55 | 100 | 71 | 47 | 29.669 | 9.572 | 7.072 | 68.803 | 28.126 | 28.04 | 27.202 | 604.074 | 25.64 | 26.205 | 1316.213 | 26.925 | 27.135 | 38.36 | 25.001 | 3.2 | 0.7 | 0.2 | 0.5 | 0.2
194 | 30/07/2025 09:23:36.403 | 89.736 | 54 | 100 | 70 | 48 | 27.224 | 9.566 | 7.073 | 70.303 | 28.137 | 28.072 | 27.217 | 604.133 | 25.641 | 26.202 | 1316.384 | 26.891 | 27.166 | 38.38 | 21.001 | 3.2 | 0.7 | 0.2 | 0.5 | 0.2
195 | 30/07/2025 09:23:38.036 | 89.856 | 55 | 100 | 70 | 48 | 26.088 | 9.574 | 7.076 | 73.48 | 28.121 | 28.06 | 27.186 | 603.973 | 25.629 | 26.232 | 1313.53 | 26.956 | 27.181 | 38.451 | 21.001 | 3.2 | 0.7 | 0.2 | 0.5 | 0.2
196 | 30/07/2025 09:23:39.674 | 92.472 | 58 | 100 | 70 | 48 | 29.293 | 9.837 | 7.074 | 75.199 | 28.141 | 28.057 | 27.171 | 603.855 | 25.657 | 26.231 | 1310.867 | 26.918 | 27.161 | 38.467 | 22.001 | 1.5 | 1.4 | 0.6 | 0.8 | 0.3
197 | 30/07/2025 09:23:41.310 | 93.072 | 58 | 100 | 71 | 49 | 29.306 | 9.734 | 7.041 | 77.747 | 28.116 | 28.041 | 27.204 | 604.112 | 25.633 | 26.229 | 1300.829 | 26.93 | 27.145 | 38.143 | 25.001 | 1.5 | 0.6 | 0.6 | 0.8 | 0.3
198 | 30/07/2025 09:23:42.943 | 93.624 | 59 | 100 | 70 | 48 | 28.7 | 9.576 | 7.034 | 79.239 | 28.136 | 28.054 | 27.212 | 604.149 | 25.647 | 26.216 | 1292.832 | 26.917 | 27.148 | 38.45 | 27.001 | 3 | 0.7 | 0.6 | 0 | 0.3
199 | 30/07/2025 09:23:44.578 | 93.912 | 59 | 99 | 70 | 48 | 29.736 | 9.574 | 7.01 | 80.866 | 28.113 | 28.077 | 27.211 | 602.714 | 25.626 | 26.234 | 1296.056 | 26.902 | 27.185 | 38.635 | 26.001 | 3 | 1.1 | 0.6 | 0 | 0.3
200 | 30/07/2025 09:23:46.210 | 95.448 | 59 | 100 | 70 | 49 | 26.552 | 9.572 | 6.99 | 83.262 | 28.11 | 28.053 | 27.178 | 602.711 | 25.629 | 26.235 | 1304.77 | 26.931 | 27.16 | 38.499 | 26.001 | 3 | 1.1 | 0.6 | 0 | 0.3
201 | 30/07/2025 09:23:47.842 | 95.904 | 61 | 100 | 71 | 48 | 26.705 | 9.73 | 6.988 | 85.48 | 28.122 | 28.046 | 27.192 | 602.908 | 25.623 | 26.208 | 1298.612 | 26.917 | 27.166 | 38.317 | 27.001 | 2.6 | 0.7 | 0.6 | 0.6 | 0.3
202 | 30/07/2025 09:23:49.474 | 96.144 | 61 | 100 | 71 | 48 | 29.451 | 9.51 | 6.913 | 86.801 | 28.11 | 28.042 | 27.196 | 602.817 | 25.624 | 26.229 | 1298.548 | 26.949 | 27.164 | 38.278 | 25.001 | 2.6 | 0.8 | 0.6 | 0.6 | 0.3
203 | 30/07/2025 09:23:51.115 | 96.048 | 61 | 100 | 71 | 48 | 28.956 | 9.597 | 6.829 | 89.904 | 28.153 | 28.07 | 27.192 | 602.811 | 25.654 | 26.231 | 1299.903 | 26.895 | 27.174 | 38.626 | 25.001 | 1.9 | 0.9 | 0 | 0.1 | 0.3
204 | 30/07/2025 09:23:52.752 | 95.856 | 61 | 100 | 71 | 49 | 29.108 | 9.676 | 6.832 | 91.149 | 28.132 | 28.065 | 27.192 | 603.979 | 25.631 | 26.233 | 1298.625 | 26.943 | 27.153 | 38.521 | 22.001 | 1.9 | 1.1 | 0 | 0.1 | 0.3
205 | 30/07/2025 09:23:54.388 | 95.736 | 60 | 100 | 71 | 49 | 29.545 | 9.722 | 6.828 | 93.127 | 28.154 | 28.061 | 27.161 | 602.75 | 25.65 | 26.21 | 1313.456 | 26.952 | 27.162 | 38.541 | 21.001 | 4.6 | 1.4 | 0.9 | 0.8 | 0.3
206 | 30/07/2025 09:23:56.021 | 97.488 | 62 | 100 | 70 | 49 | 26.228 | 9.431 | 6.866 | 93.981 | 28.132 | 28.045 | 27.186 | 602.825 | 25.616 | 26.21 | 1318.379 | 26.93 | 27.161 | 38.372 | 21.001 | 4.6 | 1.4 | 0.9 | 0.8 | 0.3
207 | 30/07/2025 09:23:57.657 | 97.416 | 62 | 100 | 72 | 49 | 27.072 | 9.576 | 6.867 | 95.91 | 28.139 | 28.057 | 27.194 | 603.994 | 25.627 | 26.237 | 1299.306 | 26.919 | 27.147 | 38.528 | 21.001 | 4.6 | 1.1 | 0.9 | 0.8 | 0.3
208 | 30/07/2025 09:23:59.294 | 97.2 | 61 | 100 | 71 | 49 | 29.469 | 9.497 | 6.902 | 97.96 | 28.137 | 28.061 | 27.204 | 604.125 | 25.603 | 26.204 | 1310.531 | 26.894 | 27.171 | 38.351 | 25.001 | 2.6 | 1.2 | 0.6 | 0.5 | 0.3
209 | 30/07/2025 09:24:00.929 | 97.2 | 61 | 100 | 71 | 49 | 26.084 | 9.496 | 6.903 | 99.08 | 28.14 | 28.059 | 27.182 | 603.955 | 25.614 | 26.218 | 1308.618 | 26.93 | 27.176 | 38.526 | 26.001 | 2.6 | 1.8 | 0.6 | 0.5 | 0.3
210 | 30/07/2025 09:24:02.566 | 97.32 | 61 | 100 | 71 | 49 | 29.281 | 9.705 | 6.901 | 99.066 | 28.133 | 28.059 | 27.174 | 603.942 | 25.611 | 26.189 | 1308.409 | 26.93 | 27.17 | 38.502 | 30.001 | 1.1 | 1.1 | 0.6 | 0.3 | 0.2
211 | 30/07/2025 09:24:04.202 | 97.944 | 63 | 100 | 71 | 50 | 29.261 | 9.731 | 6.935 | 101.662 | 28.121 | 28.03 | 27.199 | 603.939 | 25.617 | 26.219 | 1298.489 | 26.948 | 27.145 | 38.156 | 30.001 | 1.1 | 1.1 | 0.6 | 0.3 | 0.2
212 | 30/07/2025 09:24:05.838 | 98.784 | 63 | 100 | 71 | 50 | 25.725 | 9.569 | 6.936 | 103.039 | 28.148 | 28.053 | 27.207 | 604.081 | 25.625 | 26.201 | 1296.087 | 26.898 | 27.156 | 38.648 | 25.001 | 1.1 | 0.8 | 0.6 | 0.3 | 0.2
213 | 30/07/2025 09:24:07.475 | 98.88 | 63 | 100 | 71 | 51 | 27.751 | 9.577 | 6.937 | 104.835 | 28.124 | 28.075 | 27.186 | 604.018 | 25.606 | 26.188 | 1298.559 | 26.921 | 27.178 | 38.429 | 28.001 | 3.4 | 1.6 | 0.3 | 0.5 | 0.3
214 | 30/07/2025 09:24:09.110 | 98.376 | 62 | 100 | 70 | 50 | 29.529 | 9.57 | 6.937 | 104.885 | 28.14 | 28.061 | 27.164 | 603.882 | 25.631 | 26.215 | 1304.863 | 26.931 | 27.16 | 38.686 | 28.001 | 3.4 | 1.2 | 0.3 | 0.5 | 0.3
215 | 30/07/2025 09:24:10.745 | 98.184 | 63 | 100 | 71 | 52 | 26.547 | 9.583 | 6.937 | 106.385 | 28.114 | 28.057 | 27.177 | 603.879 | 25.625 | 26.204 | 1298.518 | 26.94 | 27.18 | 38.285 | 27.001 | 2.1 | 1.2 | 0 | 0 | 0.2
216 | 30/07/2025 09:24:12.378 | 97.536 | 62 | 100 | 70 | 50 | 29.394 | 9.508 | 6.935 | 108.157 | 28.125 | 28.032 | 27.193 | 604 | 25.632 | 26.214 | 1299.623 | 26.928 | 27.13 | 38.312 | 25.001 | 2.1 | 1.5 | 0 | 0 | 0.2
217 | 30/07/2025 09:24:14.014 | 97.656 | 62 | 100 | 70 | 49 | 28.874 | 9.499 | 6.939 | 109.253 | 28.123 | 28.074 | 27.195 | 603.052 | 25.617 | 26.211 | 1308.004 | 26.889 | 27.166 | 38.503 | 25.001 | 2.1 | 1.5 | 0 | 0 | 0.2
218 | 30/07/2025 09:24:15.649 | 97.368 | 62 | 100 | 69 | 50 | 25.621 | 9.577 | 7.007 | 111.085 | 28.124 | 28.054 | 27.191 | 602.597 | 25.62 | 26.251 | 1303.545 | 26.949 | 27.173 | 38.348 | 26.001 | 2 | 1.1 | 0 | 0.6 | 0.2
219 | 30/07/2025 09:24:17.284 | 98.304 | 63 | 100 | 71 | 50 | 28.243 | 9.569 | 7.007 | 111.165 | 28.115 | 28.053 | 27.176 | 603.403 | 25.643 | 26.228 | 1298.631 | 26.924 | 27.162 | 38.537 | 26.001 | 2 | 1.5 | 0 | 0.6 | 0.2
220 | 30/07/2025 09:24:18.920 | 98.304 | 62 | 100 | 71 | 51 | 26.033 | 9.612 | 7.008 | 110.93 | 28.097 | 28.034 | 27.181 | 602.601 | 25.63 | 26.231 | 1298.554 | 26.942 | 27.154 | 38.358 | 27.001 | 1.7 | 0.7 | 0.6 | 0.3 | 0.1
221 | 30/07/2025 09:24:20.555 | 98.88 | 63 | 100 | 70 | 51 | 27.22 | 9.449 | 7.067 | 112.33 | 28.109 | 28.047 | 27.209 | 602.949 | 25.642 | 26.209 | 1301.053 | 26.918 | 27.142 | 38.496 | 25.001 | 1.7 | 0.9 | 0.6 | 0.3 | 0.1
222 | 30/07/2025 09:24:22.191 | 98.712 | 63 | 100 | 72 | 51 | 29.47 | 9.558 | 7.065 | 113.853 | 28.108 | 28.076 | 27.194 | 603.954 | 25.616 | 26.218 | 1298.85 | 26.904 | 27.174 | 38.423 | 25.001 | 1.7 | 0.9 | 0.6 | 0.3 | 0.1
223 | 30/07/2025 09:24:23.825 | 99.144 | 65 | 100 | 72 | 52 | 28.429 | 9.573 | 7.036 | 115.671 | 28.123 | 28.058 | 27.184 | 603.954 | 25.626 | 26.222 | 1300.808 | 26.946 | 27.156 | 38.596 | 23.001 | 3 | 0.7 | 0.1 | 0.5 | 0.2
224 | 30/07/2025 09:24:25.461 | 98.616 | 63 | 100 | 71 | 51 | 25.547 | 9.576 | 7.034 | 115.544 | 28.128 | 28.06 | 27.186 | 603.938 | 25.626 | 26.214 | 1303.196 | 26.922 | 27.161 | 38.26 | 25.001 | 3 | 1.6 | 0.1 | 0.5 | 0.2
225 | 30/07/2025 09:24:27.097 | 98.664 | 63 | 100 | 70 | 51 | 29.338 | 9.579 | 7.035 | 116.978 | 28.149 | 28.04 | 27.197 | 603.966 | 25.634 | 26.224 | 1298.49 | 26.917 | 27.149 | 38.181 | 27.001 | 3 | 0.8 | 0 | 0.8 | 0.2
226 | 30/07/2025 09:24:28.732 | 98.712 | 64 | 100 | 70 | 51 | 25.739 | 9.667 | 7.035 | 116.702 | 28.122 | 28.063 | 27.194 | 603.973 | 25.612 | 26.216 | 1297.43 | 26.915 | 27.159 | 38.547 | 24.001 | 3 | 1.4 | 0 | 0.8 | 0.2
227 | 30/07/2025 09:24:30.369 | 98.424 | 63 | 100 | 71 | 51 | 27.62 | 9.505 | 7.038 | 116.974 | 28.12 | 28.06 | 27.188 | 603.932 | 25.62 | 26.238 | 1279.078 | 26.922 | 27.176 | 38.52 | 26.001 | 2.3 | 1.3 | 0.6 | 1.1 | 0.2
228 | 30/07/2025 09:24:32.002 | 98.376 | 64 | 100 | 70 | 52 | 29.465 | 9.424 | 7.061 | 118.332 | 28.164 | 28.055 | 27.176 | 603.961 | 25.623 | 26.2 | 1278.447 | 26.926 | 27.162 | 38.41 | 26.001 | 2.3 | 1.3 | 0.6 | 1.1 | 0.2
229 | 30/07/2025 09:24:33.635 | 97.8 | 63 | 100 | 70 | 52 | 27.902 | 9.499 | 7.036 | 118.21 | 28.14 | 28.053 | 27.188 | 603.92 | 25.607 | 26.207 | 1283.754 | 26.929 | 27.172 | 38.143 | 22.001 | 2.3 | 0.6 | 0.6 | 1.1 | 0.2
230 | 30/07/2025 09:24:35.272 | 98.136 | 63 | 100 | 71 | 51 | 25.661 | 9.573 | 7.035 | 119.709 | 28.15 | 28.051 | 27.198 | 603.878 | 25.616 | 26.214 | 1275.645 | 26.92 | 27.145 | 38.482 | 28.001 | 4.5 | 1.6 | 0 | 0.5 | 0.1
231 | 30/07/2025 09:24:36.907 | 97.776 | 63 | 100 | 70 | 51 | 28.843 | 9.575 | 7.06 | 119.533 | 28.141 | 28.077 | 27.19 | 603.909 | 25.612 | 26.196 | 1278.063 | 26.926 | 27.169 | 38.557 | 27.001 | 4.5 | 1 | 0 | 0.5 | 0.1
232 | 30/07/2025 09:24:38.543 | 99.432 | 63 | 100 | 70 | 52 | 25.464 | 9.572 | 7.055 | 121.451 | 28.148 | 28.063 | 27.189 | 603.937 | 25.613 | 26.204 | 1292.735 | 26.923 | 27.156 | 38.439 | 23.001 | 2.3 | 1.1 | 0 | 0 | 0.1
233 | 30/07/2025 09:24:40.177 | 98.952 | 63 | 100 | 70 | 52 | 28.309 | 9.742 | 7.035 | 121.377 | 28.13 | 28.06 | 27.167 | 603.876 | 25.61 | 26.193 | 1306.063 | 26.935 | 27.165 | 38.354 | 23.001 | 2.3 | 1.1 | 0 | 0 | 0.1
234 | 30/07/2025 09:24:41.814 | 99.336 | 65 | 100 | 71 | 52 | 29.52 | 9.431 | 7.036 | 122.402 | 28.129 | 28.04 | 27.202 | 604.057 | 25.627 | 26.2 | 1302.004 | 26.933 | 27.151 | 38.296 | 28.001 | 2.3 | 0.6 | 0 | 0 | 0.1
235 | 30/07/2025 09:24:43.449 | 99.744 | 64 | 100 | 71 | 51 | 27.193 | 9.423 | 7.035 | 122.668 | 28.148 | 28.064 | 27.201 | 604.094 | 25.632 | 26.206 | 1296.867 | 26.904 | 27.162 | 38.569 | 28.001 | 1.9 | 1 | 0 | 0.6 | 0.2
236 | 30/07/2025 09:24:45.086 | 99.336 | 65 | 100 | 71 | 52 | 26.101 | 9.776 | 7.063 | 122.784 | 28.122 | 28.082 | 27.192 | 603.881 | 25.637 | 26.222 | 1295.284 | 26.917 | 27.184 | 38.472 | 28.001 | 1.9 | 1.1 | 0 | 0.6 | 0.2
237 | 30/07/2025 09:24:46.721 | 99.288 | 63 | 100 | 71 | 52 | 28.364 | 9.757 | 7.061 | 122.808 | 28.133 | 28.068 | 27.195 | 604.041 | 25.636 | 26.215 | 1291.6 | 26.918 | 27.169 | 38.496 | 24.001 | 2.3 | 0.8 | 0.6 | 0.5 | 0.2
238 | 30/07/2025 09:24:48.366 | 98.928 | 63 | 100 | 70 | 52 | 25.524 | 9.744 | 7.063 | 122.728 | 28.116 | 28.055 | 27.162 | 603.782 | 25.631 | 26.234 | 1298.404 | 26.947 | 27.176 | 38.403 | 25.001 | 2.3 | 1 | 0.6 | 0.5 | 0.2
239 | 30/07/2025 09:24:50.004 | 98.928 | 64 | 100 | 70 | 52 | 28.708 | 9.806 | 7.061 | 124.234 | 28.128 | 28.043 | 27.196 | 603.96 | 25.64 | 26.239 | 1297.982 | 26.924 | 27.129 | 38.267 | 25.001 | 2.3 | 1 | 0.6 | 0.5 | 0.2
240 | 30/07/2025 09:24:51.640 | 98.64 | 62 | 100 | 70 | 51 | 29.59 | 10.019 | 7.061 | 124.388 | 28.115 | 28.08 | 27.198 | 604.038 | 25.629 | 26.222 | 1300.53 | 26.898 | 27.166 | 38.5 | 30.001 | 3.3 | 1 | 0.6 | 0.8 | 0.2
241 | 30/07/2025 09:24:53.274 | 98.496 | 63 | 99 | 71 | 51 | 26.535 | 9.739 | 7.065 | 124.526 | 28.108 | 28.064 | 27.188 | 603.858 | 25.622 | 26.238 | 1308.229 | 26.949 | 27.166 | 38.441 | 23.001 | 3.3 | 1.4 | 0.6 | 0.8 | 0.2
242 | 30/07/2025 09:24:54.910 | 98.136 | 63 | 100 | 70 | 52 | 29.482 | 9.801 | 7.062 | 125.591 | 28.111 | 28.065 | 27.16 | 602.747 | 25.607 | 26.224 | 1309.193 | 26.935 | 27.17 | 38.293 | 26.001 | 3.9 | 0.7 | 0.6 | 0.5 | 0.2
243 | 30/07/2025 09:24:56.547 | 98.376 | 63 | 100 | 71 | 52 | 27.692 | 9.578 | 7.064 | 126.057 | 28.111 | 28.036 | 27.179 | 602.59 | 25.631 | 26.22 | 1308.406 | 26.931 | 27.159 | 38.314 | 27.001 | 3.9 | 1.4 | 0.6 | 0.5 | 0.2
244 | 30/07/2025 09:24:58.184 | 98.256 | 63 | 100 | 70 | 52 | 25.603 | 9.493 | 7.06 | 125.913 | 28.13 | 28.047 | 27.202 | 602.875 | 25.629 | 26.204 | 1308.142 | 26.923 | 27.14 | 38.293 | 27.001 | 3.9 | 1.4 | 0.6 | 0.5 | 0.2
245 | 30/07/2025 09:24:59.833 | 98.616 | 63 | 100 | 70 | 52 | 28.995 | 9.795 | 7.064 | 126.265 | 28.129 | 28.067 | 27.178 | 602.713 | 25.617 | 26.222 | 1306.078 | 26.92 | 27.185 | 38.766 | 25.001 | 2.1 | 1 | 0.7 | 1.1 | 0.3
246 | 30/07/2025 09:25:01.599 | 98.376 | 62 | 100 | 69 | 51 | 29.415 | 9.573 | 7.062 | 127.675 | 28.148 | 28.058 | 27.177 | 602.735 | 25.628 | 26.224 | 1305.895 | 26.937 | 27.16 | 38.455 | 28.001 | 2.1 | 1.1 | 0.7 | 1.1 | 0.3
247 | 30/07/2025 09:25:03.233 | 98.16 | 63 | 100 | 69 | 52 | 26.01 | 9.577 | 7.036 | 127.437 | 28.132 | 28.049 | 27.177 | 602.775 | 25.626 | 26.216 | 1296.16 | 26.921 | 27.16 | 38.389 | 29.001 | 1.4 | 0.6 | 0.9 | 1 | 0.3
248 | 30/07/2025 09:25:04.868 | 97.584 | 63 | 100 | 70 | 52 | 29.51 | 9.73 | 7.033 | 127.601 | 28.147 | 28.044 | 27.193 | 602.741 | 25.639 | 26.215 | 1298.458 | 26.925 | 27.149 | 38.266 | 26.001 | 1.4 | 0.9 | 0.9 | 1 | 0.3
249 | 30/07/2025 09:25:06.503 | 97.728 | 63 | 100 | 71 | 51 | 27.25 | 9.731 | 7.039 | 127.309 | 28.136 | 28.06 | 27.191 | 602.878 | 25.607 | 26.206 | 1309.552 | 26.92 | 27.164 | 38.473 | 27.001 | 1.9 | 1 | 0 | 0 | 0.2
250 | 30/07/2025 09:25:08.138 | 97.224 | 61 | 100 | 69 | 52 | 26.143 | 9.797 | 7.063 | 128.887 | 28.147 | 28.059 | 27.188 | 602.64 | 25.606 | 26.213 | 1313.161 | 26.897 | 27.171 | 38.545 | 27.001 | 1.9 | 1 | 0 | 0 | 0.2
251 | 30/07/2025 09:25:09.773 | 96.216 | 62 | 100 | 70 | 51 | 29.299 | 9.485 | 7.073 | 129.044 | 28.139 | 28.052 | 27.169 | 602.836 | 25.615 | 26.195 | 1293.199 | 26.929 | 27.164 | 38.478 | 29.001 | 1.9 | 2 | 0 | 0 | 0.2
252 | 30/07/2025 09:25:11.407 | 96.48 | 62 | 100 | 70 | 51 | 29.279 | 9.502 | 7.063 | 128.824 | 28.123 | 28.04 | 27.182 | 603.011 | 25.59 | 26.201 | 1296.226 | 26.953 | 27.166 | 38.281 | 21.001 | 1.6 | 2.1 | 0 | 1.1 | 0.2
253 | 30/07/2025 09:25:13.042 | 97.296 | 61 | 100 | 71 | 51 | 25.735 | 9.577 | 7.062 | 128.777 | 28.133 | 28.059 | 27.191 | 602.606 | 25.629 | 26.184 | 1307.464 | 26.914 | 27.134 | 38.368 | 21.001 | 1.6 | 2.1 | 0 | 1.1 | 0.2
254 | 30/07/2025 09:25:14.679 | 96.912 | 61 | 100 | 70 | 52 | 29.614 | 9.571 | 7.067 | 128.733 | 28.13 | 28.067 | 27.192 | 602.655 | 25.616 | 26.198 | 1304.288 | 26.927 | 27.172 | 38.544 | 22.001 | 2.7 | 1.6 | 1.2 | 0 | 0.1
255 | 30/07/2025 09:25:16.315 | 97.728 | 63 | 100 | 70 | 52 | 26.618 | 9.798 | 7.074 | 129.165 | 28.152 | 28.064 | 27.183 | 603.981 | 25.642 | 26.201 | 1318.164 | 26.908 | 27.168 | 38.509 | 25.001 | 2.7 | 1.7 | 1.2 | 0 | 0.1
256 | 30/07/2025 09:25:17.952 | 96.96 | 62 | 100 | 71 | 53 | 26.501 | 9.729 | 7.074 | 128.823 | 28.117 | 28.057 | 27.161 | 603.841 | 25.625 | 26.203 | 1317.01 | 26.932 | 27.169 | 38.418 | 25.001 | 2.7 | 1.7 | 1.2 | 0 | 0.1
257 | 30/07/2025 09:25:19.588 | 97.512 | 62 | 100 | 71 | 52 | 29.367 | 9.727 | 7.086 | 128.873 | 28.132 | 28.046 | 27.19 | 603.894 | 25.628 | 26.232 | 1318.458 | 26.931 | 27.142 | 38.336 | 28.001 | 2.5 | 2.1 | 0.6 | 0.1 | 0.1
258 | 30/07/2025 09:25:21.223 | 97.296 | 62 | 100 | 70 | 52 | 28.867 | 9.574 | 7.1 | 128.755 | 28.14 | 28.066 | 27.203 | 604.099 | 25.629 | 26.213 | 1323.18 | 26.907 | 27.147 | 38.437 | 22.001 | 2.5 | 1.7 | 0.6 | 0.1 | 0.1
259 | 30/07/2025 09:25:22.859 | 97.272 | 62 | 100 | 71 | 52 | 29.055 | 9.776 | 7.103 | 128.967 | 28.113 | 28.06 | 27.186 | 603.879 | 25.627 | 26.231 | 1327.788 | 26.896 | 27.168 | 38.6 | 28.001 | 2.6 | 1.1 | 0.9 | 0.5 | 0.2
260 | 30/07/2025 09:25:24.500 | 97.536 | 63 | 100 | 70 | 52 | 29.493 | 9.73 | 7.123 | 128.986 | 28.102 | 28.072 | 27.205 | 603.975 | 25.628 | 26.218 | 1328.046 | 26.922 | 27.163 | 38.306 | 28.001 | 2.6 | 0.6 | 0.9 | 0.5 | 0.2
261 | 30/07/2025 09:25:26.135 | 97.944 | 63 | 100 | 70 | 52 | 26.059 | 9.796 | 7.074 | 128.848 | 28.09 | 28.06 | 27.161 | 603.73 | 25.618 | 26.24 | 1337.01 | 26.954 | 27.16 | 38.443 | 28.001 | 2.6 | 0.6 | 0.9 | 0.5 | 0.2
262 | 30/07/2025 09:25:27.771 | 98.064 | 64 | 100 | 70 | 52 | 27.032 | 9.576 | 7.062 | 128.988 | 28.101 | 28.036 | 27.201 | 604.107 | 25.637 | 26.219 | 1340.65 | 26.923 | 27.133 | 38.137 | 27.001 | 2.6 | 0.3 | 0 | 0.2 | 0.1
263 | 30/07/2025 09:25:29.406 | 99.72 | 65 | 100 | 70 | 53 | 29.412 | 9.753 | 7.063 | 128.707 | 28.095 | 28.084 | 27.187 | 603.976 | 25.625 | 26.221 | 1337.68 | 26.904 | 27.16 | 38.604 | 27.001 | 2.6 | 0.6 | 0 | 0.2 | 0.1
264 | 30/07/2025 09:25:31.041 | 100.248 | 66 | 100 | 70 | 53 | 28.222 | 9.428 | 7.037 | 128.916 | 28.115 | 28.067 | 27.177 | 603.821 | 25.629 | 26.238 | 1327.304 | 26.929 | 27.161 | 38.581 | 27.001 | 3.7 | 0.6 | 0.6 | 1 | 0.2
265 | 30/07/2025 09:25:32.676 | 100.248 | 65 | 100 | 70 | 52 | 29.185 | 9.429 | 7.036 | 128.901 | 28.113 | 28.068 | 27.177 | 603.832 | 25.616 | 26.224 | 1318.968 | 26.941 | 27.178 | 38.555 | 25.001 | 3.7 | 0.7 | 0.6 | 1 | 0.2
266 | 30/07/2025 09:25:34.312 | 98.736 | 63 | 100 | 71 | 52 | 29.215 | 9.553 | 7.063 | 128.892 | 28.127 | 28.047 | 27.165 | 603.749 | 25.629 | 26.22 | 1328.219 | 26.931 | 27.154 | 38.283 | 27.001 | 4.4 | 0.1 | 0.1 | 0 | 0.2
267 | 30/07/2025 09:25:35.949 | 98.568 | 63 | 100 | 70 | 52 | 25.655 | 9.734 | 7.059 | 128.973 | 28.143 | 28.06 | 27.212 | 604.139 | 25.623 | 26.214 | 1318.327 | 26.923 | 27.152 | 38.285 | 27.001 | 4.4 | 0.1 | 0.1 | 0 | 0.2
268 | 30/07/2025 09:25:37.587 | 97.752 | 62 | 100 | 70 | 52 | 27.593 | 9.5 | 7.065 | 128.706 | 28.143 | 28.07 | 27.187 | 603.869 | 25.608 | 26.221 | 1309.75 | 26.923 | 27.177 | 38.589 | 28.001 | 4.4 | 1.1 | 0.1 | 0 | 0.2
269 | 30/07/2025 09:25:39.222 | 97.56 | 63 | 99 | 70 | 52 | 29.402 | 9.722 | 6.988 | 130.702 | 28.14 | 28.066 | 27.178 | 603.875 | 25.635 | 26.213 | 1298.504 | 26.931 | 27.167 | 38.443 | 30.001 | 2 | 1.2 | 0.1 | 1.2 | 0.2
270 | 30/07/2025 09:25:40.857 | 97.44 | 62 | 100 | 70 | 52 | 26.596 | 9.767 | 6.99 | 130.435 | 28.129 | 28.057 | 27.155 | 603.746 | 25.602 | 26.224 | 1296.832 | 26.944 | 27.178 | 38.449 | 32.001 | 2 | 0.8 | 0.1 | 1.2 | 0.2
271 | 30/07/2025 09:25:42.494 | 96.816 | 61 | 100 | 70 | 52 | 29.366 | 9.79 | 6.987 | 130.495 | 28.151 | 28.047 | 27.186 | 603.934 | 25.621 | 26.2 | 1308.001 | 26.922 | 27.151 | 38.354 | 32.001 | 2.9 | 0.1 | 0.7 | 0.5 | 0.2
272 | 30/07/2025 09:25:44.128 | 97.2 | 62 | 100 | 70 | 52 | 28.84 | 9.576 | 7 | 130.078 | 28.129 | 28.062 | 27.196 | 603.889 | 25.59 | 26.208 | 1307.833 | 26.922 | 27.164 | 38.249 | 32.001 | 2.9 | 0.1 | 0.7 | 0.5 | 0.2
273 | 30/07/2025 09:25:45.761 | 97.344 | 62 | 100 | 71 | 52 | 25.555 | 9.432 | 7.036 | 130.369 | 28.136 | 28.064 | 27.186 | 603.897 | 25.616 | 26.199 | 1310.456 | 26.901 | 27.171 | 38.371 | 23.001 | 2.9 | 0.6 | 0.7 | 0.5 | 0.2
274 | 30/07/2025 09:25:47.397 | 97.44 | 62 | 100 | 71 | 52 | 28.23 | 9.623 | 7.034 | 130.418 | 28.131 | 28.079 | 27.175 | 603.977 | 25.618 | 26.188 | 1308.335 | 26.941 | 27.163 | 38.426 | 25.001 | 1.3 | 1 | 0.6 | 1 | 0.2
275 | 30/07/2025 09:25:49.033 | 98.688 | 64 | 100 | 70 | 52 | 29.565 | 9.428 | 7.037 | 130.299 | 28.121 | 28.044 | 27.16 | 603.923 | 25.604 | 26.203 | 1305.875 | 26.947 | 27.169 | 38.237 | 22.001 | 1.3 | 1.6 | 0.6 | 1 | 0.2
276 | 30/07/2025 09:25:50.666 | 99.024 | 65 | 100 | 70 | 52 | 27.057 | 9.448 | 7.033 | 130.401 | 28.128 | 28.054 | 27.191 | 604.045 | 25.623 | 26.198 | 1305.734 | 26.928 | 27.145 | 38.204 | 27.001 | 2 | 0.7 | 0.6 | 0 | 0.2
277 | 30/07/2025 09:25:52.302 | 98.688 | 64 | 100 | 70 | 51 | 29.373 | 9.799 | 7.012 | 130.184 | 28.131 | 28.068 | 27.187 | 603.891 | 25.617 | 26.225 | 1312.8 | 26.914 | 27.168 | 38.358 | 24.001 | 2 | 1.9 | 0.6 | 0 | 0.2
278 | 30/07/2025 09:25:53.938 | 99.432 | 65 | 100 | 71 | 52 | 28.444 | 9.725 | 6.988 | 130.563 | 28.144 | 28.064 | 27.192 | 603.943 | 25.626 | 26.212 | 1321.814 | 26.901 | 27.162 | 38.624 | 24.001 | 2 | 1.9 | 0.6 | 0 | 0.2
279 | 30/07/2025 09:25:55.572 | 99.816 | 65 | 100 | 70 | 52 | 25.525 | 9.711 | 6.989 | 130.237 | 28.106 | 28.065 | 27.164 | 603.907 | 25.607 | 26.234 | 1318.405 | 26.941 | 27.182 | 38.483 | 30.001 | 1.3 | 1.5 | 0.7 | 1 | 0.2
280 | 30/07/2025 09:25:57.207 | 99.768 | 65 | 100 | 70 | 52 | 28.692 | 9.801 | 6.997 | 130.456 | 28.114 | 28.037 | 27.185 | 603.869 | 25.624 | 26.242 | 1313.144 | 26.921 | 27.153 | 38.387 | 31.001 | 1.3 | 1.5 | 0.7 | 1 | 0.2
281 | 30/07/2025 09:25:58.843 | 99.312 | 63 | 100 | 71 | 53 | 25.72 | 9.739 | 7.029 | 130.252 | 28.11 | 28.031 | 27.194 | 603.916 | 25.628 | 26.231 | 1308.748 | 26.933 | 27.158 | 38.191 | 28.001 | 2 | 0.7 | 0.6 | 0 | 0.2
282 | 30/07/2025 09:26:00.478 | 99.024 | 65 | 100 | 71 | 52 | 27.624 | 9.494 | 7.02 | 130.224 | 28.109 | 28.066 | 27.176 | 603.923 | 25.631 | 26.222 | 1306.448 | 26.898 | 27.171 | 38.758 | 27.001 | 2 | 1.1 | 0.6 | 0 | 0.2
283 | 30/07/2025 09:26:02.113 | 98.832 | 65 | 100 | 70 | 52 | 29.47 | 9.87 | 7.007 | 130.461 | 28.109 | 28.075 | 27.195 | 604.038 | 25.639 | 26.218 | 1314.429 | 26.935 | 27.168 | 38.54 | 27.001 | 2 | 1.1 | 0.6 | 0 | 0.2
284 | 30/07/2025 09:26:03.750 | 98.568 | 64 | 100 | 70 | 52 | 27.694 | 9.58 | 7.036 | 131.873 | 28.098 | 28.063 | 27.162 | 603.736 | 25.622 | 26.238 | 1316.129 | 26.95 | 27.165 | 38.385 | 30.001 | 2.1 | 0.4 | 0 | 0.6 | 0.2
285 | 30/07/2025 09:26:05.388 | 98.76 | 64 | 100 | 71 | 53 | 25.562 | 9.427 | 7.022 | 131.928 | 28.141 | 28.041 | 27.198 | 604.192 | 25.64 | 26.221 | 1319.81 | 26.93 | 27.146 | 38.189 | 34.001 | 2.1 | 0.9 | 0 | 0.6 | 0.2
286 | 30/07/2025 09:26:07.024 | 98.568 | 64 | 100 | 71 | 53 | 28.935 | 9.329 | 7.006 | 131.655 | 28.122 | 28.079 | 27.182 | 604.054 | 25.618 | 26.216 | 1327.379 | 26.912 | 27.174 | 38.518 | 25.001 | 2.1 | 0.8 | 0.6 | 0.5 | 0.2
287 | 30/07/2025 09:26:08.659 | 98.904 | 65 | 100 | 70 | 53 | 25.4 | 9.717 | 7.006 | 131.907 | 28.143 | 28.068 | 27.189 | 604.006 | 25.634 | 26.21 | 1324.461 | 26.889 | 27.179 | 38.51 | 25.001 | 2.1 | 0.7 | 0.6 | 0.5 | 0.2
288 | 30/07/2025 09:26:10.295 | 99.528 | 65 | 100 | 70 | 52 | 28.066 | 9.718 | 7.007 | 131.745 | 28.13 | 28.074 | 27.165 | 603.809 | 25.615 | 26.217 | 1316.201 | 26.946 | 27.187 | 38.55 | 29.001 | 2.3 | 1.6 | 0.9 | 0.6 | 0.2
289 | 30/07/2025 09:26:11.929 | 100.224 | 66 | 100 | 71 | 52 | 29.445 | 9.571 | 7.031 | 131.97 | 28.153 | 28.048 | 27.17 | 603.792 | 25.631 | 26.231 | 1320.915 | 26.925 | 27.156 | 38.421 | 29.001 | 2.3 | 1.6 | 0.9 | 0.6 | 0.2
290 | 30/07/2025 09:26:13.566 | 100.488 | 66 | 100 | 70 | 53 | 27.196 | 9.504 | 7.033 | 131.925 | 28.136 | 28.05 | 27.207 | 604.189 | 25.598 | 26.208 | 1304.822 | 26.927 | 27.142 | 38.364 | 29.001 | 2.3 | 1.8 | 0.9 | 0.6 | 0.2
291 | 30/07/2025 09:26:15.203 | 100.248 | 66 | 100 | 71 | 53 | 26.076 | 9.712 | 7.036 | 131.737 | 28.126 | 28.067 | 27.176 | 603.804 | 25.602 | 26.218 | 1291.113 | 26.911 | 27.17 | 38.542 | 30.001 | 2.3 | 0.9 | 0.3 | 0.5 | 0.2
292 | 30/07/2025 09:26:16.839 | 100.344 | 65 | 100 | 71 | 53 | 28.349 | 9.803 | 7.025 | 131.95 | 28.132 | 28.079 | 27.186 | 603.88 | 25.6 | 26.203 | 1288.441 | 26.909 | 27.159 | 38.368 | 26.001 | 2.3 | 0.6 | 0.3 | 0.5 | 0.2
293 | 30/07/2025 09:26:18.476 | 100.68 | 66 | 100 | 70 | 53 | 25.449 | 9.728 | 7.008 | 131.927 | 28.132 | 28.071 | 27.15 | 603.697 | 25.593 | 26.202 | 1278.608 | 26.94 | 27.166 | 38.464 | 24.001 | 2.5 | 0.7 | 0.6 | 0.5 | 0.2
294 | 30/07/2025 09:26:20.111 | 100.584 | 65 | 100 | 71 | 52 | 28.606 | 9.727 | 7.005 | 131.923 | 28.144 | 28.05 | 27.19 | 603.94 | 25.623 | 26.185 | 1278.531 | 26.938 | 27.146 | 38.23 | 24.001 | 2.5 | 0.7 | 0.6 | 0.5 | 0.2
295 | 30/07/2025 09:26:21.748 | 100.824 | 66 | 100 | 70 | 53 | 29.612 | 9.749 | 7.006 | 133.051 | 28.132 | 28.064 | 27.19 | 603.97 | 25.616 | 26.199 | 1283.462 | 26.931 | 27.158 | 38.521 | 29.001 | 2.5 | 0.6 | 0.6 | 0.5 | 0.2
296 | 30/07/2025 09:26:23.383 | 100.152 | 65 | 100 | 71 | 51 | 26.591 | 9.841 | 7.035 | 133.26 | 28.13 | 28.065 | 27.185 | 604.009 | 25.635 | 26.197 | 1288.699 | 26.901 | 27.179 | 38.515 | 28.001 | 1.5 | 1 | 0 | 0.2 | 0.2
297 | 30/07/2025 09:26:25.017 | 100.272 | 66 | 100 | 70 | 52 | 26.568 | 9.594 | 7.059 | 133.4 | 28.134 | 28.079 | 27.173 | 603.889 | 25.63 | 26.204 | 1291.827 | 26.93 | 27.173 | 38.394 | 26.001 | 1.5 | 0.6 | 0 | 0.2 | 0.2
298 | 30/07/2025 09:26:26.652 | 100.584 | 66 | 100 | 71 | 53 | 27.885 | 9.708 | 7.062 | 133.546 | 28.122 | 28.056 | 27.163 | 603.75 | 25.642 | 26.214 | 1280.614 | 26.936 | 27.158 | 38.482 | 25.001 | 3.2 | 1.3 | 0.6 | 0.5 | 0.3
299 | 30/07/2025 09:26:28.288 | 100.44 | 66 | 100 | 70 | 53 | 25.666 | 9.751 | 7.07 | 133.359 | 28.116 | 28.041 | 27.191 | 603.995 | 25.609 | 26.226 | 1278.29 | 26.927 | 27.145 | 38.247 | 26.001 | 3.2 | 1.2 | 0.6 | 0.5 | 0.3
300 | 30/07/2025 09:26:29.925 | 100.296 | 65 | 100 | 71 | 53 | 29.078 | 9.578 | 7.073 | 133.072 | 28.109 | 28.066 | 27.187 | 603.9 | 25.629 | 26.237 | 1281.553 | 26.918 | 27.155 | 38.373 | 26.001 | 3.2 | 1.2 | 0.6 | 0.5 | 0.3
301 | 30/07/2025 09:26:31.562 | 100.44 | 65 | 100 | 70 | 52 | 29.514 | 9.72 | 7.063 | 133.46 | 28.126 | 28.073 | 27.187 | 603.979 | 25.628 | 26.217 | 1290.909 | 26.91 | 27.172 | 38.443 | 30.001 | 1.7 | 1.7 | 0.6 | 0.8 | 0.2
302 | 30/07/2025 09:26:33.201 | 101.208 | 66 | 100 | 70 | 53 | 26.165 | 9.729 | 7.062 | 133.362 | 28.117 | 28.078 | 27.16 | 603.722 | 25.616 | 26.21 | 1297.724 | 26.951 | 27.179 | 38.374 | 25.001 | 1.7 | 1.3 | 0.6 | 0.8 | 0.2
303 | 30/07/2025 09:26:34.836 | 100.416 | 65 | 100 | 71 | 53 | 29.546 | 9.643 | 7.061 | 133.395 | 28.107 | 28.057 | 27.177 | 603.783 | 25.619 | 26.213 | 1307.831 | 26.933 | 27.158 | 38.457 | 28.001 | 2.3 | 1.1 | 0.9 | 0.4 | 0.3
304 | 30/07/2025 09:26:36.472 | 99.672 | 66 | 100 | 71 | 52 | 27.192 | 9.765 | 7.035 | 133.236 | 28.111 | 28.03 | 27.186 | 603.863 | 25.613 | 26.23 | 1308.682 | 26.943 | 27.145 | 38.132 | 33.001 | 2.3 | 1.6 | 0.9 | 0.4 | 0.3
305 | 30/07/2025 09:26:38.106 | 99.888 | 65 | 100 | 71 | 52 | 25.947 | 9.756 | 7.034 | 133.229 | 28.114 | 28.064 | 27.193 | 603.884 | 25.641 | 26.22 | 1310.492 | 26.893 | 27.16 | 38.553 | 33.001 | 2.3 | 1.6 | 0.9 | 0.4 | 0.3
306 | 30/07/2025 09:26:39.741 | 100.152 | 65 | 100 | 71 | 53 | 29.186 | 9.733 | 7.035 | 133.451 | 28.12 | 28.076 | 27.18 | 603.88 | 25.608 | 26.211 | 1313.083 | 26.917 | 27.173 | 38.486 | 24.001 | 3.8 | 0.8 | 0.6 | 0.5 | 0.3
307 | 30/07/2025 09:26:41.376 | 99.528 | 64 | 100 | 71 | 53 | 29.228 | 9.737 | 7.038 | 133.358 | 28.121 | 28.061 | 27.157 | 603.751 | 25.626 | 26.234 | 1308.741 | 26.941 | 27.171 | 38.487 | 28.001 | 3.8 | 0.6 | 0.6 | 0.5 | 0.3
308 | 30/07/2025 09:26:43.014 | 99.672 | 66 | 100 | 70 | 53 | 25.696 | 9.634 | 7.035 | 133.478 | 28.149 | 28.044 | 27.196 | 604.006 | 25.624 | 26.209 | 1306.152 | 26.925 | 27.148 | 38.248 | 31.001 | 1.8 | 1.7 | 0.6 | 0.4 | 0.3
309 | 30/07/2025 09:26:44.649 | 99.336 | 64 | 100 | 70 | 52 | 29.546 | 9.58 | 7.034 | 133.164 | 28.14 | 28.056 | 27.179 | 603.946 | 25.625 | 26.221 | 1300.67 | 26.935 | 27.144 | 38.504 | 28.001 | 1.8 | 1.7 | 0.6 | 0.4 | 0.3
310 | 30/07/2025 09:26:46.289 | 99 | 65 | 100 | 69 | 52 | 26.688 | 9.722 | 7.034 | 133.274 | 28.135 | 28.076 | 27.192 | 605.139 | 25.613 | 26.198 | 1304.001 | 26.905 | 27.169 | 38.458 | 28.001 | 3.8 | 0.8 | 0.6 | 0.2 | 0.2
311 | 30/07/2025 09:26:47.925 | 98.448 | 64 | 100 | 70 | 52 | 26.506 | 9.813 | 7.036 | 133.271 | 28.135 | 28.074 | 27.166 | 604.976 | 25.61 | 26.2 | 1318.279 | 26.952 | 27.177 | 38.549 | 28.001 | 3.8 | 0.8 | 0.6 | 0.2 | 0.2
312 | 30/07/2025 09:26:49.561 | 98.832 | 65 | 100 | 70 | 52 | 29.366 | 9.584 | 7.006 | 133.496 | 28.146 | 28.056 | 27.163 | 604.937 | 25.614 | 26.207 | 1327.506 | 26.931 | 27.163 | 38.348 | 26.001 | 3.8 | 0.9 | 0.6 | 0.2 | 0.2
313 | 30/07/2025 09:26:51.196 | 99.072 | 64 | 100 | 71 | 52 | 28.78 | 9.583 | 7.005 | 133.244 | 28.132 | 28.048 | 27.208 | 606.469 | 25.595 | 26.189 | 1330.264 | 26.931 | 27.151 | 38.281 | 26.001 | 2.4 | 0.7 | 0 | 0 | 0.2
314 | 30/07/2025 09:26:52.832 | 98.4 | 64 | 100 | 71 | 51 | 29.023 | 9.575 | 7.004 | 133.236 | 28.144 | 28.056 | 27.192 | 605.122 | 25.63 | 26.196 | 1332.691 | 26.918 | 27.151 | 38.534 | 25.001 | 2.4 | 0.7 | 0 | 0 | 0.2
315 | 30/07/2025 09:26:54.466 | 98.76 | 65 | 100 | 70 | 52 | 29.48 | 9.799 | 7.007 | 133.257 | 28.118 | 28.073 | 27.181 | 604.843 | 25.603 | 26.183 | 1333.801 | 26.906 | 27.18 | 38.523 | 25.001 | 2.9 | 0.6 | 0.6 | 0.3 | 0.2
316 | 30/07/2025 09:26:56.102 | 98.376 | 65 | 100 | 70 | 53 | 26.064 | 9.501 | 6.99 | 134.82 | 28.122 | 28.055 | 27.156 | 603.686 | 25.614 | 26.204 | 1328.735 | 26.938 | 27.163 | 38.564 | 25.001 | 2.9 | 0.6 | 0.6 | 0.3 | 0.2
317 | 30/07/2025 09:26:57.740 | 98.4 | 63 | 100 | 71 | 52 | 27.041 | 9.713 | 6.996 | 134.771 | 28.139 | 28.049 | 27.193 | 603.903 | 25.627 | 26.19 | 1328.456 | 26.92 | 27.149 | 38.415 | 29.001 | 2.9 | 1.5 | 0.6 | 0.3 | 0.2
318 | 30/07/2025 09:26:59.374 | 98.472 | 63 | 100 | 71 | 52 | 29.42 | 9.84 | 7.007 | 134.625 | 28.122 | 28.05 | 27.187 | 604.006 | 25.633 | 26.206 | 1318.412 | 26.946 | 27.165 | 38.521 | 29.001 | 3 | 1.3 | 0.9 | 0.5 | 0.2
319 | 30/07/2025 09:27:01.009 | 98.472 | 64 | 100 | 71 | 52 | 28.439 | 9.8 | 7.008 | 133.334 | 28.116 | 28.066 | 27.187 | 603.974 | 25.64 | 26.217 | 1318.502 | 26.895 | 27.171 | 38.548 | 28.001 | 3 | 1.3 | 0.9 | 0.5 | 0.2
320 | 30/07/2025 09:27:02.645 | 98.664 | 64 | 100 | 71 | 52 | 29.285 | 9.729 | 7.008 | 133.317 | 28.114 | 28.058 | 27.175 | 603.85 | 25.632 | 26.226 | 1318.509 | 26.94 | 27.175 | 38.584 | 22.001 | 3 | 1.3 | 0.1 | 0 | 0.2
321 | 30/07/2025 09:27:04.281 | 98.976 | 64 | 100 | 71 | 54 | 29.316 | 9.579 | 7.006 | 133.541 | 28.138 | 28.062 | 27.152 | 603.774 | 25.641 | 26.228 | 1321.34 | 26.93 | 27.167 | 38.463 | 28.001 | 3 | 0.7 | 0.1 | 0 | 0.2
322 | 30/07/2025 09:27:05.918 | 98.352 | 64 | 100 | 70 | 52 | 25.738 | 9.823 | 7.018 | 133.302 | 28.1 | 28.043 | 27.04 | 603.86 | 25.615 | 26.218 | 1318.359 | 26.938 | 27.152 | 38.247 | 28.001 | 3 | 0.7 | 0.1 | 0 | 0.2
323 | 30/07/2025 09:27:07.557 | 98.808 | 64 | 100 | 70 | 52 | 27.654 | 9.576 | 7.033 | 133.112 | 28.095 | 28.058 | 27.047 | 603.914 | 25.622 | 26.238 | 1312.997 | 26.909 | 27.155 | 38.387 | 25.001 | 1.7 | 1 | 0.6 | 0.5 | 0.1
324 | 30/07/2025 09:27:09.190 | 98.376 | 65 | 100 | 70 | 51 | 29.426 | 9.574 | 7.006 | 133.311 | 28.099 | 28.072 | 27.164 | 603.971 | 25.616 | 26.219 | 1308.162 | 26.892 | 27.169 | 38.463 | 27.001 | 1.7 | 2.2 | 0.6 | 0.5 | 0.1
325 | 30/07/2025 09:27:10.826 | 98.304 | 65 | 100 | 71 | 52 | 26.493 | 9.726 | 7.007 | 133.289 | 28.093 | 28.061 | 27.037 | 603.808 | 25.631 | 26.228 | 1308.398 | 26.926 | 27.173 | 38.596 | 26.001 | 2.7 | 1.5 | 0.9 | 1 | 0.2
326 | 30/07/2025 09:27:12.463 | 98.568 | 65 | 100 | 71 | 52 | 29.333 | 9.662 | 7.061 | 133.422 | 28.103 | 28.058 | 27.162 | 603.913 | 25.616 | 26.215 | 1308.193 | 26.927 | 27.163 | 38.286 | 32.001 | 2.7 | 1.4 | 0.9 | 1 | 0.2
327 | 30/07/2025 09:27:14.099 | 98.712 | 64 | 100 | 71 | 51 | 28.91 | 9.432 | 7.063 | 133.17 | 28.113 | 28.043 | 27.179 | 603.874 | 25.613 | 26.212 | 1308.327 | 26.963 | 27.148 | 38.17 | 32.001 | 2.7 | 1.4 | 0.9 | 1 | 0.2
328 | 30/07/2025 09:27:15.733 | 98.352 | 64 | 100 | 71 | 53 | 25.48 | 9.569 | 7.06 | 133.119 | 28.145 | 28.079 | 27.18 | 603.892 | 25.647 | 26.205 | 1315.579 | 26.907 | 27.16 | 38.711 | 25.001 | 4.3 | 0.9 | 0 | 0.5 | 0.1
329 | 30/07/2025 09:27:17.371 | 98.952 | 65 | 100 | 70 | 52 | 28.15 | 9.728 | 7.062 | 133.426 | 28.132 | 28.075 | 27.185 | 603.786 | 25.614 | 26.211 | 1328.626 | 26.929 | 27.177 | 38.412 | 26.001 | 4.3 | 1.7 | 0 | 0.5 | 0.1
330 | 30/07/2025 09:27:19.008 | 98.784 | 65 | 100 | 71 | 52 | 26.188 | 9.871 | 7.061 | 133.372 | 28.146 | 28.072 | 27.17 | 603.844 | 25.609 | 26.206 | 1335.555 | 26.928 | 27.16 | 38.427 | 27.001 | 3 | 0.3 | 0.1 | 0.6 | 0.1
331 | 30/07/2025 09:27:20.643 | 99.288 | 66 | 100 | 70 | 53 | 27.079 | 9.506 | 7.007 | 133.236 | 28.137 | 28.061 | 27.176 | 603.832 | 25.609 | 26.206 | 1333.668 | 26.94 | 27.174 | 38.276 | 27.001 | 3 | 0.6 | 0.1 | 0.6 | 0.1
332 | 30/07/2025 09:27:22.278 | 99.648 | 65 | 100 | 70 | 52 | 29.378 | 9.725 | 6.988 | 133.237 | 28.132 | 28.048 | 27.041 | 603.853 | 25.611 | 26.217 | 1316.344 | 26.922 | 27.139 | 38.429 | 28.001 | 1.5 | 2 | 0.6 | 0.5 | 0.1
333 | 30/07/2025 09:27:23.914 | 99.552 | 66 | 100 | 71 | 53 | 28.36 | 9.872 | 6.988 | 133.092 | 28.139 | 28.077 | 27.061 | 603.997 | 25.6 | 26.193 | 1312.853 | 26.9 | 27.168 | 38.641 | 28.001 | 1.5 | 2 | 0.6 | 0.5 | 0.1
334 | 30/07/2025 09:27:25.553 | 99.36 | 65 | 100 | 70 | 52 | 25.502 | 9.875 | 6.99 | 133.351 | 28.137 | 28.065 | 27.162 | 603.755 | 25.62 | 26.205 | 1306.147 | 26.953 | 27.168 | 38.538 | 29.001 | 1.5 | 1.3 | 0.6 | 0.5 | 0.1
335 | 30/07/2025 09:27:27.193 | 98.736 | 65 | 100 | 70 | 52 | 28.553 | 9.857 | 7.018 | 133.523 | 28.137 | 28.065 | 27.016 | 603.818 | 25.62 | 26.207 | 1296.409 | 26.926 | 27.157 | 38.41 | 26.001 | 2.7 | 1.2 | 0 | 0 | 0.1
336 | 30/07/2025 09:27:28.827 | 98.832 | 65 | 100 | 71 | 52 | 25.71 | 9.733 | 7.073 | 133.214 | 28.127 | 28.042 | 27.042 | 603.931 | 25.601 | 26.207 | 1293.758 | 26.941 | 27.154 | 38.243 | 26.001 | 2.7 | 0.7 | 0 | 0 | 0.1
337 | 30/07/2025 09:27:30.463 | 98.256 | 65 | 100 | 70 | 52 | 27.54 | 9.552 | 7.038 | 133.151 | 28.135 | 28.061 | 27.054 | 603.965 | 25.62 | 26.174 | 1288.526 | 26.919 | 27.137 | 38.4 | 25.001 | 2.8 | 1.2 | 0.6 | 0.5 | 0.2
338 | 30/07/2025 09:27:32.099 | 98.568 | 65 | 100 | 70 | 51 | 29.482 | 9.731 | 7.007 | 133.17 | 28.116 | 28.07 | 27.047 | 603.902 | 25.613 | 26.2 | 1280.515 | 26.89 | 27.186 | 38.638 | 25.001 | 2.8 | 1.2 | 0.6 | 0.5 | 0.2
339 | 30/07/2025 09:27:33.734 | 98.136 | 65 | 100 | 72 | 52 | 27.839 | 9.728 | 7.006 | 133.42 | 28.125 | 28.062 | 27.022 | 603.752 | 25.628 | 26.215 | 1280.423 | 26.936 | 27.148 | 38.443 | 28.001 | 2.8 | 0.7 | 0.6 | 0.5 | 0.2
340 | 30/07/2025 09:27:35.368 | 97.992 | 64 | 100 | 71 | 52 | 25.682 | 9.73 | 6.976 | 133.343 | 28.132 | 28.054 | 27.054 | 603.845 | 25.625 | 26.206 | 1285.885 | 26.927 | 27.16 | 38.267 | 28.001 | 3 | 2.3 | 0.9 | 0.5 | 0.2
341 | 30/07/2025 09:27:37.001 | 97.464 | 63 | 100 | 70 | 52 | 29.005 | 9.587 | 6.937 | 133.065 | 28.111 | 28.05 | 27.184 | 603.869 | 25.616 | 26.236 | 1278.139 | 26.943 | 27.153 | 38.362 | 26.001 | 3 | 0.7 | 0.9 | 0.5 | 0.2
342 | 30/07/2025 09:27:38.637 | 97.872 | 64 | 100 | 70 | 52 | 25.443 | 9.609 | 6.902 | 133.027 | 28.111 | 28.07 | 27.189 | 603.815 | 25.607 | 26.226 | 1287.572 | 26.902 | 27.159 | 38.484 | 27.001 | 3.5 | 1 | 0.3 | 0.5 | 0.2
343 | 30/07/2025 09:27:40.276 | 97.656 | 64 | 100 | 70 | 51 | 28.186 | 9.725 | 6.832 | 133.381 | 28.104 | 28.063 | 27.028 | 603.806 | 25.621 | 26.237 | 1288.524 | 26.921 | 27.174 | 38.526 | 26.001 | 3.5 | 0.8 | 0.3 | 0.5 | 0.2
344 | 30/07/2025 09:27:41.909 | 97.512 | 65 | 100 | 70 | 52 | 29.52 | 9.813 | 6.899 | 133.438 | 28.112 | 28.065 | 27.011 | 603.838 | 25.647 | 26.214 | 1291.196 | 26.929 | 27.16 | 38.581 | 26.001 | 3.5 | 0.8 | 0.3 | 0.5 | 0.2
345 | 30/07/2025 09:27:43.551 | 97.584 | 64 | 100 | 70 | 52 | 27.174 | 9.912 | 6.91 | 133.214 | 28.085 | 28.04 | 27.031 | 603.89 | 25.616 | 26.216 | 1288.535 | 26.935 | 27.163 | 38.136 | 28.001 | 2.6 | 0.6 | 0.7 | 0 | 0.3
346 | 30/07/2025 09:27:45.186 | 97.512 | 63 | 100 | 70 | 52 | 26.079 | 9.803 | 6.936 | 133.123 | 28.106 | 28.056 | 27.031 | 603.89 | 25.617 | 26.224 | 1298.311 | 26.915 | 27.153 | 38.575 | 26.001 | 2.6 | 0 | 0.7 | 0 | 0.3
347 | 30/07/2025 09:27:46.823 | 98.28 | 65 | 100 | 69 | 52 | 28.457 | 9.803 | 6.94 | 132.965 | 28.108 | 28.081 | 27.028 | 603.892 | 25.607 | 26.221 | 1293.777 | 26.909 | 27.181 | 38.513 | 30.001 | 1.1 | 0.7 | 0 | 0.5 | 0.3
348 | 30/07/2025 09:27:48.459 | 98.184 | 63 | 100 | 70 | 52 | 25.506 | 9.784 | 6.988 | 133.381 | 28.118 | 28.062 | 27.024 | 603.869 | 25.628 | 26.22 | 1288.891 | 26.926 | 27.169 | 38.369 | 29.001 | 1.1 | 0.9 | 0 | 0.5 | 0.3
349 | 30/07/2025 09:27:50.095 | 98.592 | 64 | 100 | 71 | 53 | 28.676 | 9.803 | 6.988 | 133.387 | 28.131 | 28.056 | 27.017 | 603.8 | 25.625 | 26.216 | 1306.939 | 26.927 | 27.165 | 38.532 | 29.001 | 1.1 | 0.9 | 0 | 0.5 | 0.3
350 | 30/07/2025 09:27:51.734 | 98.904 | 65 | 100 | 71 | 52 | 29.649 | 9.834 | 6.999 | 133.258 | 28.134 | 28.041 | 27.185 | 603.855 | 25.618 | 26.234 | 1297.952 | 26.95 | 27.154 | 38.325 | 29.001 | 3.6 | 2 | 0.6 | 0.2 | 0.2
351 | 30/07/2025 09:27:53.371 | 98.352 | 64 | 100 | 70 | 52 | 26.782 | 9.873 | 7.072 | 133.252 | 28.149 | 28.082 | 27.045 | 603.925 | 25.618 | 26.217 | 1293.373 | 26.891 | 27.166 | 38.435 | 26.001 | 3.6 | 1 | 0.6 | 0.2 | 0.2
352 | 30/07/2025 09:27:55.009 | 99.288 | 67 | 100 | 71 | 53 | 29.483 | 9.806 | 7.075 | 133.045 | 28.143 | 28.074 | 27.172 | 603.705 | 25.607 | 26.238 | 1293.111 | 26.899 | 27.169 | 38.595 | 26.001 | 2.7 | 1.3 | 0.1 | 0.5 | 0.2
353 | 30/07/2025 09:27:56.643 | 99.216 | 65 | 100 | 70 | 52 | 27.914 | 9.73 | 7.072 | 133.329 | 28.133 | 28.066 | 27.148 | 603.931 | 25.611 | 26.199 | 1298.496 | 26.935 | 27.157 | 38.578 | 24.001 | 2.7 | 0.9 | 0.1 | 0.5 | 0.2
354 | 30/07/2025 09:27:58.283 | 99.576 | 65 | 100 | 70 | 52 | 25.687 | 9.759 | 7.063 | 133.172 | 28.112 | 28.073 | 27.02 | 603.753 | 25.611 | 26.199 | 1306.174 | 26.938 | 27.175 | 38.425 | 27.001 | 3.5 | 1.3 | 0.6 | 0.7 | 0.3
355 | 30/07/2025 09:27:59.920 | 99.744 | 66 | 100 | 71 | 52 | 29.038 | 9.761 | 7.061 | 133.3 | 28.134 | 28.042 | 27.038 | 603.845 | 25.597 | 26.197 | 1310.371 | 26.919 | 27.143 | 38.342 | 27.001 | 3.5 | 1.3 | 0.6 | 0.7 | 0.3
356 | 30/07/2025 09:28:01.555 | 99.672 | 66 | 100 | 70 | 52 | 29.511 | 9.871 | 7.062 | 133.161 | 28.129 | 28.076 | 27.037 | 603.881 | 25.596 | 26.194 | 1308.999 | 26.908 | 27.172 | 38.454 | 27.001 | 3.5 | 0.6 | 0.6 | 0.7 | 0.3
357 | 30/07/2025 09:28:03.189 | 99.528 | 65 | 100 | 70 | 52 | 26.079 | 9.574 | 7.035 | 133.447 | 28.121 | 28.06 | 27.023 | 603.784 | 25.6 | 26.202 | 1318.557 | 26.941 | 27.174 | 38.479 | 30.001 | 1.8 | 1.1 | 1.2 | 0.5 | 0.3
358 | 30/07/2025 09:28:04.825 | 100.104 | 65 | 100 | 70 | 53 | 29.606 | 9.797 | 7.034 | 133.376 | 28.121 | 28.068 | 27.021 | 603.792 | 25.609 | 26.191 | 1324.733 | 26.933 | 27.172 | 38.506 | 31.001 | 1.8 | 1.4 | 1.2 | 0.5 | 0.3
359 | 30/07/2025 09:28:06.460 | 99.936 | 65 | 100 | 70 | 52 | 27.254 | 9.873 | 7.036 | 133.302 | 28.122 | 28.046 | 27.034 | 603.75 | 25.618 | 26.231 | 1327.962 | 26.926 | 27.156 | 38.278 | 25.001 | 2.9 | 0.1 | 0 | 0.1 | 0.3
360 | 30/07/2025 09:28:08.095 | 99.864 | 65 | 100 | 70 | 53 | 26.029 | 9.515 | 7.033 | 133.102 | 28.127 | 28.052 | 27.039 | 603.871 | 25.626 | 26.212 | 1327.97 | 26.911 | 27.153 | 38.462 | 25.001 | 2.9 | 0.1 | 0 | 0.1 | 0.3
361 | 30/07/2025 09:28:09.732 | 99.816 | 66 | 100 | 70 | 52 | 29.248 | 9.574 | 7.036 | 133.159 | 28.11 | 28.088 | 27.032 | 603.843 | 25.618 | 26.222 | 1335.058 | 26.907 | 27.177 | 38.545 | 28.001 | 2.9 | 1.5 | 0 | 0.1 | 0.3
362 | 30/07/2025 09:28:11.369 | 99.552 | 66 | 100 | 70 | 52 | 29.286 | 9.781 | 7.006 | 133.461 | 28.111 | 28.067 | 27.018 | 603.736 | 25.631 | 26.228 | 1328.243 | 26.934 | 27.158 | 38.5 | 28.001 | 3 | 0.3 | 0 | 0 | 0.3
363 | 30/07/2025 09:28:13.003 | 100.032 | 67 | 100 | 70 | 52 | 25.694 | 9.504 | 7.006 | 133.448 | 28.113 | 28.058 | 27.029 | 603.849 | 25.629 | 26.224 | 1331.143 | 26.929 | 27.163 | 38.278 | 29.001 | 3 | 0.6 | 0 | 0 | 0.3
364 | 30/07/2025 09:28:14.638 | 100.344 | 66 | 100 | 71 | 52 | 29.555 | 9.73 | 7.005 | 133.475 | 28.126 | 28.043 | 27.046 | 603.823 | 25.628 | 26.227 | 1318.695 | 26.929 | 27.157 | 38.294 | 26.001 | 2.1 | 1.7 | 0.3 | 0.2 | 0.3
365 | 30/07/2025 09:28:16.274 | 99.912 | 65 | 100 | 70 | 52 | 26.578 | 9.775 | 7.006 | 133.066 | 28.099 | 28.075 | 27.184 | 603.951 | 25.607 | 26.228 | 1308.031 | 26.915 | 27.164 | 38.454 | 26.001 | 2.1 | 1.3 | 0.3 | 0.2 | 0.3
366 | 30/07/2025 09:28:17.913 | 99.576 | 66 | 100 | 71 | 52 | 26.486 | 9.727 | 7.008 | 133.296 | 28.089 | 28.064 | 27.034 | 603.774 | 25.623 | 26.24 | 1317.208 | 26.907 | 27.177 | 38.514 | 26.001 | 2.1 | 1.3 | 0.3 | 0.2 | 0.3
367 | 30/07/2025 09:28:19.549 | 99.168 | 65 | 100 | 70 | 53 | 29.31 | 9.499 | 6.988 | 133.392 | 28.107 | 28.062 | 27.149 | 605.048 | 25.634 | 26.21 | 1316.279 | 26.924 | 27.167 | 38.417 | 32.001 | 1.1 | 1.2 | 0.1 | 0 | 0.3
368 | 30/07/2025 09:28:21.184 | 99.072 | 64 | 100 | 70 | 52 | 28.946 | 9.703 | 6.988 | 133.26 | 28.112 | 28.05 | 27.025 | 606.323 | 25.618 | 26.213 | 1315.687 | 26.942 | 27.164 | 38.281 | 33.001 | 1.1 | 2.1 | 0.1 | 0 | 0.3
369 | 30/07/2025 09:28:22.825 | 98.76 | 65 | 100 | 72 | 52 | 28.984 | 9.575 | 6.986 | 133.291 | 28.113 | 28.046 | 27.054 | 606.554 | 25.615 | 26.209 | 1318.241 | 26.922 | 27.139 | 38.175 | 31.001 | 3.9 | 0.2 | 0.6 | 0.7 | 0.3
370 | 30/07/2025 09:28:24.461 | 99 | 65 | 100 | 70 | 52 | 29.562 | 9.749 | 6.989 | 132.92 | 28.117 | 28.072 | 27.177 | 606.241 | 25.614 | 26.224 | 1319.119 | 26.921 | 27.178 | 38.503 | 30.001 | 3.9 | 0.6 | 0.6 | 0.7 | 0.3
371 | 30/07/2025 09:28:26.097 | 99.312 | 66 | 100 | 70 | 50 | 26.269 | 9.801 | 6.988 | 133.37 | 28.15 | 28.07 | 27.173 | 606.312 | 25.631 | 26.218 | 1318.964 | 26.92 | 27.162 | 38.563 | 30.001 | 3.9 | 0.6 | 0.6 | 0.7 | 0.3
372 | 30/07/2025 09:28:27.735 | 98.664 | 65 | 100 | 70 | 52 | 27.192 | 9.495 | 7.021 | 133.34 | 28.14 | 28.071 | 27.149 | 606.242 | 25.607 | 26.205 | 1329.871 | 26.939 | 27.16 | 38.278 | 29.001 | 3.4 | 0.7 | 0 | 1.1 | 0.2
373 | 30/07/2025 09:28:29.366 | 99.024 | 66 | 100 | 70 | 53 | 29.418 | 9.863 | 7.03 | 133.276 | 28.132 | 28.109 | 27.171 | 606.279 | 25.603 | 26.216 | 1335.483 | 26.94 | 27.137 | 38.165 | 26.001 | 3.4 | 1.9 | 0 | 1.1 | 0.2
374 | 30/07/2025 09:28:31.002 | 98.472 | 65 | 100 | 70 | 52 | 26.086 | 9.815 | 7.004 | 133.252 | 28.126 | 28.058 | 27.045 | 606.369 | 25.603 | 26.202 | 1332.067 | 26.925 | 27.159 | 38.27 | 28.001 | 2.8 | 1.4 | 0 | 1.1 | 0.2
375 | 30/07/2025 09:28:32.641 | 99.144 | 66 | 100 | 69 | 52 | 29.281 | 10.017 | 7.008 | 132.969 | 28.127 | 28.085 | 27.173 | 605.003 | 25.597 | 26.213 | 1327.828 | 26.89 | 27.166 | 38.723 | 27.001 | 2.8 | 0.8 | 0 | 1.1 | 0.2
376 | 30/07/2025 09:28:34.276 | 98.472 | 63 | 100 | 70 | 52 | 29.307 | 9.576 | 6.987 | 133.399 | 28.124 | 28.216 | 27.029 | 603.884 | 25.603 | 26.197 | 1328.104 | 26.926 | 27.162 | 38.384 | 27.001 | 3.3 | 0.4 | 1.2 | 0.6 | 0.2
377 | 30/07/2025 09:28:35.914 | 98.904 | 66 | 100 | 71 | 53 | 25.863 | 10.022 | 7.005 | 133.171 | 28.121 | 28.065 | 27.025 | 603.638 | 25.608 | 26.185 | 1318.12 | 26.954 | 27.181 | 38.414 | 27.001 | 3.3 | 0.4 | 1.2 | 0.6 | 0.2
378 | 30/07/2025 09:28:37.548 | 98.568 | 66 | 100 | 69 | 54 | 27.53 | 9.434 | 7.005 | 133.414 | 28.135 | 28.05 | 27.035 | 603.853 | 25.621 | 26.202 | 1325.493 | 26.917 | 27.127 | 38.184 | 25.001 | 3.3 | 2.3 | 1.2 | 0.6 | 0.2
379 | 30/07/2025 09:28:39.186 | 98.976 | 66 | 100 | 70 | 52 | 29.546 | 9.56 | 7.007 | 133.119 | 28.112 | 28.08 | 27.041 | 603.925 | 25.62 | 26.197 | 1336.929 | 26.905 | 27.162 | 38.492 | 26.001 | 3.6 | 1.1 | 0.1 | 0.5 | 0.2
380 | 30/07/2025 09:28:40.822 | 99.72 | 65 | 100 | 70 | 52 | 26.461 | 9.797 | 7.006 | 133.269 | 28.153 | 28.125 | 27.17 | 603.813 | 25.634 | 26.205 | 1337.798 | 26.884 | 27.161 | 38.625 | 24.001 | 3.6 | 1.2 | 0.1 | 0.5 | 0.2
381 | 30/07/2025 09:28:42.457 | 100.32 | 66 | 100 | 70 | 52 | 29.364 | 9.577 | 6.937 | 133.278 | 28.124 | 28.072 | 27.146 | 603.904 | 25.629 | 26.21 | 1330.991 | 26.934 | 27.174 | 38.504 | 27.001 | 2.2 | 0.6 | 0.6 | 0.5 | 0.2
382 | 30/07/2025 09:28:44.092 | 100.488 | 68 | 100 | 70 | 51 | 28.946 | 9.733 | 6.938 | 131.875 | 28.112 | 28.059 | 27.046 | 603.75 | 25.63 | 26.235 | 1327.078 | 26.932 | 27.159 | 38.382 | 27.001 | 2.2 | 0.6 | 0.6 | 0.5 | 0.2
383 | 30/07/2025 09:28:45.728 | 100.68 | 66 | 100 | 70 | 52 | 25.538 | 9.635 | 6.935 | 131.67 | 28.107 | 28.058 | 27.195 | 603.89 | 25.616 | 26.219 | 1318.392 | 26.912 | 27.146 | 38.251 | 28.001 | 2.2 | 0.8 | 0.6 | 0.5 | 0.2
384 | 30/07/2025 09:28:47.365 | 100.752 | 67 | 100 | 70 | 52 | 28.113 | 9.799 | 6.939 | 131.589 | 28.105 | 28.077 | 27.019 | 603.676 | 25.61 | 26.227 | 1318.201 | 26.903 | 27.184 | 38.621 | 32.001 | 3 | 1 | 0.6 | 0.9 | 0.2
385 | 30/07/2025 09:28:48.999 | 100.848 | 68 | 100 | 70 | 52 | 26.04 | 9.98 | 6.936 | 131.927 | 28.115 | 28.167 | 27.174 | 603.973 | 25.617 | 26.219 | 1318.397 | 26.898 | 27.166 | 38.401 | 27.001 | 3 | 1.1 | 0.6 | 0.9 | 0.2
386 | 30/07/2025 09:28:50.633 | 100.68 | 66 | 100 | 70 | 52 | 26.982 | 9.885 | 6.938 | 133.089 | 28.107 | 28.07 | 26.988 | 603.697 | 25.612 | 26.236 | 1314.254 | 26.953 | 27.182 | 38.475 | 24.001 | 2.1 | 0.9 | 0.3 | 0.1 | 0.2
387 | 30/07/2025 09:28:52.268 | 100.08 | 67 | 100 | 70 | 52 | 29.427 | 9.651 | 6.934 | 133.484 | 28.123 | 28.045 | 27.037 | 603.88 | 25.64 | 26.223 | 1320.231 | 26.921 | 27.161 | 38.289 | 26.001 | 2.1 | 1 | 0.3 | 0.1 | 0.2
388 | 30/07/2025 09:28:53.902 | 100.272 | 67 | 100 | 70 | 52 | 28.412 | 9.73 | 6.935 | 133.043 | 28.102 | 28.216 | 27.03 | 603.871 | 25.607 | 26.213 | 1330.32 | 26.911 | 27.164 | 38.361 | 26.001 | 2.1 | 1 | 0.3 | 0.1 | 0.2
389 | 30/07/2025 09:28:55.536 | 100.512 | 67 | 100 | 72 | 52 | 25.463 | 9.806 | 6.99 | 133.241 | 28.11 | 28.065 | 27.026 | 603.726 | 25.616 | 26.221 | 1326.135 | 26.904 | 27.165 | 38.587 | 27.001 | 3 | 0.2 | 0 | 0 | 0.2
390 | 30/07/2025 09:28:57.171 | 100.368 | 66 | 100 | 69 | 52 | 28.636 | 9.507 | 6.989 | 133.517 | 28.12 | 28.072 | 27.013 | 603.964 | 25.618 | 26.212 | 1329.713 | 26.944 | 27.169 | 38.452 | 28.001 | 3 | 1.5 | 0 | 0 | 0.2
391 | 30/07/2025 09:28:58.810 | 100.008 | 66 | 100 | 70 | 52 | 25.784 | 9.429 | 6.988 | 133.41 | 28.128 | 28.055 | 27 | 603.658 | 25.619 | 26.215 | 1326.081 | 26.934 | 27.154 | 38.382 | 30.001 | 4.2 | 0.5 | 0 | 0.8 | 0.2
392 | 30/07/2025 09:29:00.441 | 99.984 | 67 | 100 | 70 | 51 | 27.715 | 9.762 | 6.941 | 133.305 | 28.141 | 28.057 | 27.05 | 603.982 | 25.611 | 26.205 | 1325.322 | 26.924 | 27.142 | 38.122 | 27.001 | 4.2 | 1.4 | 0 | 0.8 | 0.2
393 | 30/07/2025 09:29:02.076 | 100.152 | 66 | 100 | 70 | 52 | 29.555 | 9.757 | 6.936 | 133.023 | 28.117 | 28.068 | 27.161 | 603.777 | 25.596 | 26.22 | 1330.828 | 26.927 | 27.164 | 38.497 | 27.001 | 4.2 | 1.4 | 0 | 0.8 | 0.2
394 | 30/07/2025 09:29:03.713 | 99.744 | 67 | 100 | 71 | 52 | 27.975 | 9.458 | 6.936 | 133.413 | 28.138 | 28.07 | 27.03 | 603.804 | 25.624 | 26.209 | 1320.309 | 26.903 | 27.166 | 38.504 | 27.001 | 3.7 | 1.1 | 0.6 | 1.7 | 0.2
395 | 30/07/2025 09:29:05.347 | 99.528 | 66 | 100 | 70 | 52 | 25.762 | 9.873 | 6.936 | 134.593 | 28.124 | 28.074 | 27.145 | 603.835 | 25.582 | 26.21 | 1323.192 | 26.936 | 27.175 | 38.629 | 23.001 | 3.7 | 1.9 | 0.6 | 1.7 | 0.2
396 | 30/07/2025 09:29:06.983 | 99.24 | 65 | 100 | 71 | 53 | 29.002 | 9.874 | 6.935 | 134.697 | 28.14 | 28.061 | 27.029 | 603.735 | 25.609 | 26.195 | 1323.303 | 26.931 | 27.166 | 38.488 | 27.001 | 1.6 | 1.7 | 0.6 | 0 | 0.2
397 | 30/07/2025 09:29:08.619 | 99.072 | 66 | 100 | 71 | 52 | 25.654 | 9.879 | 6.917 | 134.636 | 28.116 | 28.058 | 27.118 | 603.989 | 25.593 | 26.183 | 1322.141 | 26.928 | 27.154 | 38.248 | 26.001 | 1.6 | 0.8 | 0.6 | 0 | 0.2
398 | 30/07/2025 09:29:10.255 | 98.664 | 66 | 100 | 70 | 52 | 28.241 | 9.75 | 6.903 | 134.644 | 28.127 | 28.076 | 27.168 | 603.784 | 25.6 | 26.197 | 1322.708 | 26.901 | 27.169 | 38.714 | 28.001 | 1.5 | 0.6 | 0.1 | 0 | 0.2
399 | 30/07/2025 09:29:11.891 | 98.304 | 65 | 100 | 70 | 52 | 29.64 | 9.75 | 6.988 | 134.894 | 28.132 | 28.081 | 27.171 | 603.814 | 25.601 | 26.186 | 1313.362 | 26.925 | 27.164 | 38.415 | 28.001 | 1.5 | 0.6 | 0.1 | 0 | 0.2
400 | 30/07/2025 09:29:13.528 | 98.304 | 65 | 100 | 70 | 52 | 27.499 | 9.85 | 6.988 | 134.652 | 28.118 | 28.06 | 27.158 | 603.658 | 25.608 | 26.208 | 1307.948 | 26.959 | 27.169 | 38.364 | 30.001 | 1.5 | 0 | 0.1 | 0 | 0.2
401 | 30/07/2025 09:29:15.167 | 97.896 | 65 | 100 | 71 | 52 | 26.038 | 9.424 | 6.986 | 134.839 | 28.129 | 28.042 | 27.186 | 603.836 | 25.635 | 26.219 | 1303.714 | 26.919 | 27.14 | 38.279 | 30.001 | 1.9 | 0 | 0 | 0.5 | 0.2
402 | 30/07/2025 09:29:16.803 | 97.944 | 65 | 100 | 71 | 52 | 28.53 | 9.495 | 6.988 | 134.497 | 28.124 | 28.061 | 27.173 | 603.781 | 25.616 | 26.234 | 1297.974 | 26.93 | 27.154 | 38.48 | 27.001 | 1.9 | 2.5 | 0 | 0.5 | 0.2
403 | 30/07/2025 09:29:18.438 | 97.872 | 65 | 100 | 70 | 52 | 25.529 | 9.743 | 7.006 | 134.748 | 28.141 | 28.07 | 27.172 | 603.833 | 25.626 | 26.214 | 1298.276 | 26.886 | 27.164 | 38.613 | 28.001 | 4.2 | 1.5 | 0.3 | 0.5 | 0.2
404 | 30/07/2025 09:29:20.076 | 97.8 | 65 | 100 | 70 | 52 | 28.667 | 9.873 | 7.008 | 134.711 | 28.115 | 28.093 | 27.159 | 603.713 | 25.619 | 26.225 | 1304.391 | 26.944 | 27.172 | 38.419 | 28.001 | 4.2 | 1.5 | 0.3 | 0.5 | 0.2
405 | 30/07/2025 09:29:21.711 | 97.296 | 65 | 100 | 70 | 52 | 29.692 | 9.607 | 6.981 | 134.829 | 28.097 | 28.052 | 27.156 | 603.781 | 25.616 | 26.233 | 1312.952 | 26.933 | 27.154 | 38.342 | 27.001 | 4.2 | 0.1 | 0.3 | 0.5 | 0.2
406 | 30/07/2025 09:29:23.347 | 97.296 | 63 | 100 | 71 | 52 | 26.682 | 9.582 | 6.934 | 134.546 | 28.092 | 28.067 | 27.048 | 603.89 | 25.512 | 26.216 | 1307.879 | 26.927 | 27.141 | 38.328 | 24.001 | 3.5 | 1 | 0.3 | 0.5 | 0.2
407 | 30/07/2025 09:29:24.980 | 97.392 | 64 | 100 | 70 | 52 | 29.582 | 9.748 | 6.943 | 134.751 | 28.106 | 28.073 | 27.167 | 603.766 | 25.485 | 26.221 | 1307.827 | 26.915 | 27.149 | 38.51 | 25.001 | 3.5 | 0.8 | 0.3 | 0.5 | 0.2
408 | 30/07/2025 09:29:26.615 | 96.984 | 64 | 100 | 70 | 52 | 27.802 | 9.577 | 6.989 | 134.826 | 28.111 | 28.091 | 27.169 | 603.892 | 25.586 | 26.217 | 1307.929 | 26.909 | 27.17 | 38.481 | 30.001 | 2.4 | 1.1 | 0.6 | 0.2 | 0.2
409 | 30/07/2025 09:29:28.249 | 96.912 | 64 | 100 | 70 | 53 | 25.675 | 9.755 | 7.036 | 134.678 | 28.095 | 28.065 | 27.007 | 603.684 | 25.461 | 26.228 | 1318.061 | 26.945 | 27.173 | 38.391 | 25.001 | 2.4 | 1.2 | 0.6 | 0.2 | 0.2
410 | 30/07/2025 09:29:29.895 | 96.168 | 64 | 100 | 71 | 52 | 29.016 | 10.023 | 7.036 | 134.851 | 28.131 | 28.099 | 27.188 | 603.901 | 25.478 | 26.216 | 1318.506 | 26.918 | 27.153 | 38.235 | 25.001 | 2.4 | 1.2 | 0.6 | 0.2 | 0.2
411 | 30/07/2025 09:29:31.530 | 97.824 | 66 | 100 | 70 | 52 | 29.576 | 9.555 | 7.032 | 132.945 | 28.12 | 28.222 | 27.18 | 603.829 | 25.466 | 26.205 | 1322.664 | 26.914 | 27.159 | 38.299 | 29.001 | 4.1 | 0.9 | 0.6 | 0 | 0.2
412 | 30/07/2025 09:29:33.167 | 97.8 | 64 | 100 | 70 | 52 | 26.139 | 9.477 | 6.939 | 133.244 | 28.127 | 28.12 | 27.173 | 603.831 | 25.47 | 26.233 | 1318.823 | 26.898 | 27.172 | 38.785 | 24.001 | 4.1 | 0.6 | 0.6 | 0 | 0.2
413 | 30/07/2025 09:29:34.802 | 98.376 | 65 | 100 | 71 | 52 | 29.628 | 9.575 | 6.937 | 133.206 | 28.111 | 28.085 | 27.158 | 603.805 | 25.463 | 26.209 | 1313.388 | 26.936 | 27.175 | 38.478 | 23.001 | 2.6 | 0.7 | 0 | 0.5 | 0.2
414 | 30/07/2025 09:29:36.438 | 97.968 | 65 | 100 | 71 | 54 | 27.292 | 9.874 | 7.006 | 133.377 | 28.151 | 28.185 | 26.99 | 603.611 | 25.478 | 26.213 | 1315.858 | 26.937 | 27.147 | 38.47 | 23.001 | 2.6 | 1.3 | 0 | 0.5 | 0.2
415 | 30/07/2025 09:29:38.075 | 97.68 | 64 | 100 | 70 | 52 | 26.117 | 9.824 | 7.005 | 133.288 | 28.126 | 28.191 | 27.05 | 603.937 | 25.444 | 26.206 | 1310.357 | 26.924 | 27.149 | 38.255 | 23.001 | 2.6 | 1.3 | 0 | 0.5 | 0.2
416 | 30/07/2025 09:29:39.712 | 98.04 | 65 | 100 | 70 | 52 | 29.303 | 9.878 | 7.034 | 132.926 | 28.124 | 28.221 | 27.167 | 603.739 | 25.455 | 26.213 | 1325.237 | 26.924 | 27.16 | 38.551 | 27.001 | 0.7 | 0.1 | 0.6 | 0 | 0.2
417 | 30/07/2025 09:29:41.346 | 97.488 | 65 | 100 | 70 | 53 | 29.377 | 9.801 | 7.005 | 133.451 | 28.145 | 28.222 | 27.176 | 603.879 | 25.471 | 26.178 | 1320.981 | 26.91 | 27.17 | 38.501 | 28.001 | 0.7 | 0.6 | 0.6 | 0 | 0.2
418 | 30/07/2025 09:29:42.981 | 98.328 | 64 | 100 | 70 | 53 | 25.886 | 9.803 | 7.007 | 133.193 | 28.119 | 28.086 | 27.014 | 602.483 | 25.437 | 26.181 | 1334.021 | 26.939 | 27.18 | 38.237 | 26.001 | 3.6 | 0.1 | 0.3 | 0.5 | 0.2
419 | 30/07/2025 09:29:44.615 | 98.448 | 65 | 100 | 71 | 52 | 29.672 | 9.799 | 7.006 | 131.854 | 28.128 | 28.111 | 27.125 | 603.791 | 25.466 | 26.192 | 1336.212 | 26.925 | 27.165 | 38.307 | 24.001 | 3.6 | 2.3 | 0.3 | 0.5 | 0.2
420 | 30/07/2025 09:29:46.253 | 98.616 | 65 | 100 | 70 | 52 | 26.866 | 9.507 | 7.005 | 131.759 | 28.117 | 28.2 | 27.171 | 603.898 | 25.464 | 26.199 | 1337.755 | 26.939 | 27.154 | 38.32 | 25.001 | 3.5 | 1.8 | 0.4 | 0.5 | 0.2
421 | 30/07/2025 09:29:47.890 | 99.168 | 66 | 100 | 71 | 52 | 26.5 | 9.518 | 6.989 | 131.622 | 28.134 | 28.217 | 27.159 | 603.832 | 25.48 | 26.205 | 1344.764 | 26.903 | 27.162 | 38.6 | 25.001 | 3.5 | 1.8 | 0.4 | 0.5 | 0.2
422 | 30/07/2025 09:29:49.530 | 100.2 | 67 | 100 | 71 | 52 | 29.411 | 10.023 | 6.989 | 131.878 | 28.124 | 28.178 | 27.165 | 603.85 | 25.465 | 26.21 | 1330.672 | 26.919 | 27.162 | 38.451 | 28.001 | 3.5 | 1.1 | 0.4 | 0.5 | 0.2
423 | 30/07/2025 09:29:51.165 | 100.632 | 67 | 100 | 71 | 52 | 29.097 | 9.577 | 6.989 | 131.818 | 28.12 | 28.216 | 27.147 | 603.654 | 25.476 | 26.228 | 1337.966 | 26.955 | 27.169 | 38.424 | 30.001 | 3.9 | 1 | 0.6 | 0.6 | 0.2
424 | 30/07/2025 09:29:52.799 | 100.776 | 66 | 100 | 70 | 52 | 29.052 | 9.438 | 7.005 | 131.807 | 28.098 | 28.206 | 27.154 | 603.806 | 25.467 | 26.216 | 1335.389 | 26.935 | 27.164 | 38.355 | 26.001 | 3.9 | 0.8 | 0.6 | 0.6 | 0.2
425 | 30/07/2025 09:29:54.434 | 100.392 | 68 | 100 | 68 | 52 | 29.631 | 9.728 | 7.006 | 131.556 | 28.111 | 28.206 | 27.165 | 602.53 | 25.468 | 26.234 | 1320.259 | 26.928 | 27.15 | 38.359 | 29.001 | 1.2 | 1.1 | 0 | 0.5 | 0.2
426 | 30/07/2025 09:29:56.069 | 100.032 | 67 | 100 | 70 | 52 | 26.28 | 9.841 | 7.007 | 131.846 | 28.112 | 28.079 | 27.186 | 603.943 | 25.468 | 26.217 | 1318.53 | 26.891 | 27.175 | 38.53 | 29.001 | 1.2 | 1.1 | 0 | 0.5 | 0.2
427 | 30/07/2025 09:29:57.704 | 100.08 | 66 | 100 | 70 | 53 | 26.957 | 9.877 | 6.938 | 131.729 | 28.089 | 28.089 | 27.137 | 602.559 | 25.46 | 26.218 | 1328.178 | 26.948 | 27.182 | 38.54 | 24.001 | 1.2 | 1.7 | 0 | 0.5 | 0.2
428 | 30/07/2025 09:29:59.340 | 99.576 | 67 | 100 | 70 | 52 | 29.477 | 9.73 | 6.935 | 132.039 | 28.11 | 28.201 | 27.15 | 602.567 | 25.48 | 26.232 | 1327.907 | 26.927 | 27.156 | 38.493 | 21.001 | 1.9 | 1.7 | 0.7 | 0.6 | 0.2
429 | 30/07/2025 09:30:00.975 | 99.912 | 67 | 100 | 71 | 53 | 25.984 | 9.731 | 6.937 | 131.745 | 28.11 | 28.044 | 27.154 | 602.511 | 25.469 | 26.225 | 1327.751 | 26.954 | 27.165 | 38.471 | 25.001 | 1.9 | 1.6 | 0.7 | 0.6 | 0.2
430 | 30/07/2025 09:30:02.608 | 99.528 | 66 | 100 | 71 | 52 | 29.241 | 9.811 | 6.934 | 133.251 | 28.112 | 28.217 | 27.178 | 602.612 | 25.491 | 26.221 | 1328.024 | 26.91 | 27.155 | 38.582 | 29.001 | 1.1 | 1 | 0.6 | 0.5 | 0.2
431 | 30/07/2025 09:30:04.244 | 99.36 | 66 | 100 | 71 | 52 | 29.336 | 9.589 | 6.903 | 133.268 | 28.109 | 28.229 | 27.174 | 602.619 | 25.466 | 26.21 | 1318.173 | 26.904 | 27.174 | 38.553 | 25.001 | 1.1 | 1.3 | 0.6 | 0.5 | 0.2
432 | 30/07/2025 09:30:05.884 | 99.24 | 66 | 100 | 70 | 53 | 25.817 | 9.788 | 6.903 | 133.209 | 28.13 | 28.224 | 27.131 | 602.43 | 25.464 | 26.238 | 1318.371 | 26.938 | 27.157 | 38.675 | 25.001 | 1.1 | 1.3 | 0.6 | 0.5 | 0.2
433 | 30/07/2025 09:30:07.522 | 98.976 | 66 | 100 | 72 | 52 | 27.639 | 9.816 | 6.899 | 133.33 | 28.136 | 28.204 | 27.187 | 602.629 | 25.469 | 26.199 | 1308.383 | 26.925 | 27.15 | 38.296 | 23.001 | 2.4 | 1.6 | 0.6 | 0.5 | 0.2
434 | 30/07/2025 09:30:09.184 | 99.24 | 65 | 100 | 70 | 52 | 29.581 | 9.756 | 6.934 | 133.081 | 28.132 | 28.16 | 27.173 | 602.712 | 25.454 | 26.212 | 1297.7 | 26.93 | 27.16 | 38.436 | 29.001 | 2.4 | 1.7 | 0.6 | 0.5 | 0.2
435 | 30/07/2025 09:30:10.820 | 99.12 | 67 | 100 | 70 | 52 | 26.569 | 9.738 | 6.935 | 133.099 | 28.124 | 28.127 | 27.183 | 602.676 | 25.447 | 26.201 | 1297.741 | 26.897 | 27.162 | 38.295 | 27.001 | 3.1 | 1.4 | 0.6 | 0 | 0.2
436 | 30/07/2025 09:30:12.456 | 97.848 | 65 | 100 | 69 | 52 | 29.436 | 9.814 | 6.937 | 133.317 | 28.12 | 28.077 | 27.154 | 602.426 | 25.432 | 26.203 | 1298.035 | 26.927 | 27.169 | 38.481 | 27.001 | 3.1 | 1.6 | 0.6 | 0 | 0.2
437 | 30/07/2025 09:30:14.091 | 98.376 | 66 | 100 | 72 | 52 | 29.032 | 9.642 | 6.936 | 133.491 | 28.141 | 28.212 | 27.143 | 602.412 | 25.472 | 26.206 | 1298.171 | 26.929 | 27.157 | 38.579 | 27.001 | 3.1 | 1.6 | 0.6 | 0 | 0.2
438 | 30/07/2025 09:30:15.728 | 98.352 | 65 | 100 | 70 | 52 | 25.609 | 9.671 | 6.936 | 133.163 | 28.119 | 28.034 | 27.182 | 602.581 | 25.453 | 26.19 | 1301.835 | 26.928 | 27.154 | 38.281 | 26.001 | 5.2 | 1.4 | 0.6 | 0 | 0.2
439 | 30/07/2025 09:30:17.365 | 97.968 | 66 | 100 | 71 | 52 | 28.224 | 9.634 | 6.937 | 133.026 | 28.119 | 28.076 | 27.172 | 602.379 | 25.449 | 26.217 | 1295.936 | 26.921 | 27.155 | 38.526 | 24.001 | 5.2 | 0.9 | 0.6 | 0 | 0.2
440 | 30/07/2025 09:30:19.001 | 97.824 | 65 | 100 | 71 | 52 | 29.624 | 9.741 | 6.936 | 133.288 | 28.132 | 28.16 | 27.189 | 602.619 | 25.475 | 26.188 | 1291.907 | 26.898 | 27.163 | 38.578 | 25.001 | 3.9 | 1.2 | 0.6 | 1.2 | 0.2
441 | 30/07/2025 09:30:20.637 | 98.088 | 66 | 100 | 70 | 53 | 27.138 | 9.731 | 6.939 | 133.435 | 28.132 | 28.069 | 27.156 | 602.544 | 25.464 | 26.201 | 1284.958 | 26.925 | 27.159 | 38.57 | 23.001 | 3.9 | 1.1 | 0.6 | 1.2 | 0.2
442 | 30/07/2025 09:30:22.271 | 97.872 | 66 | 100 | 71 | 52 | 29.551 | 9.929 | 6.966 | 133.326 | 28.137 | 28.21 | 27.168 | 602.545 | 25.476 | 26.191 | 1281.515 | 26.922 | 27.156 | 38.334 | 27.001 | 3.6 | 0.5 | 0.1 | 0.6 | 0.2
443 | 30/07/2025 09:30:23.907 | 98.544 | 68 | 100 | 70 | 53 | 28.602 | 9.793 | 6.987 | 133.236 | 28.11 | 28.079 | 27.179 | 602.607 | 25.462 | 26.218 | 1295.839 | 26.948 | 27.165 | 38.306 | 27.001 | 3.6 | 0.5 | 0.1 | 0.6 | 0.2
444 | 30/07/2025 09:30:25.545 | 98.256 | 67 | 100 | 70 | 52 | 25.646 | 9.861 | 6.937 | 133.215 | 28.136 | 28.221 | 27.174 | 602.57 | 25.49 | 26.229 | 1297.79 | 26.897 | 27.166 | 38.58 | 26.001 | 3.6 | 1.2 | 0.1 | 0.6 | 0.2
445 | 30/07/2025 09:30:27.180 | 98.064 | 65 | 100 | 70 | 53 | 28.732 | 9.574 | 6.989 | 133.296 | 28.104 | 28.08 | 27.172 | 602.558 | 25.46 | 26.225 | 1302.441 | 26.922 | 27.164 | 38.336 | 30.001 | 5.3 | 1 | 0.1 | 0.8 | 0.3
446 | 30/07/2025 09:30:28.813 | 98.592 | 65 | 100 | 71 | 55 | 25.909 | 9.8 | 7.006 | 133.372 | 28.113 | 28.136 | 27.149 | 602.535 | 25.478 | 26.224 | 1305.542 | 26.93 | 27.165 | 38.563 | 28.001 | 5.3 | 1.1 | 0.1 | 0.8 | 0.3
447 | 30/07/2025 09:30:30.447 | 98.712 | 65 | 100 | 70 | 51 | 27.598 | 9.873 | 6.95 | 133.272 | 28.098 | 28.207 | 27.156 | 602.603 | 25.46 | 26.232 | 1308.588 | 26.936 | 27.172 | 38.297 | 29.001 | 2.6 | 1.6 | 0.1 | 0.5 | 0.2
448 | 30/07/2025 09:30:32.083 | 98.424 | 65 | 100 | 72 | 53 | 29.602 | 9.741 | 6.934 | 133.183 | 28.094 | 28.205 | 27.176 | 602.579 | 25.474 | 26.24 | 1306.575 | 26.918 | 27.137 | 38.424 | 29.001 | 2.6 | 1.6 | 0.1 | 0.5 | 0.2
449 | 30/07/2025 09:30:33.717 | 98.52 | 67 | 100 | 70 | 52 | 27.988 | 9.725 | 6.937 | 133.234 | 28.102 | 28.226 | 27.176 | 602.739 | 25.468 | 26.218 | 1297.057 | 26.884 | 27.173 | 38.604 | 28.001 | 2.6 | 1.5 | 0.1 | 0.5 | 0.2
450 | 30/07/2025 09:30:35.354 | 98.568 | 64 | 100 | 71 | 52 | 25.707 | 9.73 | 6.937 | 133.038 | 28.096 | 28.215 | 27.13 | 602.5 | 25.458 | 26.218 | 1298.308 | 26.944 | 27.177 | 38.655 | 23.001 | 3 | 1.9 | 0.1 | 0.6 | 0.2
451 | 30/07/2025 09:30:36.990 | 99.216 | 66 | 100 | 70 | 52 | 29.024 | 9.8 | 6.935 | 133.321 | 28.115 | 28.221 | 27.153 | 602.572 | 25.472 | 26.211 | 1291.209 | 26.93 | 27.16 | 38.418 | 23.001 | 3 | 0.7 | 0.1 | 0.6 | 0.2
452 | 30/07/2025 09:30:38.624 | 99.72 | 67 | 100 | 70 | 52 | 25.622 | 9.619 | 6.958 | 133.292 | 28.12 | 28.197 | 27.175 | 602.491 | 25.462 | 26.221 | 1290.135 | 26.953 | 27.161 | 38.339 | 24.001 | 2.1 | 0.8 | 0.1 | 1.1 | 0.2
453 | 30/07/2025 09:30:40.258 | 99.864 | 67 | 100 | 71 | 52 | 28.154 | 9.711 | 6.986 | 133.385 | 28.144 | 28.215 | 27.183 | 602.518 | 25.489 | 26.213 | 1286.35 | 26.906 | 27.153 | 38.511 | 23.001 | 2.1 | 1.4 | 0.1 | 1.1 | 0.2
454 | 30/07/2025 09:30:41.894 | 99.432 | 66 | 100 | 70 | 51 | 29.642 | 9.803 | 6.937 | 133.261 | 28.121 | 28.086 | 27.167 | 602.564 | 25.449 | 26.214 | 1285.583 | 26.912 | 27.184 | 38.434 | 23.001 | 2.1 | 1.4 | 0.1 | 1.1 | 0.2
455 | 30/07/2025 09:30:43.529 | 99.216 | 67 | 100 | 70 | 52 | 27.268 | 9.73 | 6.936 | 133.364 | 28.122 | 28.068 | 27.149 | 602.431 | 25.453 | 26.229 | 1290.524 | 26.934 | 27.166 | 38.472 | 28.001 | 3.1 | 0.9 | 0.6 | 0 | 0.3
456 | 30/07/2025 09:30:45.168 | 98.376 | 65 | 100 | 70 | 53 | 26.086 | 10.022 | 6.935 | 133.319 | 28.119 | 28.067 | 27.174 | 602.501 | 25.463 | 26.201 | 1298.103 | 26.923 | 27.156 | 38.263 | 30.001 | 3.1 | 0.7 | 0.6 | 0 | 0.3
457 | 30/07/2025 09:30:46.804 | 98.52 | 66 | 100 | 70 | 52 | 28.434 | 10.025 | 6.961 | 133.121 | 28.143 | 28.132 | 27.168 | 602.529 | 25.453 | 26.206 | 1302.9 | 26.923 | 27.148 | 38.254 | 26.001 | 1.7 | 2.2 | 0 | 1.1 | 0.2
458 | 30/07/2025 09:30:48.439 | 98.04 | 66 | 100 | 71 | 52 | 25.531 | 9.875 | 6.987 | 133.204 | 28.131 | 28.085 | 27.177 | 602.67 | 25.453 | 26.195 | 1307.717 | 26.909 | 27.163 | 38.298 | 28.001 | 1.7 | 1.1 | 0 | 1.1 | 0.2
459 | 30/07/2025 09:30:50.076 | 98.328 | 66 | 100 | 71 | 54 | 28.652 | 9.727 | 6.991 | 133.431 | 28.124 | 28.22 | 27.152 | 602.559 | 25.447 | 26.215 | 1303.269 | 26.93 | 27.174 | 38.536 | 28.001 | 1.7 | 1.1 | 0 | 1.1 | 0.2
460 | 30/07/2025 09:30:51.713 | 98.232 | 65 | 100 | 71 | 52 | 29.716 | 9.712 | 6.988 | 133.367 | 28.139 | 28.195 | 27.138 | 602.489 | 25.469 | 26.179 | 1307.347 | 26.932 | 27.165 | 38.594 | 26.001 | 0.7 | 2.2 | 0 | 0.5 | 0.2
461 | 30/07/2025 09:30:53.348 | 98.784 | 66 | 100 | 71 | 52 | 26.87 | 9.587 | 6.986 | 134.783 | 28.127 | 28.054 | 27.168 | 602.694 | 25.448 | 26.188 | 1296.176 | 26.934 | 27.162 | 38.191 | 23.001 | 0.7 | 1.1 | 0 | 0.5 | 0.2
462 | 30/07/2025 09:30:54.984 | 98.304 | 65 | 100 | 70 | 52 | 29.608 | 9.697 | 6.989 | 134.773 | 28.136 | 28.198 | 27.19 | 602.798 | 25.466 | 26.193 | 1295.688 | 26.925 | 27.14 | 38.3 | 27.001 | 3.5 | 1.9 | 0.6 | 0.9 | 0.2
463 | 30/07/2025 09:30:56.620 | 98.28 | 66 | 100 | 71 | 52 | 28.117 | 9.803 | 7.007 | 134.437 | 28.114 | 28.094 | 27.157 | 602.597 | 25.467 | 26.204 | 1299.132 | 26.906 | 27.186 | 38.714 | 28.001 | 3.5 | 2 | 0.6 | 0.9 | 0.2
464 | 30/07/2025 09:30:58.254 | 98.616 | 67 | 100 | 71 | 53 | 25.806 | 9.575 | 7.034 | 135.017 | 28.114 | 28.219 | 27.161 | 602.484 | 25.478 | 26.218 | 1305.331 | 26.919 | 27.17 | 38.554 | 28.001 | 1.6 | 1.6 | 0.3 | 0 | 0.2
465 | 30/07/2025 09:30:59.889 | 98.256 | 65 | 100 | 70 | 53 | 29.073 | 9.577 | 7.016 | 134.724 | 28.11 | 28.07 | 27.169 | 602.49 | 25.476 | 26.223 | 1314.9 | 26.933 | 27.168 | 38.429 | 28.001 | 1.6 | 1.6 | 0.3 | 0 | 0.2
466 | 30/07/2025 09:31:01.525 | 98.136 | 65 | 100 | 72 | 53 | 29.638 | 9.719 | 7.007 | 134.665 | 28.092 | 28.033 | 27.182 | 602.504 | 25.464 | 26.236 | 1325.426 | 26.945 | 27.152 | 38.205 | 28.001 | 1.6 | 1.4 | 0.3 | 0 | 0.2
467 | 30/07/2025 09:31:03.161 | 97.8 | 66 | 100 | 70 | 52 | 26.316 | 9.571 | 7.005 | 134.695 | 28.113 | 28.082 | 27.18 | 602.719 | 25.495 | 26.231 | 1321.306 | 26.902 | 27.158 | 38.619 | 34.001 | 2.9 | 1 | 0.6 | 1.1 | 0.2
468 | 30/07/2025 09:31:04.797 | 97.512 | 65 | 100 | 69 | 53 | 29.705 | 9.572 | 7.008 | 134.64 | 28.101 | 28.194 | 27.16 | 602.481 | 25.461 | 26.226 | 1318.161 | 26.904 | 27.169 | 38.599 | 34.001 | 2.9 | 0.8 | 0.6 | 1.1 | 0.2
469 | 30/07/2025 09:31:06.433 | 97.56 | 65 | 100 | 69 | 52 | 27.478 | 9.495 | 7.006 | 134.994 | 28.112 | 28.078 | 27.162 | 602.511 | 25.491 | 26.21 | 1318.236 | 26.926 | 27.161 | 38.483 | 28.001 | 0.9 | 1.2 | 0 | 0.5 | 0.1
470 | 30/07/2025 09:31:08.072 | 97.92 | 67 | 100 | 71 | 52 | 26.067 | 9.806 | 7.007 | 134.623 | 28.081 | 28.22 | 27.163 | 602.498 | 25.462 | 26.211 | 1327.847 | 26.937 | 27.177 | 38.235 | 28.001 | 0.9 | 1.2 | 0 | 0.5 | 0.1
471 | 30/07/2025 09:31:09.710 | 97.944 | 66 | 100 | 70 | 52 | 29.33 | 9.796 | 7.005 | 134.743 | 28.107 | 28.202 | 27.173 | 602.657 | 25.477 | 26.222 | 1328.836 | 26.927 | 27.143 | 38.241 | 30.001 | 0.9 | 1.4 | 0 | 0.5 | 0.1
472 | 30/07/2025 09:31:11.345 | 97.848 | 65 | 100 | 70 | 52 | 29.475 | 9.726 | 7.007 | 134.696 | 28.101 | 28.23 | 27.178 | 602.576 | 25.457 | 26.207 | 1329.509 | 26.899 | 27.164 | 38.388 | 26.001 | 2.3 | 0.6 | 0.9 | 0 | 0.2
473 | 30/07/2025 09:31:12.982 | 97.368 | 64 | 100 | 71 | 52 | 28.667 | 9.781 | 7.007 | 134.999 | 28.122 | 28.22 | 27.16 | 602.408 | 25.47 | 26.215 | 1339.768 | 26.88 | 27.172 | 38.501 | 32.001 | 2.3 | 1.6 | 0.9 | 0 | 0.2
474 | 30/07/2025 09:31:14.617 | 97.032 | 65 | 100 | 70 | 53 | 29.708 | 9.843 | 7.006 | 134.777 | 28.119 | 28.198 | 27.15 | 602.398 | 25.458 | 26.214 | 1337.215 | 26.931 | 27.164 | 38.392 | 25.001 | 2.9 | 1.1 | 0 | 0.7 | 0.3
475 | 30/07/2025 09:31:16.250 | 97.464 | 66 | 100 | 70 | 53 | 26.743 | 9.735 | 6.992 | 134.746 | 28.111 | 28.051 | 27.163 | 602.49 | 25.454 | 26.227 | 1330.682 | 26.943 | 27.146 | 38.376 | 24.001 | 2.9 | 2.1 | 0 | 0.7 | 0.3
476 | 30/07/2025 09:31:17.885 | 96.792 | 65 | 99 | 70 | 52 | 26.523 | 9.818 | 6.933 | 134.666 | 28.131 | 28.22 | 27.174 | 601.158 | 25.467 | 26.204 | 1330.319 | 26.92 | 27.144 | 38.578 | 24.001 | 2.9 | 2.1 | 0 | 0.7 | 0.3
477 | 30/07/2025 09:31:19.521 | 96.384 | 64 | 100 | 70 | 52 | 29.435 | 9.738 | 6.937 | 134.74 | 28.128 | 28.235 | 27.175 | 601.055 | 25.454 | 26.199 | 1332.681 | 26.907 | 27.185 | 38.489 | 25.001 | 2.5 | 1.1 | 0.6 | 0.6 | 0.3
478 | 30/07/2025 09:31:21.156 | 96 | 63 | 100 | 70 | 53 | 29.02 | 9.803 | 6.937 | 134.752 | 28.128 | 28.215 | 27.136 | 602.407 | 25.465 | 26.201 | 1326.363 | 26.934 | 27.163 | 38.62 | 23.001 | 2.5 | 1.3 | 0.6 | 0.6 | 0.3
479 | 30/07/2025 09:31:22.794 | 96.048 | 64 | 100 | 72 | 53 | 29.054 | 9.802 | 6.937 | 134.635 | 28.123 | 28.113 | 27.141 | 602.389 | 25.43 | 26.197 | 1323.448 | 26.951 | 27.177 | 38.507 | 24.001 | 3.2 | 1.9 | 0 | 0.8 | 0.3
480 | 30/07/2025 09:31:24.431 | 96.504 | 66 | 100 | 71 | 52 | 29.631 | 9.733 | 6.935 | 134.846 | 28.122 | 28.197 | 27.152 | 602.619 | 25.469 | 26.187 | 1328.017 | 26.925 | 27.153 | 38.235 | 26.001 | 3.2 | 0.9 | 0 | 0.8 | 0.3
481 | 30/07/2025 09:31:26.067 | 96.384 | 66 | 100 | 71 | 52 | 26.27 | 9.743 | 6.987 | 134.604 | 28.122 | 28.233 | 27.184 | 602.532 | 25.467 | 26.176 | 1331.264 | 26.91 | 27.156 | 38.463 | 26.001 | 3.2 | 0.9 | 0 | 0.8 | 0.3
482 | 30/07/2025 09:31:27.703 | 96.888 | 65 | 100 | 70 | 52 | 27.03 | 9.732 | 6.99 | 133.331 | 28.108 | 28.074 | 27.157 | 602.371 | 25.468 | 26.201 | 1327.902 | 26.924 | 27.162 | 38.524 | 27.001 | 3.3 | 1 | 0.9 | 0 | 0.3
483 | 30/07/2025 09:31:29.338 | 97.272 | 65 | 100 | 70 | 51 | 29.53 | 9.722 | 6.974 | 133.325 | 28.137 | 28.219 | 27.136 | 602.401 | 25.462 | 26.188 | 1318.511 | 26.927 | 27.164 | 38.678 | 27.001 | 3.3 | 0 | 0.9 | 0 | 0.3
484 | 30/07/2025 09:31:30.972 | 97.32 | 65 | 100 | 70 | 53 | 28.638 | 9.581 | 6.935 | 133.159 | 28.11 | 28.21 | 27.168 | 602.574 | 25.473 | 26.212 | 1306.811 | 26.933 | 27.166 | 38.45 | 24.001 | 3.7 | 0.7 | 0 | 0.1 | 0.2
485 | 30/07/2025 09:31:32.607 | 97.344 | 65 | 100 | 71 | 52 | 29.303 | 9.578 | 6.933 | 133.191 | 28.126 | 28.057 | 27.185 | 602.652 | 25.479 | 26.204 | 1307.31 | 26.923 | 27.134 | 38.366 | 23.001 | 3.7 | 0.9 | 0 | 0.1 | 0.2
486 | 30/07/2025 09:31:34.241 | 97.8 | 66 | 100 | 71 | 52 | 29.465 | 9.724 | 6.937 | 132.959 | 28.109 | 28.161 | 27.158 | 602.456 | 25.463 | 26.218 | 1315.373 | 26.922 | 27.175 | 38.49 | 25.001 | 2 | 3.5 | 0.6 | 0.8 | 0.2
487 | 30/07/2025 09:31:35.878 | 97.248 | 66 | 100 | 71 | 54 | 25.891 | 9.594 | 6.937 | 133.544 | 28.118 | 28.129 | 27.166 | 602.488 | 25.492 | 26.212 | 1307.805 | 26.922 | 27.169 | 38.489 | 25.001 | 2 | 3.5 | 0.6 | 0.8 | 0.2
488 | 30/07/2025 09:31:37.514 | 97.416 | 66 | 100 | 70 | 52 | 27.578 | 9.578 | 6.936 | 133.276 | 28.116 | 28.07 | 27.158 | 602.357 | 25.46 | 26.22 | 1297.796 | 26.932 | 27.166 | 38.415 | 26.001 | 2 | 1.8 | 0.6 | 0.8 | 0.2
489 | 30/07/2025 09:31:39.150 | 97.68 | 65 | 100 | 71 | 52 | 29.589 | 9.801 | 6.987 | 133.263 | 28.074 | 28.062 | 27.168 | 602.437 | 25.454 | 26.218 | 1297.888 | 26.937 | 27.155 | 38.251 | 28.001 | 3.7 | 2.2 | 1.3 | 1.3 | 0.2
490 | 30/07/2025 09:31:40.787 | 97.008 | 64 | 100 | 71 | 52 | 26.561 | 9.882 | 6.978 | 133.066 | 28.083 | 28.203 | 27.16 | 602.595 | 25.461 | 26.216 | 1304.138 | 26.92 | 27.155 | 38.383 | 27.001 | 3.7 | 1.3 | 1.3 | 1.3 | 0.2
491 | 30/07/2025 09:31:42.423 | 96.816 | 65 | 100 | 70 | 52 | 29.418 | 9.729 | 6.939 | 132.994 | 28.099 | 28.215 | 27.164 | 602.457 | 25.473 | 26.22 | 1314.704 | 26.905 | 27.166 | 38.686 | 27.001 | 2.5 | 1.9 | 0.6 | 0.1 | 0.2
492 | 30/07/2025 09:31:44.058 | 96.576 | 64 | 100 | 70 | 53 | 29.15 | 9.868 | 6.936 | 133.421 | 28.118 | 28.222 | 27.171 | 602.454 | 25.462 | 26.209 | 1315.932 | 26.93 | 27.161 | 38.494 | 27.001 | 2.5 | 1.9 | 0.6 | 0.1 | 0.2
493 | 30/07/2025 09:31:45.693 | 96.672 | 64 | 100 | 70 | 52 | 25.702 | 9.778 | 6.936 | 133.258 | 28.107 | 28.068 | 27.137 | 602.425 | 25.458 | 26.217 | 1316.112 | 26.949 | 27.178 | 38.376 | 21.001 | 2.5 | 2.5 | 0.6 | 0.1 | 0.2
494 | 30/07/2025 09:31:47.328 | 96.528 | 65 | 100 | 71 | 52 | 28.166 | 9.809 | 6.899 | 133.315 | 28.145 | 28.208 | 27.161 | 602.526 | 25.464 | 26.217 | 1307.867 | 26.919 | 27.141 | 38.227 | 28.001 | 2.3 | 1.5 | 0.1 | 0 | 0.3
495 | 30/07/2025 09:31:48.962 | 96.648 | 65 | 100 | 70 | 52 | 29.659 | 9.802 | 6.901 | 133.156 | 28.125 | 28.095 | 27.179 | 602.572 | 25.459 | 26.199 | 1305.799 | 26.908 | 27.167 | 38.72 | 30.001 | 2.3 | 0.9 | 0.1 | 0 | 0.3
496 | 30/07/2025 09:31:50.597 | 96.888 | 65 | 100 | 70 | 53 | 27.019 | 9.802 | 6.901 | 133.362 | 28.137 | 28.213 | 27.169 | 602.456 | 25.478 | 26.222 | 1307.94 | 26.885 | 27.168 | 38.476 | 27.001 | 3.9 | 0.7 | 0 | 0.3 | 0.3
497 | 30/07/2025 09:31:52.233 | 96.504 | 65 | 100 | 72 | 52 | 29.507 | 9.577 | 6.929 | 133.293 | 28.109 | 28.077 | 27.137 | 602.473 | 25.448 | 26.211 | 1310.349 | 26.929 | 27.175 | 38.296 | 25.001 | 3.9 | 0 | 0 | 0.3 | 0.3
498 | 30/07/2025 09:31:53.880 | 96.816 | 65 | 100 | 70 | 53 | 28.561 | 9.574 | 6.935 | 133.317 | 28.114 | 28.052 | 27.148 | 602.373 | 25.438 | 26.221 | 1311.52 | 26.927 | 27.148 | 38.352 | 25.001 | 3.9 | 0 | 0 | 0.3 | 0.3
499 | 30/07/2025 09:31:55.516 | 96.912 | 65 | 100 | 71 | 52 | 25.544 | 9.868 | 6.9 | 133.22 | 28.132 | 28.072 | 27.183 | 602.669 | 25.457 | 26.201 | 1327.626 | 26.91 | 27.15 | 38.329 | 27.001 | 1.8 | 1.2 | 0 | 1 | 0.2
500 | 30/07/2025 09:31:57.153 | 97.824 | 66 | 100 | 69 | 52 | 28.689 | 9.862 | 6.902 | 133.145 | 28.115 | 28.092 | 27.152 | 602.55 | 25.439 | 26.195 | 1330.118 | 26.894 | 27.183 | 38.518 | 27.001 | 1.8 | 1.2 | 0 | 1 | 0.2
501 | 30/07/2025 09:31:58.792 | 97.752 | 66 | 100 | 70 | 54 | 25.91 | 9.876 | 6.902 | 133.43 | 28.128 | 28.086 | 27.182 | 602.581 | 25.449 | 26.186 | 1326.849 | 26.914 | 27.166 | 38.465 | 26.001 | 4.1 | 0.9 | 0.3 | 0 | 0.2
502 | 30/07/2025 09:32:00.426 | 97.944 | 66 | 100 | 70 | 53 | 27.58 | 9.582 | 6.903 | 132.436 | 28.12 | 28.227 | 27.133 | 602.34 | 25.437 | 26.196 | 1313.671 | 26.954 | 27.169 | 38.519 | 26.001 | 4.1 | 1.1 | 0.3 | 0 | 0.2
503 | 30/07/2025 09:32:02.066 | 97.992 | 65 | 100 | 70 | 52 | 29.659 | 9.838 | 6.9 | 132.001 | 28.139 | 28.062 | 27.167 | 602.467 | 25.482 | 26.214 | 1307.837 | 26.926 | 27.138 | 38.332 | 26.001 | 4.1 | 1.1 | 0.3 | 0 | 0.2
504 | 30/07/2025 09:32:03.699 | 98.544 | 66 | 100 | 70 | 52 | 28.011 | 9.876 | 6.865 | 131.579 | 28.109 | 28.087 | 27.177 | 602.651 | 25.468 | 26.186 | 1307.476 | 26.911 | 27.151 | 38.481 | 24.001 | 1.1 | 0.6 | 0.9 | 0.6 | 0.2
505 | 30/07/2025 09:32:05.334 | 98.952 | 67 | 100 | 70 | 52 | 25.77 | 9.874 | 6.833 | 131.788 | 28.117 | 28.082 | 27.167 | 602.395 | 25.448 | 26.229 | 1305.556 | 26.907 | 27.171 | 38.525 | 27.001 | 1.1 | 0.9 | 0.9 | 0.6 | 0.2
506 | 30/07/2025 09:32:06.968 | 98.784 | 68 | 100 | 70 | 52 | 29.045 | 9.878 | 6.829 | 131.772 | 28.112 | 28.234 | 27.146 | 602.49 | 25.461 | 26.215 | 1307.612 | 26.927 | 27.172 | 38.564 | 34.001 | 3.3 | 0.6 | 0 | 0 | 0.2
507 | 30/07/2025 09:32:08.603 | 99.072 | 66 | 100 | 71 | 52 | 25.653 | 9.801 | 6.829 | 131.75 | 28.109 | 28.08 | 27.145 | 602.308 | 25.474 | 26.232 | 1296.211 | 26.929 | 27.162 | 38.51 | 30.001 | 3.3 | 0 | 0 | 0 | 0.2
508 | 30/07/2025 09:32:10.239 | 99.024 | 68 | 100 | 71 | 52 | 28.152 | 9.731 | 6.827 | 131.815 | 28.107 | 28.198 | 27.191 | 602.69 | 25.474 | 26.211 | 1290.446 | 26.919 | 27.129 | 38.2 | 25.001 | 3.3 | 1.1 | 0.6 | 0.6 | 0.2
509 | 30/07/2025 09:32:11.890 | 99.816 | 68 | 100 | 70 | 52 | 29.681 | 9.753 | 6.829 | 131.357 | 28.1 | 31.651 | 27.152 | 602.419 | 25.46 | 26.24 | 1293.639 | 26.918 | 27.167 | 38.544 | 25.001 | 3.3 | 1.1 | 0.6 | 0.6 | 0.2
510 | 30/07/2025 09:32:13.526 | 99.936 | 69 | 100 | 70 | 52 | 27.471 | 9.781 | 6.828 | 132.087 | 28.098 | 28.222 | 27.157 | 602.558 | 25.488 | 26.224 | 1290.887 | 26.914 | 27.163 | 38.716 | 29.001 | 3.3 | 1 | 0.6 | 0.6 | 0.2
511 | 30/07/2025 09:32:15.160 | 100.008 | 67 | 100 | 70 | 52 | 26.115 | 9.809 | 6.828 | 131.818 | 28.101 | 28.074 | 27.143 | 602.487 | 25.456 | 26.207 | 1297.919 | 26.938 | 27.165 | 38.464 | 25.001 | 1.3 | 1.7 | 0.6 | 0.8 | 0.3
512 | 30/07/2025 09:32:16.794 | 99.624 | 69 | 100 | 70 | 52 | 28.727 | 9.867 | 6.828 | 131.953 | 28.124 | 28.194 | 27.155 | 602.572 | 25.486 | 26.211 | 1298.074 | 26.912 | 27.161 | 38.351 | 24.001 | 1.3 | 1.9 | 0.6 | 0.8 | 0.3
513 | 30/07/2025 09:32:18.428 | 99.384 | 68 | 100 | 71 | 52 | 25.658 | 9.882 | 6.828 | 131.572 | 28.115 | 28.068 | 27.157 | 602.567 | 25.449 | 26.213 | 1299.509 | 26.928 | 27.169 | 38.313 | 25.001 | 2.5 | 0.7 | 0 | 0.5 | 0.2
514 | 30/07/2025 09:32:20.061 | 99 | 67 | 100 | 70 | 53 | 28.797 | 9.808 | 6.902 | 131.582 | 28.115 | 28.222 | 27.162 | 602.444 | 25.458 | 26.214 | 1302.673 | 26.902 | 27.16 | 38.683 | 25.001 | 2.5 | 0.7 | 0 | 0.5 | 0.2
515 | 30/07/2025 09:32:21.695 | 98.76 | 67 | 100 | 71 | 52 | 29.772 | 9.8 | 6.901 | 132.021 | 28.126 | 28.074 | 27.165 | 602.742 | 25.458 | 26.206 | 1307.421 | 26.929 | 27.166 | 38.569 | 26.001 | 2.5 | 1.5 | 0 | 0.5 | 0.2
516 | 30/07/2025 09:32:23.331 | 99.168 | 67 | 99 | 70 | 52 | 26.943 | 9.783 | 6.902 | 131.677 | 28.118 | 28.154 | 27.131 | 602.406 | 25.446 | 26.215 | 1300.739 | 26.948 | 27.175 | 38.427 | 22.001 | 1.2 | 2.2 | 0.6 | 0.6 | 0.3
517 | 30/07/2025 09:32:24.966 | 98.64 | 67 | 100 | 70 | 52 | 26.553 | 9.766 | 6.934 | 131.984 | 28.145 | 28.056 | 27.163 | 602.598 | 25.479 | 26.213 | 1301.374 | 26.922 | 27.132 | 38.335 | 24.001 | 1.2 | 0.7 | 0.6 | 0.6 | 0.3
518 | 30/07/2025 09:32:26.602 | 98.856 | 67 | 100 | 71 | 52 | 28.06 | 9.736 | 6.936 | 131.537 | 28.125 | 28.08 | 27.16 | 602.435 | 25.45 | 26.22 | 1302.641 | 26.942 | 27.161 | 38.457 | 22.001 | 1.7 | 1.1 | 0 | 0.5 | 0.3
519 | 30/07/2025 09:32:28.236 | 99.312 | 67 | 100 | 70 | 53 | 25.797 | 9.792 | 6.936 | 131.955 | 28.145 | 28.079 | 27.167 | 602.279 | 25.461 | 26.208 | 1296.955 | 26.884 | 27.16 | 38.664 | 24.001 | 1.7 | 1.3 | 0 | 0.5 | 0.3
520 | 30/07/2025 09:32:29.880 | 98.976 | 67 | 100 | 70 | 53 | 29.126 | 9.811 | 6.936 | 131.935 | 28.115 | 28.093 | 27.143 | 602.564 | 25.445 | 26.192 | 1298.135 | 26.942 | 27.169 | 38.446 | 24.001 | 1.7 | 1.3 | 0 | 0.5 | 0.3
521 | 30/07/2025 09:32:31.513 | 99.24 | 68 | 100 | 70 | 52 | 29.776 | 9.816 | 6.938 | 131.796 | 28.12 | 28.203 | 27.153 | 603.61 | 25.452 | 26.198 | 1302.832 | 26.927 | 27.164 | 38.343 | 27.001 | 2.2 | 0.7 | 0 | 0.8 | 0.2
522 | 30/07/2025 09:32:33.150 | 99.624 | 68 | 100 | 70 | 52 | 26.433 | 9.722 | 6.933 | 131.72 | 28.116 | 28.067 | 27.188 | 603.862 | 25.449 | 26.192 | 1300.95 | 26.917 | 27.134 | 38.398 | 25.001 | 2.2 | 0.6 | 0 | 0.8 | 0.2
523 | 30/07/2025 09:32:34.783 | 99.816 | 68 | 100 | 71 | 52 | 29.747 | 9.726 | 6.936 | 131.628 | 28.13 | 28.22 | 27.15 | 603.123 | 25.462 | 26.197 | 1300.927 | 26.905 | 27.157 | 38.571 | 28.001 | 2.6 | 1.1 | 0 | 0 | 0.2
524 | 30/07/2025 09:32:36.417 | 100.008 | 69 | 100 | 73 | 52 | 27.467 | 9.577 | 6.902 | 131.896 | 28.122 | 28.199 | 27.17 | 602.652 | 25.464 | 26.194 | 1301.205 | 26.893 | 27.163 | 38.469 | 28.001 | 2.6 | 1 | 0 | 0 | 0.2
525 | 30/07/2025 09:32:38.051 | 100.248 | 70 | 100 | 70 | 52 | 26.118 | 9.729 | 6.903 | 131.779 | 28.115 | 28.078 | 27.13 | 603.552 | 25.469 | 26.212 | 1300.43 | 26.954 | 27.168 | 38.52 | 28.001 | 2.6 | 1 | 0 | 0 | 0.2
526 | 30/07/2025 09:32:39.687 | 100.728 | 69 | 100 | 70 | 52 | 29.352 | 9.613 | 6.9 | 131.853 | 28.13 | 28.195 | 27.163 | 603.811 | 25.485 | 26.213 | 1295.876 | 26.918 | 27.15 | 38.204 | 25.001 | 3.8 | 1.2 | 0.7 | 0.4 | 0.3
527 | 30/07/2025 09:32:41.324 | 100.272 | 69 | 100 | 71 | 53 | 29.524 | 9.793 | 6.9 | 131.577 | 28.098 | 28.092 | 27.171 | 602.576 | 25.459 | 26.219 | 1275.625 | 26.924 | 27.162 | 38.434 | 28.001 | 3.8 | 0.9 | 0.7 | 0.4 | 0.3
528 | 30/07/2025 09:32:42.958 | 100.656 | 70 | 100 | 71 | 52 | 25.914 | 9.5 | 6.917 | 131.732 | 28.116 | 28.226 | 27.161 | 602.379 | 25.469 | 26.239 | 1270.422 | 26.894 | 27.167 | 38.605 | 28.001 | 2.9 | 0.9 | 0.9 | 0 | 0.3
529 | 30/07/2025 09:32:44.593 | 100.392 | 69 | 100 | 70 | 52 | 29.76 | 9.549 | 6.936 | 131.745 | 28.098 | 28.231 | 27.157 | 602.441 | 25.476 | 26.221 | 1270.616 | 26.933 | 27.174 | 38.496 | 26.001 | 2.9 | 0.7 | 0.9 | 0 | 0.3
530 | 30/07/2025 09:32:46.228 | 100.056 | 69 | 100 | 71 | 52 | 26.854 | 9.576 | 6.947 | 131.852 | 28.098 | 28.122 | 27.137 | 602.282 | 25.47 | 26.206 | 1268.207 | 26.929 | 27.157 | 38.48 | 26.001 | 2.9 | 0.7 | 0.9 | 0 | 0.3
531 | 30/07/2025 09:32:47.864 | 99.696 | 68 | 100 | 71 | 52 | 26.481 | 9.579 | 6.986 | 133.248 | 28.092 | 28.061 | 27.17 | 602.485 | 25.469 | 26.208 | 1274.563 | 26.926 | 27.144 | 38.018 | 25.001 | 3.6 | 1.4 | 0.6 | 0.5 | 0.3
532 | 30/07/2025 09:32:49.499 | 99.36 | 68 | 100 | 71 | 53 | 29.511 | 9.733 | 7.006 | 132.977 | 28.097 | 28.085 | 27.163 | 602.464 | 25.452 | 26.224 | 1270.941 | 26.928 | 27.165 | 38.472 | 25.001 | 3.6 | 2.8 | 0.6 | 0.5 | 0.3
533 | 30/07/2025 09:32:51.131 | 99.504 | 69 | 100 | 70 | 52 | 29.181 | 9.797 | 7.006 | 133.678 | 28.115 | 28.223 | 27.156 | 602.42 | 25.476 | 26.215 | 1275.596 | 26.909 | 27.175 | 38.535 | 34.001 | 2.6 | 2.3 | 0.1 | 0 | 0.3
534 | 30/07/2025 09:32:52.766 | 99.912 | 68 | 100 | 70 | 53 | 29.139 | 9.768 | 7.008 | 133.421 | 28.101 | 28.068 | 27.151 | 602.375 | 25.456 | 26.224 | 1278.117 | 26.941 | 27.164 | 38.441 | 30.001 | 2.6 | 1.8 | 0.1 | 0 | 0.3
535 | 30/07/2025 09:32:54.401 | 100.392 | 68 | 100 | 70 | 52 | 29.724 | 9.584 | 7.006 | 133.324 | 28.287 | 28.209 | 27.154 | 601.093 | 25.476 | 26.207 | 1279.665 | 26.913 | 27.167 | 38.405 | 26.001 | 1.3 | 2 | 0 | 0.5 | 0.2
536 | 30/07/2025 09:32:56.036 | 99.96 | 69 | 100 | 70 | 52 | 26.375 | 9.579 | 7.005 | 133.015 | 28.128 | 28.114 | 27.162 | 602.499 | 25.457 | 26.213 | 1299.557 | 26.936 | 27.154 | 38.229 | 26.001 | 1.3 | 2 | 0 | 0.5 | 0.2
537 | 30/07/2025 09:32:57.670 | 99.288 | 68 | 100 | 71 | 52 | 30.643 | 9.844 | 6.989 | 132.973 | 28.274 | 28.226 | 27.157 | 601.043 | 25.466 | 26.205 | 1300.057 | 26.897 | 27.154 | 38.577 | 29.001 | 1.3 | 1.6 | 0 | 0.5 | 0.2
538 | 30/07/2025 09:32:59.361 | 99.504 | 69 | 100 | 71 | 52 | 29.651 | 9.532 | 6.988 | 133.312 | 28.277 | 28.215 | 27.165 | 602.536 | 25.44 | 26.203 | 1300.234 | 26.925 | 27.163 | 38.417 | 29.001 | 3.5 | 1 | 0.9 | 0.5 | 0.2
539 | 30/07/2025 09:33:00.999 | 99.768 | 68 | 100 | 72 | 51 | 28.674 | 9.503 | 6.988 | 133.164 | 28.276 | 28.207 | 27.124 | 602.362 | 25.449 | 26.209 | 1304.484 | 26.95 | 27.167 | 38.421 | 29.001 | 3.5 | 0.7 | 0.9 | 0.5 | 0.2
540 | 30/07/2025 09:33:02.635 | 99.432 | 68 | 100 | 71 | 53 | 29.382 | 9.429 | 6.987 | 133.298 | 28.264 | 28.205 | 27.163 | 602.637 | 25.428 | 26.196 | 1302.839 | 26.92 | 27.161 | 38.103 | 28.001 | 3.2 | 1.7 | 0.3 | 1.1 | 0.2
541 | 30/07/2025 09:33:04.271 | 98.952 | 68 | 100 | 71 | 53 | 29.527 | 9.571 | 6.988 | 133.161 | 28.274 | 28.099 | 27.153 | 602.452 | 25.436 | 26.194 | 1312.335 | 26.924 | 27.137 | 38.309 | 27.001 | 3.2 | 2.3 | 0.3 | 1.1 | 0.2
542 | 30/07/2025 09:33:05.906 | 98.76 | 68 | 100 | 70 | 52 | 26.032 | 9.571 | 6.988 | 133.286 | 28.233 | 28.229 | 27.16 | 602.356 | 25.461 | 26.175 | 1314.46 | 26.894 | 27.17 | 38.436 | 27.001 | 3.2 | 2.3 | 0.3 | 1.1 | 0.2
543 | 30/07/2025 09:33:07.542 | 98.544 | 67 | 100 | 70 | 52 | 27.669 | 9.719 | 6.989 | 133.357 | 28.105 | 28.184 | 27.139 | 602.468 | 25.444 | 26.2 | 1307.811 | 26.947 | 27.188 | 38.443 | 30.001 | 2.6 | 1 | 1.2 | 0.2 | 0.4
544 | 30/07/2025 09:33:09.181 | 98.568 | 67 | 100 | 71 | 52 | 29.718 | 9.575 | 6.989 | 133.334 | 28.281 | 28.21 | 27.154 | 603.502 | 25.466 | 26.201 | 1299.019 | 26.931 | 27.153 | 38.449 | 28.001 | 2.6 | 0.8 | 1.2 | 0.2 | 0.4
545 | 30/07/2025 09:33:10.814 | 98.136 | 67 | 100 | 71 | 52 | 26.614 | 9.59 | 6.991 | 134.623 | 28.272 | 28.199 | 27.169 | 603.739 | 25.45 | 26.199 | 1293.719 | 26.931 | 27.164 | 38.232 | 33.001 | 1.5 | 1.3 | 0.6 | 0.5 | 0.4
546 | 30/07/2025 09:33:12.449 | 98.064 | 67 | 100 | 71 | 52 | 29.547 | 9.524 | 7.032 | 134.604 | 28.263 | 28.15 | 27.157 | 603.712 | 25.479 | 26.2 | 1288.238 | 26.897 | 27.145 | 38.533 | 30.001 | 1.5 | 0.9 | 0.6 | 0.5 | 0.4
547 | 30/07/2025 09:33:14.081 | 97.92 | 66 | 100 | 70 | 52 | 29.158 | 9.727 | 6.99 | 134.761 | 28.259 | 28.232 | 27.162 | 603.662 | 25.466 | 26.217 | 1292.024 | 26.9 | 27.167 | 38.556 | 30.001 | 1.5 | 0.9 | 0.6 | 0.5 | 0.4
548 | 30/07/2025 09:33:15.714 | 97.656 | 66 | 100 | 70 | 52 | 25.707 | 9.754 | 6.99 | 134.687 | 28.248 | 28.073 | 27.135 | 603.461 | 25.468 | 26.243 | 1285.649 | 26.947 | 27.165 | 38.584 | 24.001 | 2 | 1.3 | 0 | 0.6 | 0.4
549 | 30/07/2025 09:33:17.346 | 97.608 | 67 | 100 | 70 | 52 | 28.066 | 9.801 | 7.005 | 134.791 | 28.286 | 28.2 | 27.17 | 603.851 | 25.449 | 26.228 | 1283.288 | 26.916 | 27.153 | 38.287 | 29.001 | 2 | 1.4 | 0 | 0.6 | 0.4
550 | 30/07/2025 09:33:18.979 | 97.848 | 68 | 100 | 69 | 51 | 26.353 | 9.582 | 7.005 | 134.625 | 28.241 | 28.195 | 27.178 | 603.636 | 25.471 | 26.237 | 1287.313 | 26.93 | 27.131 | 38.226 | 29.001 | 1.9 | 1.4 | 0 | 0.5 | 0.4
551 | 30/07/2025 09:33:20.612 | 97.584 | 67 | 100 | 71 | 51 | 27.026 | 9.73 | 7.006 | 134.583 | 28.247 | 28.224 | 27.168 | 603.734 | 25.477 | 26.223 | 1288.645 | 26.893 | 27.164 | 38.478 | 25.001 | 1.9 | 0.9 | 0 | 0.5 | 0.4
552 | 30/07/2025 09:33:22.245 | 97.776 | 68 | 100 | 71 | 51 | 29.593 | 9.486 | 6.938 | 134.652 | 28.239 | 28.242 | 27.144 | 603.628 | 25.46 | 26.221 | 1302.617 | 26.924 | 27.179 | 38.456 | 25.001 | 3.6 | 0.2 | 0 | 0 | 0.4
553 | 30/07/2025 09:33:23.880 | 97.272 | 68 | 100 | 70 | 52 | 28.734 | 9.726 | 6.936 | 134.838 | 28.252 | 28.216 | 27.131 | 603.501 | 25.483 | 26.215 | 1307.479 | 26.93 | 27.153 | 38.443 | 25.001 | 3.6 | 0.2 | 0 | 0 | 0.4
554 | 30/07/2025 09:33:25.517 | 97.536 | 68 | 100 | 70 | 52 | 25.613 | 9.747 | 6.985 | 134.829 | 28.261 | 28.203 | 27.166 | 603.724 | 25.456 | 26.215 | 1307.669 | 26.929 | 27.149 | 38.238 | 25.001 | 3.6 | 1.4 | 0 | 0 | 0.4
555 | 30/07/2025 09:33:27.151 | 97.56 | 66 | 100 | 71 | 52 | 28.732 | 9.501 | 6.989 | 134.595 | 28.258 | 28.224 | 27.155 | 603.62 | 25.465 | 26.23 | 1311.622 | 26.926 | 27.147 | 38.5 | 32.001 | 3 | 1 | 0.7 | 0.6 | 0.4
556 | 30/07/2025 09:33:28.786 | 97.368 | 66 | 100 | 70 | 50 | 25.941 | 9.556 | 6.988 | 134.574 | 28.267 | 28.235 | 27.161 | 603.683 | 25.457 | 26.209 | 1317.778 | 26.894 | 27.174 | 38.454 | 26.001 | 3 | 0.8 | 0.7 | 0.6 | 0.4
557 | 30/07/2025 09:33:30.418 | 97.344 | 66 | 100 | 70 | 52 | 27.68 | 9.72 | 7.007 | 134.746 | 28.274 | 28.218 | 27.141 | 602.309 | 25.463 | 26.23 | 1308.153 | 26.927 | 27.161 | 38.601 | 27.001 | 2 | 1 | 0 | 0 | 0.3
558 | 30/07/2025 09:33:32.050 | 97.2 | 66 | 100 | 70 | 52 | 29.704 | 9.68 | 7.006 | 134.737 | 28.283 | 28.214 | 27.156 | 602.678 | 25.458 | 26.201 | 1317.061 | 26.923 | 27.164 | 38.479 | 27.001 | 2 | 1 | 0 | 0 | 0.3
559 | 30/07/2025 09:33:33.681 | 97.2 | 66 | 100 | 70 | 52 | 28.154 | 10.027 | 6.988 | 134.537 | 28.267 | 28.222 | 27.17 | 602.507 | 25.456 | 26.217 | 1327.689 | 26.941 | 27.153 | 38.265 | 22.001 | 2 | 1 | 0 | 0 | 0.3
560 | 30/07/2025 09:33:35.314 | 96.576 | 67 | 100 | 71 | 52 | 25.832 | 9.731 | 6.937 | 134.455 | 28.29 | 28.082 | 27.153 | 602.39 | 25.454 | 26.208 | 1337.144 | 26.899 | 27.165 | 38.804 | 22.001 | 2.1 | 1.3 | 1.2 | 0.1 | 0.3
561 | 30/07/2025 09:33:36.949 | 96.792 | 66 | 100 | 71 | 52 | 29.175 | 9.624 | 6.937 | 134.602 | 28.269 | 28.089 | 27.145 | 602.365 | 25.459 | 26.208 | 1340.078 | 26.921 | 27.176 | 38.523 | 27.001 | 2.1 | 0.9 | 1.2 | 0.1 | 0.3
562 | 30/07/2025 09:33:38.586 | 96.912 | 67 | 100 | 71 | 52 | 25.763 | 9.72 | 6.936 | 134.928 | 28.281 | 28.231 | 27.126 | 602.34 | 25.456 | 26.219 | 1348.207 | 26.936 | 27.164 | 38.591 | 30.001 | 3.9 | 0.8 | 0.6 | 1.2 | 0.3
563 | 30/07/2025 09:33:40.219 | 96.888 | 67 | 100 | 70 | 52 | 28.345 | 10.011 | 6.935 | 134.78 | 28.269 | 28.211 | 27.167 | 602.604 | 25.448 | 26.185 | 1342.672 | 26.931 | 27.156 | 38.403 | 30.001 | 3.9 | 0.8 | 0.6 | 1.2 | 0.3
564 | 30/07/2025 09:33:41.852 | 96.648 | 66 | 100 | 70 | 52 | 29.802 | 9.881 | 6.986 | 134.43 | 28.275 | 28.218 | 27.161 | 602.447 | 25.459 | 26.203 | 1337.423 | 26.927 | 27.146 | 38.348 | 26.001 | 3.9 | 0.6 | 0.6 | 1.2 | 0.3
565 | 30/07/2025 09:33:43.487 | 96.528 | 68 | 100 | 70 | 52 | 27.558 | 9.844 | 6.937 | 134.713 | 28.274 | 28.224 | 27.171 | 602.69 | 25.469 | 26.183 | 1322.487 | 26.899 | 27.174 | 38.433 | 27.001 | 3.3 | 0.7 | 1.2 | 0.2 | 0.2
566 | 30/07/2025 09:33:45.123 | 96.6 | 66 | 100 | 70 | 53 | 26.175 | 9.572 | 6.936 | 133.384 | 28.267 | 28.235 | 27.135 | 602.415 | 25.47 | 26.208 | 1318.161 | 26.95 | 27.184 | 38.73 | 27.001 | 3.3 | 1.6 | 1.2 | 0.2 | 0.2
567 | 30/07/2025 09:33:46.760 | 96.504 | 67 | 100 | 70 | 54 | 28.748 | 9.729 | 6.935 | 133.238 | 28.266 | 28.224 | 27.141 | 602.342 | 25.463 | 26.194 | 1315.838 | 26.932 | 27.161 | 38.514 | 29.001 | 3.4 | 1.3 | 0 | 0.5 | 0.2
568 | 30/07/2025 09:33:48.395 | 96.432 | 66 | 100 | 71 | 52 | 25.722 | 9.729 | 6.937 | 133.196 | 28.258 | 28.198 | 27.153 | 602.552 | 25.456 | 26.235 | 1298.957 | 26.954 | 27.153 | 38.28 | 28.001 | 3.4 | 1.1 | 0 | 0.5 | 0.2
569 | 30/07/2025 09:33:50.032 | 95.688 | 66 | 100 | 71 | 52 | 28.602 | 9.875 | 6.935 | 133.292 | 28.276 | 28.219 | 27.17 | 602.5 | 25.485 | 26.226 | 1302.307 | 26.899 | 27.146 | 38.468 | 28.001 | 3.4 | 1.1 | 0 | 0.5 | 0.2
570 | 30/07/2025 09:33:51.666 | 96.072 | 66 | 100 | 71 | 54 | 29.885 | 9.739 | 6.937 | 133.139 | 28.24 | 28.229 | 27.169 | 602.553 | 25.459 | 26.21 | 1307.987 | 26.899 | 27.16 | 38.693 | 26.001 | 2.4 | 0.2 | 0 | 0.5 | 0.1
571 | 30/07/2025 09:33:53.302 | 96.24 | 66 | 100 | 71 | 52 | 26.986 | 9.729 | 6.939 | 133.32 | 28.255 | 28.221 | 27.142 | 602.212 | 25.471 | 26.233 | 1310.393 | 26.949 | 27.165 | 38.569 | 27.001 | 2.4 | 1.1 | 0 | 0.5 | 0.1
572 | 30/07/2025 09:33:54.938 | 96.84 | 67 | 100 | 70 | 53 | 29.803 | 9.587 | 6.936 | 133.257 | 28.238 | 28.227 | 27.121 | 602.352 | 25.453 | 26.223 | 1317.598 | 26.932 | 27.177 | 38.356 | 35.001 | 3.5 | 1.4 | 0 | 0.6 | 0.2
573 | 30/07/2025 09:33:56.573 | 96.792 | 67 | 100 | 71 | 52 | 28.226 | 9.509 | 6.934 | 133.236 | 28.239 | 28.198 | 27.17 | 602.485 | 25.458 | 26.226 | 1307.645 | 26.927 | 27.145 | 38.349 | 31.001 | 3.5 | 1.3 | 0 | 0.6 | 0.2
574 | 30/07/2025 09:33:58.206 | 97.08 | 66 | 100 | 70 | 53 | 25.805 | 9.58 | 6.935 | 133.155 | 28.25 | 28.234 | 27.176 | 602.573 | 25.47 | 26.213 | 1307.58 | 26.895 | 27.162 | 38.602 | 31.001 | 3.5 | 1.3 | 0 | 0.6 | 0.2
575 | 30/07/2025 09:33:59.842 | 97.656 | 67 | 99 | 70 | 52 | 29.132 | 9.576 | 6.938 | 133.227 | 28.248 | 28.234 | 27.15 | 602.421 | 25.461 | 26.219 | 1307.801 | 26.938 | 27.177 | 38.551 | 19 | 3.8 | 0.4 | 1 | 0.5 | 0.3
576 | 30/07/2025 09:34:01.476 | 98.064 | 68 | 100 | 70 | 52 | 29.775 | 9.433 | 6.936 | 133.293 | 28.28 | 28.217 | 27.133 | 602.371 | 25.483 | 26.208 | 1307.97 | 26.93 | 27.15 | 38.518 | 21.001 | 3.8 | 1.2 | 1 | 0.5 | 0.3
577 | 30/07/2025 09:34:03.112 | 98.28 | 67 | 100 | 71 | 53 | 26.417 | 9.579 | 6.934 | 131.765 | 28.273 | 28.201 | 27.162 | 602.529 | 25.451 | 26.212 | 1296.402 | 26.928 | 27.155 | 38.287 | 22.001 | 1.9 | 2.5 | 0 | 0.5 | 0.3
578 | 30/07/2025 09:34:04.749 | 98.04 | 68 | 100 | 70 | 54 | 29.82 | 9.624 | 6.933 | 131.726 | 28.298 | 28.211 | 27.17 | 602.484 | 25.475 | 26.206 | 1293.233 | 26.921 | 27.145 | 38.565 | 24.001 | 1.9 | 2.6 | 0 | 0.5 | 0.3
579 | 30/07/2025 09:34:06.387 | 98.424 | 67 | 100 | 70 | 52 | 27.51 | 9.799 | 6.99 | 131.598 | 28.266 | 28.237 | 27.157 | 602.467 | 25.438 | 26.217 | 1278.612 | 26.902 | 27.182 | 38.562 | 28.001 | 4.3 | 0.9 | 0.6 | 0.6 | 0.2
580 | 30/07/2025 09:34:08.022 | 98.712 | 68 | 100 | 70 | 52 | 26.148 | 9.666 | 6.989 | 131.864 | 28.282 | 28.223 | 27.147 | 602.381 | 25.46 | 26.215 | 1286.563 | 26.925 | 27.167 | 38.58 | 28.001 | 4.3 | 0.9 | 0.6 | 0.6 | 0.2
581 | 30/07/2025 09:34:09.658 | 99 | 67 | 100 | 70 | 54 | 29.413 | 9.573 | 6.987 | 131.811 | 28.271 | 28.222 | 27.151 | 602.296 | 25.45 | 26.194 | 1289.266 | 26.93 | 27.157 | 38.39 | 29.001 | 4.3 | 0.6 | 0.6 | 0.6 | 0.2
582 | 30/07/2025 09:34:11.295 | 99.408 | 69 | 100 | 71 | 53 | 29.607 | 9.509 | 6.986 | 131.572 | 28.271 | 28.213 | 27.165 | 602.41 | 25.411 | 26.2 | 1297.648 | 26.941 | 27.162 | 38.155 | 21.001 | 2.9 | 0.9 | 0.6 | 0.6 | 0.2
583 | 30/07/2025 09:34:12.932 | 99.96 | 69 | 100 | 71 | 52 | 28.792 | 9.577 | 6.985 | 131.676 | 28.285 | 28.221 | 27.177 | 602.554 | 25.447 | 26.198 | 1303.882 | 26.922 | 27.148 | 38.305 | 28.001 | 2.9 | 1.6 | 0.6 | 0.6 | 0.2
584 | 30/07/2025 09:34:14.568 | 99.552 | 68 | 100 | 71 | 53 | 29.894 | 9.578 | 6.938 | 131.698 | 28.264 | 28.226 | 27.144 | 602.277 | 25.442 | 26.202 | 1307.855 | 26.909 | 27.179 | 38.641 | 26.001 | 3.1 | 2 | 0.3 | 0 | 0.2
585 | 30/07/2025 09:34:16.203 | 99.72 | 69 | 100 | 70 | 51 | 27.12 | 9.422 | 6.921 | 131.982 | 28.283 | 28.219 | 27.148 | 602.462 | 25.473 | 26.195 | 1316.221 | 26.921 | 27.168 | 38.585 | 26.001 | 3.1 | 2 | 0.3 | 0 | 0.2
586 | 30/07/2025 09:34:17.838 | 98.904 | 68 | 100 | 71 | 52 | 26.699 | 9.579 | 6.9 | 133.123 | 28.25 | 28.213 | 27.153 | 602.419 | 25.454 | 26.2 | 1307.583 | 26.939 | 27.176 | 38.304 | 27.001 | 3.1 | 1.2 | 0.3 | 0 | 0.2
587 | 30/07/2025 09:34:19.472 | 98.64 | 68 | 100 | 70 | 52 | 29.62 | 9.677 | 6.935 | 133.217 | 28.258 | 28.207 | 27.166 | 603.401 | 25.481 | 26.217 | 1305.383 | 26.925 | 27.141 | 38.329 | 29.001 | 2.5 | 1.5 | 0.6 | 0.6 | 0.1
588 | 30/07/2025 09:34:21.106 | 98.136 | 68 | 100 | 71 | 52 | 25.911 | 9.582 | 6.936 | 133.075 | 28.26 | 28.24 | 27.153 | 603.657 | 25.468 | 26.211 | 1300.773 | 26.921 | 27.173 | 38.384 | 26.001 | 2.5 | 1.6 | 0.6 | 0.6 | 0.1
589 | 30/07/2025 09:34:22.740 | 98.496 | 68 | 100 | 70 | 53 | 29.253 | 9.576 | 6.988 | 133.344 | 28.263 | 28.224 | 27.147 | 603.733 | 25.47 | 26.216 | 1302.94 | 26.904 | 27.161 | 38.502 | 24.001 | 4.6 | 0.7 | 0 | 0.1 | 0.2
590 | 30/07/2025 09:34:24.377 | 98.472 | 68 | 100 | 70 | 52 | 29.811 | 9.651 | 6.955 | 133.266 | 28.26 | 28.219 | 27.12 | 602.517 | 25.473 | 26.219 | 1305.304 | 26.928 | 27.164 | 38.328 | 26.001 | 4.6 | 0.8 | 0 | 0.1 | 0.2
591 | 30/07/2025 09:34:26.012 | 98.064 | 66 | 99 | 71 | 52 | 26.542 | 9.566 | 6.936 | 133.051 | 28.238 | 28.201 | 27.155 | 602.356 | 25.463 | 26.236 | 1308.126 | 26.948 | 27.158 | 38.128 | 26.001 | 4.6 | 0.8 | 0 | 0.1 | 0.2
592 | 30/07/2025 09:34:27.649 | 98.232 | 67 | 100 | 71 | 52 | 27.051 | 9.731 | 6.985 | 133.253 | 28.262 | 28.219 | 27.169 | 602.655 | 25.48 | 26.217 | 1291.995 | 26.914 | 27.153 | 38.505 | 30.001 | 2.7 | 1 | 0.6 | 0.8 | 0.2
593 | 30/07/2025 09:34:29.285 | 98.376 | 67 | 100 | 70 | 52 | 29.722 | 9.727 | 6.99 | 133.268 | 28.24 | 28.239 | 27.166 | 603.76 | 25.459 | 26.215 | 1298.08 | 26.896 | 27.177 | 38.549 | 23.001 | 2.7 | 0.8 | 0.6 | 0.8 | 0.2
594 | 30/07/2025 09:34:30.921 | 98.088 | 69 | 100 | 70 | 53 | 26.084 | 9.727 | 6.988 | 133.384 | 28.242 | 28.222 | 27.158 | 603.767 | 25.478 | 26.213 | 1300.368 | 26.911 | 27.17 | 38.466 | 25.001 | 3.5 | 1.7 | 1.2 | 0.5 | 0.2
595 | 30/07/2025 09:34:32.556 | 98.112 | 68 | 100 | 70 | 52 | 29.4 | 9.581 | 6.959 | 133.22 | 28.244 | 28.219 | 27.135 | 603.593 | 25.452 | 26.218 | 1300.132 | 26.933 | 27.186 | 38.409 | 21.001 | 3.5 | 2 | 1.2 | 0.5 | 0.2
596 | 30/07/2025 09:34:34.190 | 97.968 | 67 | 100 | 71 | 51 | 29.596 | 9.837 | 6.936 | 133.36 | 28.26 | 28.193 | 27.163 | 603.69 | 25.465 | 26.23 | 1288.131 | 26.922 | 27.141 | 38.318 | 21.001 | 3.5 | 2 | 1.2 | 0.5 | 0.2
597 | 30/07/2025 09:34:35.827 | 97.392 | 68 | 100 | 72 | 52 | 26.005 | 9.43 | 6.936 | 133.038 | 28.251 | 28.234 | 27.168 | 603.735 | 25.461 | 26.216 | 1297.613 | 26.9 | 27.163 | 38.544 | 25.001 | 4.1 | 1 | 0.1 | 1 | 0.2
598 | 30/07/2025 09:34:37.464 | 97.608 | 68 | 100 | 72 | 52 | 27.676 | 9.833 | 6.938 | 133.246 | 28.274 | 28.224 | 27.158 | 603.528 | 25.455 | 26.219 | 1297.713 | 26.934 | 27.167 | 38.573 | 28.001 | 4.1 | 1 | 0.1 | 1 | 0.2
599 | 30/07/2025 09:34:39.097 | 97.728 | 67 | 100 | 70 | 53 | 26.948 | 9.874 | 6.936 | 133.223 | 28.276 | 28.237 | 27.155 | 603.689 | 25.458 | 26.214 | 1288.711 | 26.934 | 27.169 | 38.55 | 28.001 | 1.3 | 1.9 | 0 | 0.5 | 0.2
600 | 30/07/2025 09:34:40.733 | 97.512 | 67 | 100 | 70 | 52 | 26.572 | 9.473 | 6.936 | 133.25 | 28.272 | 28.204 | 27.13 | 603.454 | 25.45 | 26.223 | 1297.746 | 26.945 | 27.153 | 38.432 | 27.001 | 1.3 | 0.8 | 0 | 0.5 | 0.2
601 | 30/07/2025 09:34:42.368 | 97.536 | 67 | 100 | 70 | 52 | 29.553 | 9.495 | 6.934 | 133.222 | 28.272 | 28.206 | 27.171 | 603.77 | 25.452 | 26.204 | 1298.947 | 26.925 | 27.148 | 38.194 | 27.001 | 3.7 | 1.6 | 0 | 0.5 | 0.2
602 | 30/07/2025 09:34:44.004 | 97.584 | 68 | 99 | 70 | 52 | 29.271 | 9.629 | 6.937 | 133.089 | 28.258 | 28.24 | 27.157 | 603.583 | 25.435 | 26.2 | 1309.741 | 26.914 | 27.186 | 38.466 | 27.001 | 3.7 | 1.6 | 0 | 0.5 | 0.2
603 | 30/07/2025 09:34:45.639 | 97.656 | 66 | 100 | 70 | 53 | 25.837 | 9.744 | 6.943 | 133.331 | 28.276 | 28.22 | 27.146 | 603.559 | 25.454 | 26.195 | 1317.016 | 26.914 | 27.161 | 38.559 | 26.001 | 3.7 | 0.7 | 0 | 0.5 | 0.2
604 | 30/07/2025 09:34:47.275 | 97.824 | 68 | 100 | 70 | 52 | 28.257 | 9.502 | 6.987 | 133.221 | 28.267 | 28.215 | 27.152 | 603.587 | 25.454 | 26.189 | 1313.476 | 26.933 | 27.158 | 38.385 | 23.001 | 2.6 | 2.8 | 2.4 | 0 | 0.2
605 | 30/07/2025 09:34:48.912 | 97.56 | 65 | 100 | 70 | 52 | 26.491 | 9.699 | 6.988 | 133.332 | 28.275 | 28.213 | 27.153 | 603.637 | 25.463 | 26.198 | 1310.169 | 26.926 | 27.146 | 38.525 | 28.001 | 2.6 | 1.6 | 2.4 | 0 | 0.2
606 | 30/07/2025 09:34:50.546 | 97.488 | 67 | 100 | 71 | 52 | 27.173 | 9.588 | 6.986 | 133.128 | 28.263 | 28.223 | 27.16 | 603.752 | 25.448 | 26.202 | 1312.696 | 26.921 | 27.143 | 38.391 | 22.001 | 3.8 | 0.8 | 0.6 | 0.5 | 0.2
607 | 30/07/2025 09:34:52.179 | 97.8 | 67 | 100 | 70 | 51 | 29.709 | 9.772 | 6.939 | 133.088 | 28.272 | 28.224 | 27.154 | 602.988 | 25.466 | 26.208 | 1309.695 | 26.911 | 27.179 | 38.713 | 22.001 | 3.8 | 0.8 | 0.6 | 0.5 | 0.2
608 | 30/07/2025 09:34:53.816 | 98.4 | 68 | 100 | 70 | 52 | 28.81 | 9.718 | 6.935 | 133.475 | 28.281 | 28.226 | 27.149 | 602.399 | 25.463 | 26.209 | 1307.821 | 26.931 | 27.164 | 38.541 | 29.001 | 3.8 | 1.9 | 0.6 | 0.5 | 0.2
609 | 30/07/2025 09:34:55.450 | 97.992 | 68 | 100 | 71 | 52 | 25.79 | 9.562 | 6.988 | 133.172 | 28.258 | 28.226 | 27.142 | 602.353 | 25.466 | 26.219 | 1315.882 | 26.937 | 27.175 | 38.258 | 24.001 | 2.3 | 1.1 | 1.5 | 0.2 | 0.2
610 | 30/07/2025 09:34:57.083 | 97.824 | 68 | 100 | 70 | 52 | 28.734 | 9.452 | 6.935 | 133.23 | 28.258 | 28.213 | 27.161 | 602.444 | 25.471 | 26.218 | 1326.045 | 26.918 | 27.137 | 38.24 | 28.001 | 2.3 | 0.7 | 1.5 | 0.2 | 0.2
611 | 30/07/2025 09:34:58.719 | 97.704 | 66 | 100 | 71 | 53 | 26.132 | 9.574 | 6.937 | 133.098 | 28.25 | 28.242 | 27.169 | 602.303 | 25.45 | 26.222 | 1327.281 | 26.926 | 27.168 | 38.521 | 31.001 | 2.3 | 1.1 | 0.6 | 0 | 0.1
612 | 30/07/2025 09:35:00.352 | 97.632 | 68 | 100 | 71 | 52 | 27.63 | 9.73 | 6.937 | 133.403 | 28.256 | 28.222 | 27.154 | 602.454 | 25.468 | 26.233 | 1329.583 | 26.886 | 27.17 | 38.482 | 33.001 | 2.3 | 2.8 | 0.6 | 0 | 0.1
613 | 30/07/2025 09:35:01.987 | 97.944 | 66 | 100 | 71 | 52 | 29.762 | 9.576 | 6.936 | 133.249 | 28.231 | 28.221 | 27.127 | 600.877 | 25.468 | 26.221 | 1325.23 | 26.928 | 27.178 | 38.403 | 33.001 | 2.3 | 2.8 | 0.6 | 0 | 0.1
614 | 30/07/2025 09:35:03.707 | 97.896 | 68 | 100 | 71 | 52 | 28.296 | 9.582 | 6.936 | 133.15 | 28.242 | 28.205 | 27.146 | 600.864 | 25.462 | 26.235 | 1334.773 | 26.939 | 27.156 | 38.218 | 29.001 | 1.9 | 1.6 | 0.6 | 0.5 | 0.2
615 | 30/07/2025 09:35:05.341 | 97.896 | 68 | 100 | 70 | 52 | 25.836 | 9.799 | 6.934 | 133.035 | 28.272 | 28.228 | 27.175 | 601.008 | 25.483 | 26.215 | 1324.669 | 26.911 | 27.145 | 38.425 | 23.001 | 1.9 | 0.1 | 0.6 | 0.5 | 0.2
616 | 30/07/2025 09:35:06.977 | 98.472 | 69 | 99 | 70 | 52 | 29.303 | 9.822 | 6.938 | 132.967 | 28.253 | 28.235 | 27.137 | 600.94 | 25.469 | 26.223 | 1317.881 | 26.914 | 27.164 | 38.566 | 27.001 | 3.3 | 0.6 | 0.7 | 0.5 | 0.1
617 | 30/07/2025 09:35:08.612 | 98.184 | 67 | 100 | 70 | 53 | 25.814 | 9.571 | 6.935 | 133.425 | 28.265 | 28.232 | 27.15 | 601.2 | 25.451 | 26.199 | 1322.373 | 26.909 | 27.16 | 38.609 | 25.001 | 3.3 | 1.3 | 0.7 | 0.5 | 0.1
618 | 30/07/2025 09:35:10.247 | 98.16 | 68 | 100 | 70 | 52 | 28.232 | 9.575 | 6.937 | 133.191 | 28.277 | 28.233 | 27.132 | 600.798 | 25.45 | 26.217 | 1327.827 | 26.953 | 27.184 | 38.43 | 26.001 | 3 | 2.1 | 0 | 0.5 | 0.2
619 | 30/07/2025 09:35:11.895 | 97.92 | 68 | 100 | 71 | 53 | 29.83 | 9.736 | 6.934 | 133.413 | 28.282 | 28.19 | 27.163 | 601.099 | 25.469 | 26.213 | 1312.928 | 26.912 | 27.153 | 38.227 | 26.001 | 3 | 2.1 | 0 | 0.5 | 0.2
620 | 30/07/2025 09:35:13.531 | 98.688 | 68 | 100 | 71 | 53 | 27.619 | 9.575 | 6.935 | 133.087 | 28.274 | 28.23 | 27.16 | 601.131 | 25.453 | 26.214 | 1312.654 | 26.905 | 27.165 | 38.537 | 27.001 | 3 | 1.3 | 0 | 0.5 | 0.2
621 | 30/07/2025 09:35:15.164 | 98.616 | 68 | 100 | 70 | 52 | 26.032 | 9.389 | 6.94 | 133.289 | 28.281 | 28.227 | 27.146 | 600.894 | 25.45 | 26.225 | 1317.874 | 26.914 | 27.158 | 38.588 | 30.001 | 1.9 | 1.3 | 0 | 0 | 0.2
622 | 30/07/2025 09:35:16.799 | 98.784 | 70 | 100 | 71 | 53 | 28.755 | 9.573 | 6.935 | 133.242 | 28.26 | 28.223 | 27.141 | 600.964 | 25.43 | 26.205 | 1312.106 | 26.941 | 27.177 | 38.348 | 29.001 | 1.9 | 0.9 | 0 | 0 | 0.2
623 | 30/07/2025 09:35:18.435 | 99.048 | 69 | 100 | 70 | 52 | 25.747 | 9.73 | 6.937 | 133.331 | 28.263 | 28.218 | 27.115 | 600.87 | 25.452 | 26.22 | 1297.735 | 26.935 | 27.157 | 38.442 | 28.001 | 1 | 1.2 | 0.7 | 1 | 0.2
624 | 30/07/2025 09:35:20.073 | 99.024 | 69 | 100 | 70 | 52 | 28.708 | 9.431 | 6.986 | 133.277 | 28.263 | 28.21 | 27.17 | 601.156 | 25.457 | 26.189 | 1299.801 | 26.92 | 27.147 | 38.372 | 28.001 | 1 | 1.2 | 0.7 | 1 | 0.2
625 | 30/07/2025 09:35:21.710 | 98.664 | 68 | 100 | 71 | 52 | 29.919 | 9.525 | 6.989 | 133.028 | 28.262 | 28.239 | 27.15 | 600.99 | 25.444 | 26.192 | 1307.257 | 26.922 | 27.175 | 38.43 | 27.001 | 1 | 0.6 | 0.7 | 1 | 0.2
626 | 30/07/2025 09:35:23.345 | 99.552 | 68 | 100 | 71 | 52 | 27.02 | 9.575 | 6.988 | 133.44 | 28.273 | 28.223 | 27.147 | 601.074 | 25.456 | 26.194 | 1302.889 | 26.916 | 27.164 | 38.598 | 27.001 | 2.2 | 1.3 | 0.6 | 1.7 | 0.2
627 | 30/07/2025 09:35:24.981 | 99.552 | 68 | 100 | 71 | 52 | 26.664 | 9.574 | 6.935 | 133.322 | 28.268 | 28.225 | 27.128 | 600.984 | 25.456 | 26.187 | 1307.666 | 26.926 | 27.164 | 38.431 | 25.001 | 2.2 | 1 | 0.6 | 1.7 | 0.2
628 | 30/07/2025 09:35:26.618 | 99.408 | 69 | 100 | 70 | 52 | 28.327 | 9.577 | 6.935 | 133.442 | 28.278 | 28.21 | 27.151 | 600.952 | 25.477 | 26.199 | 1309.935 | 26.92 | 27.153 | 38.435 | 30.001 | 2.2 | 1 | 0 | 1.2 | 0.2
629 | 30/07/2025 09:35:28.255 | 99.312 | 69 | 100 | 70 | 53 | 25.906 | 9.572 | 6.935 | 133.1 | 28.266 | 28.205 | 27.17 | 601.125 | 25.458 | 26.211 | 1289.906 | 26.919 | 27.14 | 38.317 | 31.001 | 2.2 | 0.2 | 0 | 1.2 | 0.2
630 | 30/07/2025 09:35:29.890 | 99.768 | 69 | 100 | 70 | 52 | 29.182 | 9.577 | 6.97 | 133.291 | 28.262 | 28.231 | 27.144 | 600.991 | 25.466 | 26.23 | 1290.486 | 26.894 | 27.17 | 38.632 | 31.001 | 2.2 | 0.2 | 0 | 1.2 | 0.2
631 | 30/07/2025 09:35:31.542 | 99.648 | 69 | 100 | 70 | 52 | 29.805 | 9.575 | 6.987 | 133.37 | 28.26 | 28.225 | 27.143 | 600.974 | 25.464 | 26.219 | 1297.99 | 26.929 | 27.164 | 38.592 | 27.001 | 3.6 | 0.6 | 0.6 | 0.1 | 0.2
632 | 30/07/2025 09:35:33.178 | 99.048 | 70 | 100 | 71 | 52 | 26.635 | 9.801 | 6.988 | 133.132 | 28.245 | 28.231 | 27.128 | 600.826 | 25.458 | 26.228 | 1308.227 | 26.949 | 27.174 | 38.55 | 26.001 | 3.6 | 0.6 | 0.6 | 0.1 | 0.2
633 | 30/07/2025 09:35:34.811 | 98.952 | 69 | 100 | 71 | 52 | 29.846 | 9.594 | 6.986 | 133.264 | 28.24 | 28.201 | 27.178 | 601.037 | 25.459 | 26.214 | 1312.056 | 26.915 | 27.141 | 38.172 | 26.001 | 2.3 | 1.4 | 0.3 | 0 | 0.1
634 | 30/07/2025 09:35:36.445 | 98.496 | 68 | 100 | 70 | 52 | 27.766 | 9.577 | 6.988 | 132.985 | 28.235 | 28.231 | 27.137 | 601.031 | 25.46 | 26.229 | 1312.393 | 26.939 | 27.149 | 38.454 | 27.001 | 2.3 | 0.9 | 0.3 | 0 | 0.1
635 | 30/07/2025 09:35:38.080 | 98.16 | 67 | 100 | 72 | 51 | 26.218 | 9.714 | 6.941 | 134.841 | 28.26 | 28.228 | 27.149 | 601.124 | 25.483 | 26.22 | 1318.733 | 26.882 | 27.167 | 38.566 | 27.001 | 2.3 | 0.9 | 0.3 | 0 | 0.1
636 | 30/07/2025 09:35:39.715 | 98.376 | 69 | 100 | 70 | 52 | 29.442 | 9.498 | 6.936 | 134.791 | 28.24 | 28.224 | 27.135 | 600.801 | 25.46 | 26.214 | 1322.847 | 26.938 | 27.178 | 38.373 | 30.001 | 2.2 | 0.6 | 0.9 | 0.5 | 0.2
637 | 30/07/2025 09:35:41.351 | 98.184 | 68 | 100 | 71 | 52 | 29.678 | 9.575 | 6.938 | 134.638 | 28.25 | 28.2 | 27.151 | 601.007 | 25.453 | 26.232 | 1327.965 | 26.925 | 27.153 | 38.311 | 31.001 | 2.2 | 2.2 | 0.9 | 0.5 | 0.2
638 | 30/07/2025 09:35:42.986 | 97.872 | 67 | 100 | 71 | 53 | 26.111 | 9.501 | 6.965 | 134.668 | 28.267 | 28.217 | 27.161 | 601.167 | 25.457 | 26.206 | 1332.452 | 26.908 | 27.147 | 38.362 | 26.001 | 5 | 2.2 | 0.6 | 0.1 | 0.3
639 | 30/07/2025 09:35:44.620 | 98.256 | 68 | 100 | 70 | 52 | 29.854 | 9.552 | 6.989 | 134.514 | 28.278 | 28.232 | 27.147 | 601.003 | 25.461 | 26.228 | 1327.94 | 26.906 | 27.154 | 38.435 | 32.001 | 5 | 1.8 | 0.6 | 0.1 | 0.3
640 | 30/07/2025 09:35:46.259 | 97.68 | 67 | 100 | 71 | 53 | 27.054 | 9.573 | 7.002 | 134.83 | 28.264 | 28.219 | 27.165 | 601.021 | 25.455 | 26.202 | 1313.941 | 26.907 | 27.158 | 38.416 | 27.001 | 2.5 | 0.9 | 0.3 | 0.6 | 0.3
641 | 30/07/2025 09:35:47.897 | 97.584 | 69 | 100 | 69 | 53 | 26.534 | 9.505 | 7.006 | 134.576 | 28.279 | 28.22 | 27.094 | 600.762 | 25.442 | 26.216 | 1300.385 | 26.956 | 27.191 | 38.459 | 27.001 | 2.5 | 0.9 | 0.3 | 0.6 | 0.3
642 | 30/07/2025 09:35:49.533 | 97.488 | 67 | 100 | 70 | 52 | 29.562 | 9.504 | 7.005 | 134.842 | 28.287 | 28.207 | 27.166 | 601.148 | 25.468 | 26.21 | 1298.153 | 26.915 | 27.148 | 38.405 | 25.001 | 2.5 | 0.3 | 0.3 | 0.6 | 0.3
643 | 30/07/2025 09:35:51.170 | 97.68 | 68 | 100 | 70 | 52 | 29.309 | 9.578 | 7.005 | 134.665 | 28.262 | 28.242 | 27.157 | 602.501 | 25.442 | 26.198 | 1299.816 | 26.918 | 27.157 | 38.413 | 26.001 | 2.6 | 0.6 | 0 | 0.6 | 0.3
644 | 30/07/2025 09:35:52.807 | 97.944 | 69 | 100 | 71 | 53 | 29.123 | 9.576 | 7.006 | 134.565 | 28.291 | 28.229 | 27.165 | 602.471 | 25.453 | 26.199 | 1300.956 | 26.898 | 27.169 | 38.648 | 30.001 | 2.6 | 0.9 | 0 | 0.6 | 0.3
645 | 30/07/2025 09:35:54.443 | 97.464 | 69 | 100 | 70 | 53 | 29.848 | 9.5 | 7.019 | 134.873 | 28.26 | 28.23 | 27.144 | 601.016 | 25.438 | 26.192 | 1305.718 | 26.937 | 27.174 | 38.517 | 32.001 | 3.2 | 1 | 0 | 1.1 | 0.3
646 | 30/07/2025 09:35:56.077 | 97.032 | 66 | 100 | 70 | 52 | 26.535 | 9.645 | 7.036 | 133.278 | 28.27 | 28.21 | 27.139 | 602.223 | 25.44 | 26.206 | 1302.876 | 26.932 | 27.161 | 38.426 | 32.001 | 3.2 | 1 | 0 | 1.1 | 0.3
647 | 30/07/2025 09:35:57.712 | 97.44 | 68 | 100 | 70 | 52 | 27.092 | 9.504 | 7.004 | 133.198 | 28.262 | 28.206 | 27.171 | 601.163 | 25.444 | 26.172 | 1308.506 | 26.923 | 27.141 | 38.207 | 30.001 | 3.2 | 1.7 | 0 | 1.1 | 0.3
648 | 30/07/2025 09:35:59.345 | 97.728 | 68 | 100 | 70 | 52 | 29.723 | 9.733 | 7.006 | 133.057 | 28.259 | 28.236 | 27.139 | 600.979 | 25.45 | 26.202 | 1310.096 | 26.927 | 27.172 | 38.627 | 24.001 | 1.8 | 1.4 | 0 | 0.9 | 0.3
649 | 30/07/2025 09:36:00.981 | 97.44 | 69 | 100 | 71 | 54 | 28.757 | 9.525 | 7.006 | 133.38 | 28.265 | 28.225 | 27.138 | 602.519 | 25.487 | 26.212 | 1315.822 | 26.893 | 27.161 | 38.532 | 26.001 | 1.8 | 0.8 | 0 | 0.9 | 0.3
650 | 30/07/2025 09:36:02.616 | 97.248 | 68 | 100 | 70 | 53 | 29.471 | 9.461 | 6.971 | 133.344 | 28.252 | 28.225 | 27.129 | 602.288 | 25.464 | 26.21 | 1314.314 | 26.962 | 27.161 | 38.486 | 26.001 | 3.2 | 2.3 | 0 | 0.5 | 0.2
651 | 30/07/2025 09:36:04.256 | 96.888 | 67 | 100 | 69 | 51 | 29.627 | 9.572 | 6.935 | 133.303 | 28.277 | 28.217 | 27.148 | 602.357 | 25.472 | 26.221 | 1309.204 | 26.924 | 27.151 | 38.429 | 32.001 | 3.2 | 0.9 | 0 | 0.5 | 0.2
652 | 30/07/2025 09:36:05.890 | 97.128 | 68 | 100 | 70 | 52 | 26.079 | 9.587 | 6.986 | 133.156 | 28.258 | 28.218 | 27.159 | 602.573 | 25.456 | 26.228 | 1312.4 | 26.936 | 27.151 | 38.337 | 32.001 | 3.2 | 0.9 | 0 | 0.5 | 0.2
653 | 30/07/2025 09:36:07.526 | 97.368 | 67 | 100 | 71 | 52 | 27.704 | 9.544 | 6.987 | 133.265 | 28.247 | 28.228 | 27.155 | 602.33 | 25.455 | 26.226 | 1317.757 | 26.891 | 27.164 | 38.717 | 31.001 | 2.3 | 1 | 0.6 | 0.7 | 0.2
654 | 30/07/2025 09:36:09.162 | 97.944 | 68 | 100 | 70 | 52 | 29.804 | 9.575 | 6.988 | 133.286 | 28.248 | 28.228 | 27.146 | 602.591 | 25.467 | 26.199 | 1318.45 | 26.915 | 27.163 | 38.324 | 29.001 | 2.3 | 0.6 | 0.6 | 0.7 | 0.2
655 | 30/07/2025 09:36:10.799 | 98.352 | 68 | 100 | 70 | 52 | 26.664 | 9.729 | 6.989 | 133.413 | 28.249 | 28.221 | 27.121 | 602.32 | 25.466 | 26.229 | 1314.62 | 26.932 | 27.149 | 38.487 | 28.001 | 3.6 | 0.7 | 0.3 | 0.1 | 0.1
656 | 30/07/2025 09:36:12.438 | 98.64 | 69 | 100 | 70 | 51 | 29.68 | 9.734 | 6.988 | 133.243 | 28.241 | 28.211 | 27.16 | 602.549 | 25.46 | 26.216 | 1316.89 | 26.919 | 27.156 | 38.249 | 28.001 | 3.6 | 0.8 | 0.3 | 0.1 | 0.1
657 | 30/07/2025 09:36:14.075 | 99.168 | 69 | 100 | 71 | 52 | 29.393 | 9.579 | 6.988 | 133.036 | 28.247 | 28.221 | 27.154 | 602.339 | 25.454 | 26.227 | 1317.619 | 26.934 | 27.146 | 38.563 | 28.001 | 3.6 | 0.8 | 0.3 | 0.1 | 0.1
658 | 30/07/2025 09:36:15.708 | 99.264 | 70 | 100 | 71 | 52 | 25.838 | 9.569 | 6.988 | 133.334 | 28.279 | 28.226 | 27.151 | 602.471 | 25.473 | 26.212 | 1322.907 | 26.882 | 27.168 | 38.585 | 30.001 | 2.9 | 1.1 | 0.6 | 0.5 | 0.2
659 | 30/07/2025 09:36:17.350 | 99.216 | 69 | 100 | 71 | 54 | 28.369 | 9.526 | 6.987 | 133.116 | 28.267 | 28.237 | 27.131 | 602.31 | 25.445 | 26.212 | 1325.424 | 26.935 | 27.178 | 38.684 | 28.001 | 2.9 | 0.9 | 0.6 | 0.5 | 0.2
660 | 30/07/2025 09:36:18.985 | 99.312 | 70 | 100 | 72 | 51 | 26.632 | 9.426 | 6.965 | 133.34 | 28.288 | 28.221 | 27.14 | 602.355 | 25.463 | 26.198 | 1328.253 | 26.929 | 27.156 | 38.555 | 30.001 | 3.6 | 0.6 | 0 | 0.8 | 0.2
661 | 30/07/2025 09:36:20.619 | 99.744 | 69 | 100 | 71 | 54 | 27.17 | 9.734 | 6.934 | 133.221 | 28.307 | 28.215 | 27.148 | 602.452 | 25.446 | 26.203 | 1330.459 | 26.943 | 27.146 | 38.076 | 28.001 | 3.6 | 0.9 | 0 | 0.8 | 0.2
662 | 30/07/2025 09:36:22.256 | 99 | 69 | 100 | 70 | 53 | 29.782 | 9.583 | 6.936 | 133.178 | 28.427 | 28.229 | 27.157 | 602.315 | 25.447 | 26.217 | 1328.009 | 26.923 | 27.157 | 38.607 | 25.001 | 2.7 | 2.2 | 0.7 | 0.5 | 0.2
663 | 30/07/2025 09:36:23.891 | 99.312 | 70 | 100 | 71 | 52 | 28.979 | 9.792 | 6.925 | 133.327 | 28.3 | 28.232 | 27.149 | 602.57 | 25.446 | 26.2 | 1331.955 | 26.904 | 27.164 | 38.532 | 25.001 | 2.7 | 2.2 | 0.7 | 0.5 | 0.2
664 | 30/07/2025 09:36:25.525 | 99.168 | 70 | 100 | 71 | 52 | 25.821 | 9.579 | 6.868 | 133.184 | 28.405 | 28.228 | 27.114 | 602.268 | 25.439 | 26.216 | 1332.914 | 26.95 | 27.158 | 38.579 | 29.001 | 2.7 | 1 | 0.7 | 0.5 | 0.2
665 | 30/07/2025 09:36:27.162 | 98.688 | 69 | 100 | 70 | 52 | 28.758 | 9.576 | 6.897 | 133.391 | 28.428 | 28.209 | 27.154 | 602.463 | 25.449 | 26.198 | 1327.83 | 26.916 | 27.16 | 38.33 | 23.001 | 2.7 | 0.2 | 0 | 0.8 | 0.2
666 | 30/07/2025 09:36:28.798 | 98.76 | 67 | 100 | 69 | 52 | 26.244 | 9.8 | 6.902 | 133.15 | 28.406 | 28.208 | 27.164 | 602.393 | 25.426 | 26.219 | 1327.244 | 26.928 | 27.142 | 38.304 | 24.001 | 2.7 | 0 | 0 | 0.8 | 0.2
667 | 30/07/2025 09:36:30.433 | 98.472 | 68 | 100 | 71 | 52 | 27.689 | 9.601 | 6.9 | 133.168 | 28.403 | 28.233 | 27.157 | 602.311 | 25.452 | 26.184 | 1325.307 | 26.89 | 27.166 | 38.514 | 27.001 | 2.4 | 2.8 | 0.3 | 1 | 0.3
668 | 30/07/2025 09:36:32.070 | 99.096 | 70 | 100 | 70 | 52 | 29.892 | 9.647 | 6.903 | 133.24 | 28.406 | 28.228 | 27.137 | 601.066 | 25.447 | 26.198 | 1312.917 | 26.934 | 27.181 | 38.406 | 27.001 | 2.4 | 2.8 | 0.3 | 1 | 0.3
669 | 30/07/2025 09:36:33.707 | 99.48 | 70 | 100 | 69 | 52 | 28.261 | 9.73 | 6.936 | 133.303 | 28.413 | 28.215 | 27.116 | 600.848 | 25.458 | 26.208 | 1307.758 | 26.927 | 27.156 | 38.51 | 21.001 | 2.4 | 2.3 | 0.3 | 1 | 0.3
670 | 30/07/2025 09:36:35.341 | 98.976 | 69 | 100 | 71 | 52 | 25.906 | 9.577 | 6.933 | 133.272 | 28.406 | 28.214 | 27.147 | 601.103 | 25.454 | 26.208 | 1303.277 | 26.922 | 27.143 | 38.264 | 24.001 | 2.5 | 0.7 | 0.6 | 1.1 | 0.2
671 | 30/07/2025 09:36:36.983 | 99.528 | 70 | 100 | 70 | 52 | 29.17 | 9.579 | 6.937 | 133.112 | 28.406 | 28.227 | 27.154 | 600.966 | 25.458 | 26.238 | 1304.923 | 26.932 | 27.169 | 38.583 | 24.001 | 2.5 | 3.1 | 0.6 | 1.1 | 0.2
672 | 30/07/2025 09:36:38.620 | 99.24 | 70 | 100 | 70 | 52 | 25.857 | 9.577 | 6.937 | 133.182 | 28.397 | 28.237 | 27.163 | 600.905 | 25.458 | 26.217 | 1311.185 | 26.899 | 27.178 | 38.53 | 25.001 | 1.8 | 1.5 | 1 | 0 | 0.2
673 | 30/07/2025 09:36:40.259 | 99.624 | 69 | 100 | 70 | 52 | 28.158 | 9.731 | 6.937 | 133.319 | 28.388 | 28.226 | 27.133 | 600.893 | 25.451 | 26.238 | 1313.236 | 26.944 | 27.168 | 38.478 | 28.001 | 1.8 | 1.3 | 1 | 0 | 0.2
674 | 30/07/2025 09:36:41.895 | 99.504 | 69 | 100 | 70 | 52 | 29.905 | 9.577 | 6.935 | 133.43 | 28.407 | 28.218 | 27.134 | 601.934 | 25.479 | 26.225 | 1302.692 | 26.919 | 27.164 | 38.53 | 28.001 | 1.8 | 1.3 | 1 | 0 | 0.2
675 | 30/07/2025 09:36:43.532 | 99.24 | 70 | 100 | 71 | 53 | 27.787 | 9.432 | 6.934 | 133.05 | 28.384 | 28.224 | 27.155 | 602.33 | 25.45 | 26.227 | 1315.466 | 26.968 | 27.149 | 38.207 | 28.001 | 3.2 | 0.7 | 0.7 | 0 | 0.2
676 | 30/07/2025 09:36:45.166 | 99.072 | 69 | 100 | 70 | 52 | 26.203 | 9.458 | 6.936 | 133.2 | 28.381 | 28.235 | 27.139 | 602.358 | 25.466 | 26.228 | 1317.875 | 27.046 | 27.165 | 38.703 | 30.001 | 3.2 | 0.9 | 0.7 | 0 | 0.2
677 | 30/07/2025 09:36:46.800 | 99.12 | 70 | 100 | 70 | 51 | 28.944 | 9.284 | 6.937 | 133.125 | 28.386 | 28.239 | 27.15 | 602.463 | 25.445 | 26.224 | 1324.751 | 27.065 | 27.176 | 38.589 | 31.001 | 4.1 | 2.9 | 0.1 | 1.1 | 0.2
678 | 30/07/2025 09:36:48.437 | 99.144 | 69 | 100 | 71 | 52 | 25.745 | 9.445 | 6.935 | 133.489 | 28.401 | 28.228 | 27.127 | 602.34 | 25.466 | 26.217 | 1329.952 | 26.939 | 27.154 | 38.511 | 32.001 | 4.1 | 0.9 | 0.1 | 1.1 | 0.2
679 | 30/07/2025 09:36:50.072 | 99.792 | 70 | 100 | 70 | 52 | 28.788 | 9.549 | 6.935 | 133.274 | 28.4 | 28.21 | 27.154 | 602.465 | 25.444 | 26.214 | 1317.727 | 26.924 | 27.153 | 38.169 | 32.001 | 4.1 | 0.9 | 0.1 | 1.1 | 0.2
680 | 30/07/2025 09:36:51.707 | 99.96 | 70 | 100 | 71 | 52 | 29.893 | 9.576 | 6.937 | 133.139 | 28.408 | 28.219 | 27.18 | 602.303 | 25.443 | 26.224 | 1325.168 | 26.93 | 27.137 | 38.206 | 34.001 | 2.4 | 1.2 | 0 | 0 | 0.2
681 | 30/07/2025 09:36:53.345 | 99.792 | 69 | 100 | 70 | 52 | 27.179 | 9.424 | 6.937 | 133.371 | 28.429 | 28.235 | 27.298 | 602.54 | 25.459 | 26.195 | 1327.628 | 26.895 | 27.166 | 38.501 | 30.001 | 2.4 | 0.9 | 0 | 0 | 0.2
682 | 30/07/2025 09:36:54.980 | 99.528 | 70 | 100 | 70 | 51 | 26.706 | 9.577 | 6.935 | 133.136 | 28.415 | 28.24 | 27.274 | 602.315 | 25.445 | 26.209 | 1321.837 | 26.932 | 27.178 | 38.659 | 33.001 | 3.1 | 1.5 | 0.7 | 0 | 0.2
683 | 30/07/2025 09:36:56.618 | 99.264 | 69 | 100 | 71 | 53 | 28.425 | 9.572 | 6.935 | 133.308 | 28.416 | 28.226 | 27.286 | 602.39 | 25.458 | 26.207 | 1324.324 | 26.935 | 27.168 | 38.378 | 32.001 | 3.1 | 0.8 | 0.7 | 0 | 0.2
684 | 30/07/2025 09:36:58.253 | 99.168 | 68 | 100 | 70 | 52 | 25.908 | 9.46 | 6.935 | 133.183 | 28.402 | 28.214 | 27.297 | 602.456 | 25.441 | 26.209 | 1323.956 | 26.936 | 27.155 | 38.222 | 32.001 | 2.6 | 0.7 | 0.6 | 0 | 0.2
685 | 30/07/2025 09:36:59.894 | 99.072 | 70 | 100 | 70 | 52 | 29.286 | 9.578 | 6.978 | 134.599 | 28.414 | 28.223 | 27.299 | 602.416 | 25.46 | 26.207 | 1307.964 | 26.91 | 27.142 | 38.545 | 32.001 | 2.6 | 0.7 | 0.6 | 0 | 0.2
686 | 30/07/2025 09:37:01.532 | 98.664 | 68 | 100 | 72 | 51 | 29.875 | 9.378 | 6.988 | 134.81 | 28.426 | 28.231 | 27.291 | 602.425 | 25.443 | 26.198 | 1320.256 | 26.898 | 27.168 | 38.559 | 28.001 | 2.6 | 1.4 | 0.6 | 0 | 0.2
687 | 30/07/2025 09:37:03.169 | 98.616 | 69 | 100 | 71 | 52 | 26.717 | 9.628 | 6.988 | 134.748 | 28.411 | 28.221 | 27.263 | 602.227 | 25.438 | 26.193 | 1310.398 | 26.95 | 27.165 | 38.489 | 24.001 | 1.9 | 0.7 | 0 | 0 | 0.2
688 | 30/07/2025 09:37:04.809 | 98.352 | 69 | 100 | 71 | 52 | 29.906 | 9.579 | 6.988 | 134.697 | 28.397 | 28.218 | 27.288 | 602.443 | 25.439 | 26.188 | 1311.881 | 26.935 | 27.165 | 38.177 | 28.001 | 1.9 | 0.6 | 0 | 0 | 0.2
689 | 30/07/2025 09:37:06.446 | 98.304 | 69 | 100 | 71 | 52 | 27.737 | 9.655 | 6.987 | 134.605 | 28.4 | 28.209 | 27.302 | 602.362 | 25.442 | 26.201 | 1313.02 | 26.921 | 27.133 | 38.295 | 28.001 | 2.6 | 0.6 | 0 | 1.3 | 0.1
690 | 30/07/2025 09:37:08.081 | 98.232 | 69 | 100 | 69 | 52 | 26.197 | 9.57 | 6.939 | 134.518 | 28.404 | 28.234 | 27.312 | 603.292 | 25.461 | 26.198 | 1300.728 | 26.895 | 27.164 | 38.458 | 28.001 | 2.6 | 0.6 | 0 | 1.3 | 0.1
691 | 30/07/2025 09:37:09.718 | 98.4 | 68 | 100 | 69 | 52 | 29.481 | 9.604 | 6.937 | 134.877 | 28.398 | 28.243 | 27.28 | 602.443 | 25.452 | 26.219 | 1309.697 | 26.916 | 27.19 | 38.608 | 28.001 | 2.6 | 1.5 | 0 | 1.3 | 0.1
692 | 30/07/2025 09:37:11.354 | 97.896 | 69 | 100 | 71 | 51 | 29.681 | 9.287 | 6.935 | 134.781 | 28.408 | 28.215 | 27.266 | 602.195 | 25.484 | 26.229 | 1316.516 | 26.936 | 27.163 | 38.471 | 26.001 | 3.6 | 1.1 | 0.3 | 0.5 | 0.1
693 | 30/07/2025 09:37:12.993 | 98.16 | 68 | 100 | 70 | 53 | 28.683 | 9.483 | 6.937 | 134.693 | 28.39 | 28.209 | 27.265 | 602.278 | 25.453 | 26.237 | 1317.926 | 26.942 | 27.162 | 38.467 | 29.001 | 3.6 | 0.6 | 0.3 | 0.5 | 0.1
694 | 30/07/2025 09:37:14.630 | 98.64 | 69 | 100 | 70 | 52 | 29.915 | 9.729 | 6.934 | 134.59 | 28.405 | 28.225 | 27.282 | 602.462 | 25.482 | 26.214 | 1320.425 | 26.906 | 27.127 | 38.441 | 27.001 | 3.3 | 0.8 | 0.6 | 0 | 0.2
695 | 30/07/2025 09:37:16.265 | 98.736 | 69 | 100 | 71 | 52 | 27.169 | 9.577 | 6.936 | 134.598 | 28.385 | 28.233 | 27.302 | 602.483 | 25.456 | 26.232 | 1307.624 | 26.902 | 27.181 | 38.742 | 23.001 | 3.3 | 0.6 | 0.6 | 0 | 0.2
696 | 30/07/2025 09:37:17.903 | 98.856 | 69 | 100 | 69 | 52 | 26.6 | 9.5 | 6.937 | 134.856 | 28.396 | 28.229 | 27.272 | 602.339 | 25.467 | 26.239 | 1312.1 | 26.929 | 27.16 | 38.53 | 23.001 | 3.3 | 0.6 | 0.6 | 0 | 0.2
697 | 30/07/2025 09:37:19.539 | 98.664 | 70 | 100 | 70 | 52 | 29.696 | 9.286 | 6.935 | 134.838 | 28.396 | 28.22 | 27.29 | 602.51 | 25.455 | 26.206 | 1310.373 | 26.926 | 27.157 | 38.418 | 26.001 | 2.9 | 1.7 | 0.6 | 0.5 | 0.2
698 | 30/07/2025 09:37:21.173 | 98.568 | 68 | 100 | 71 | 52 | 29.357 | 9.433 | 6.935 | 134.618 | 28.384 | 28.22 | 27.305 | 602.496 | 25.459 | 26.223 | 1320.652 | 26.936 | 27.146 | 38.226 | 31.001 | 2.9 | 1 | 0.6 | 0.5 | 0.2
699 | 30/07/2025 09:37:22.811 | 98.472 | 70 | 100 | 71 | 53 | 29.231 | 9.431 | 6.935 | 134.624 | 28.386 | 28.226 | 27.311 | 602.473 | 25.457 | 26.208 | 1322.036 | 26.911 | 27.152 | 38.279 | 27.001 | 3.1 | 1.9 | 0 | 0.6 | 0.2
700 | 30/07/2025 09:37:24.446 | 98.472 | 70 | 100 | 71 | 52 | 29.809 | 9.718 | 6.939 | 134.7 | 28.404 | 28.229 | 27.286 | 602.314 | 25.449 | 26.218 | 1318.645 | 26.919 | 27.172 | 38.611 | 30.001 | 3.1 | 1.3 | 0 | 0.6 | 0.2
701 | 30/07/2025 09:37:26.082 | 98.304 | 69 | 100 | 70 | 52 | 26.627 | 9.574 | 6.936 | 135.136 | 28.432 | 28.224 | 27.272 | 602.452 | 25.469 | 26.219 | 1320.565 | 26.932 | 27.156 | 38.599 | 30.001 | 3.1 | 1.3 | 0 | 0.6 | 0.2
702 | 30/07/2025 09:37:27.719 | 97.92 | 70 | 100 | 70 | 54 | 27.133 | 9.501 | 6.935 | 134.771 | 28.413 | 28.212 | 27.291 | 602.507 | 25.445 | 26.214 | 1315.454 | 26.932 | 27.166 | 38.335 | 25.001 | 2.3 | 1.4 | 0 | 0.8 | 0.2
703 | 30/07/2025 09:37:29.354 | 97.896 | 68 | 100 | 69 | 52 | 29.783 | 9.43 | 6.935 | 134.477 | 28.407 | 28.217 | 27.288 | 602.477 | 25.441 | 26.218 | 1307.759 | 27.078 | 27.135 | 38.357 | 33.001 | 2.3 | 1.2 | 0 | 0.8 | 0.2
704 | 30/07/2025 09:37:30.991 | 97.56 | 68 | 100 | 70 | 52 | 26.207 | 9.445 | 6.936 | 134.421 | 28.422 | 28.254 | 27.289 | 602.475 | 25.449 | 26.199 | 1304.92 | 26.92 | 27.164 | 38.555 | 26.001 | 2.5 | 1.8 | 0 | 0.5 | 0.2
705 | 30/07/2025 09:37:32.627 | 97.92 | 69 | 100 | 70 | 52 | 29.548 | 9.561 | 6.938 | 134.798 | 28.413 | 28.225 | 27.292 | 602.384 | 25.443 | 26.208 | 1307.28 | 27.054 | 27.16 | 38.685 | 26.001 | 2.5 | 0.1 | 0 | 0.5 | 0.2
706 | 30/07/2025 09:37:34.279 | 98.352 | 69 | 100 | 71 | 53 | 29.765 | 9.496 | 6.935 | 134.895 | 28.416 | 28.224 | 27.278 | 602.392 | 25.434 | 26.196 | 1307.326 | 26.924 | 27.163 | 38.413 | 25.001 | 1.5 | 0.9 | 0.9 | 1.1 | 0.3
707 | 30/07/2025 09:37:35.919 | 98.28 | 69 | 100 | 70 | 52 | 26.28 | 9.424 | 6.936 | 134.637 | 28.401 | 28.201 | 27.284 | 602.46 | 25.43 | 26.193 | 1307.755 | 26.946 | 27.161 | 38.29 | 25.001 | 1.5 | 0.9 | 0.9 | 1.1 | 0.3
708 | 30/07/2025 09:37:37.553 | 98.232 | 69 | 100 | 71 | 53 | 27.802 | 9.731 | 6.935 | 134.611 | 28.433 | 28.223 | 27.295 | 601.055 | 25.446 | 26.187 | 1317.799 | 26.914 | 27.153 | 38.456 | 25.001 | 1.5 | 1 | 0.9 | 1.1 | 0.3
709 | 30/07/2025 09:37:39.191 | 98.376 | 69 | 100 | 71 | 50 | 29.873 | 9.445 | 6.936 | 134.81 | 28.395 | 28.231 | 27.293 | 600.982 | 25.419 | 26.19 | 1324.81 | 26.902 | 27.173 | 38.447 | 29.001 | 2.1 | 1.2 | 0 | 0.5 | 0.3
710 | 30/07/2025 09:37:40.827 | 98.376 | 70 | 100 | 70 | 53 | 26.65 | 9.569 | 6.933 | 134.841 | 28.427 | 28.226 | 27.292 | 601.002 | 25.48 | 26.196 | 1327.762 | 26.911 | 27.165 | 38.56 | 23.001 | 2.1 | 1.7 | 0 | 0.5 | 0.3
711 | 30/07/2025 09:37:42.464 | 98.376 | 69 | 100 | 70 | 52 | 29.737 | 9.578 | 6.936 | 134.594 | 28.399 | 28.222 | 27.264 | 601.009 | 25.445 | 26.197 | 1325.826 | 27.07 | 27.178 | 38.589 | 28.001 | 2.4 | 1.6 | 0 | 0.8 | 0.3
712 | 30/07/2025 09:37:44.099 | 98.304 | 69 | 100 | 71 | 52 | 29.401 | 9.576 | 6.935 | 134.726 | 28.409 | 28.204 | 27.292 | 602.26 | 25.458 | 26.212 | 1327.352 | 26.921 | 27.138 | 38.349 | 28.001 | 2.4 | 1.6 | 0 | 0.8 | 0.3
713 | 30/07/2025 09:37:45.736 | 97.704 | 69 | 100 | 72 | 52 | 25.889 | 9.798 | 6.944 | 134.489 | 28.408 | 28.238 | 27.307 | 602.572 | 25.464 | 26.205 | 1327.467 | 26.901 | 27.149 | 38.384 | 26.001 | 2.4 | 1.1 | 0 | 0.8 | 0.3
714 | 30/07/2025 09:37:47.372 | 97.104 | 67 | 100 | 71 | 51 | 28.195 | 9.771 | 6.989 | 134.787 | 28.387 | 28.231 | 27.283 | 602.347 | 25.449 | 26.241 | 1327.882 | 26.926 | 27.164 | 38.699 | 25.001 | 3.1 | 0.6 | 0 | 0.5 | 0.2
715 | 30/07/2025 09:37:49.008 | 96.696 | 68 | 100 | 71 | 53 | 29.918 | 9.428 | 6.986 | 134.931 | 28.398 | 28.226 | 27.278 | 602.305 | 25.47 | 26.223 | 1337.303 | 26.936 | 27.169 | 38.532 | 26.001 | 3.1 | 1.9 | 0 | 0.5 | 0.2
716 | 30/07/2025 09:37:50.642 | 96.792 | 68 | 100 | 70 | 53 | 27.081 | 9.504 | 6.988 | 134.665 | 28.381 | 28.214 | 27.279 | 602.252 | 25.452 | 26.231 | 1342.456 | 26.95 | 27.165 | 38.501 | 28.001 | 1.4 | 2.8 | 0.6 | 0.6 | 0.2
717 | 30/07/2025 09:37:52.278 | 96.816 | 68 | 100 | 73 | 52 | 29.772 | 9.285 | 6.935 | 134.733 | 28.395 | 28.22 | 27.313 | 602.444 | 25.473 | 26.218 | 1322.27 | 26.916 | 27.142 | 38.263 | 27.001 | 1.4 | 0.9 | 0.6 | 0.6 | 0.2
718 | 30/07/2025 09:37:53.919 | 96.912 | 69 | 100 | 70 | 52 | 28.87 | 9.427 | 6.937 | 134.527 | 28.381 | 28.231 | 27.285 | 602.496 | 25.447 | 26.209 | 1319.158 | 26.897 | 27.183 | 38.417 | 27.001 | 1.4 | 0.9 | 0.6 | 0.6 | 0.2
719 | 30/07/2025 09:37:55.556 | 96.936 | 69 | 100 | 70 | 53 | 25.84 | 9.425 | 6.937 | 134.814 | 28.392 | 28.22 | 27.266 | 602.305 | 25.461 | 26.224 | 1320.388 | 26.916 | 27.157 | 38.75 | 25.001 | 3.1 | 0.6 | 1.2 | 0.8 | 0.2
720 | 30/07/2025 09:37:57.190 | 97.08 | 68 | 100 | 71 | 52 | 28.73 | 9.282 | 6.935 | 134.804 | 28.398 | 28.222 | 27.28 | 602.282 | 25.468 | 26.213 | 1312.728 | 26.933 | 27.16 | 38.458 | 26.001 | 3.1 | 0.7 | 1.2 | 0.8 | 0.2
721 | 30/07/2025 09:37:58.826 | 97.056 | 68 | 100 | 72 | 53 | 26.147 | 9.284 | 6.936 | 134.765 | 28.41 | 28.21 | 27.297 | 602.475 | 25.467 | 26.223 | 1303.038 | 26.921 | 27.156 | 38.334 | 23.001 | 2.5 | 1.3 | 0.6 | 0.2 | 0.2
722 | 30/07/2025 09:38:00.464 | 97.32 | 68 | 100 | 71 | 52 | 27.628 | 9.517 | 6.933 | 134.51 | 28.4 | 28.228 | 27.284 | 602.464 | 25.447 | 26.195 | 1295.621 | 26.916 | 27.152 | 38.472 | 24.001 | 2.5 | 3.3 | 0.6 | 0.2 | 0.2
723 | 30/07/2025 09:38:02.099 | 97.272 | 67 | 100 | 70 | 52 | 29.855 | 9.318 | 6.939 | 134.533 | 28.411 | 28.233 | 27.274 | 602.158 | 25.444 | 26.22 | 1288.122 | 26.912 | 27.16 | 38.515 | 24.001 | 2.5 | 3.3 | 0.6 | 0.2 | 0.2
724 | 30/07/2025 09:38:03.735 | 96.96 | 67 | 100 | 70 | 52 | 28.4 | 9.562 | 6.934 | 134.91 | 28.432 | 28.229 | 27.286 | 602.332 | 25.462 | 26.205 | 1286.575 | 26.928 | 27.168 | 38.454 | 23.001 | 1.6 | 1 | 0 | 0.1 | 0.3
725 | 30/07/2025 09:38:05.371 | 97.152 | 69 | 100 | 70 | 52 | 25.993 | 9.443 | 6.934 | 134.63 | 28.405 | 28.211 | 27.277 | 602.481 | 25.435 | 26.207 | 1288.999 | 26.947 | 27.162 | 38.44 | 24.001 | 1.6 | 0.8 | 0 | 0.1 | 0.3
726 | 30/07/2025 09:38:07.008 | 96.984 | 67 | 100 | 71 | 52 | 29.502 | 9.567 | 6.935 | 134.748 | 28.428 | 28.21 | 27.317 | 602.573 | 25.443 | 26.203 | 1291.745 | 26.921 | 27.152 | 38.199 | 34.001 | 2.8 | 1.6 | 0 | 0.3 | 0.2
727 | 30/07/2025 09:38:08.644 | 96.192 | 66 | 100 | 70 | 53 | 25.948 | 9.561 | 6.936 | 134.368 | 28.411 | 28.259 | 27.293 | 602.429 | 25.425 | 26.194 | 1297.339 | 27.024 | 27.171 | 38.569 | 25.001 | 2.8 | 1.2 | 0 | 0.3 | 0.2
728 | 30/07/2025 09:38:10.283 | 95.928 | 67 | 100 | 70 | 52 | 28.364 | 9.581 | 6.936 | 134.829 | 28.409 | 28.23 | 27.288 | 602.309 | 25.455 | 26.205 | 1307.482 | 27.047 | 27.159 | 38.659 | 24.001 | 3 | 0.9 | 0.3 | 0 | 0.3
729 | 30/07/2025 09:38:11.918 | 95.64 | 66 | 100 | 71 | 52 | 29.941 | 9.577 | 6.935 | 134.742 | 28.407 | 28.231 | 27.266 | 602.31 | 25.44 | 26.185 | 1307.699 | 27.073 | 27.154 | 38.395 | 24.001 | 3 | 0.9 | 0.3 | 0 | 0.3
730 | 30/07/2025 09:38:13.555 | 95.616 | 66 | 100 | 70 | 55 | 27.91 | 9.289 | 6.936 | 134.684 | 28.404 | 28.212 | 27.281 | 603.544 | 25.448 | 26.195 | 1305.453 | 27.081 | 27.16 | 38.265 | 28.001 | 3 | 1.7 | 0.3 | 0 | 0.3
731 | 30/07/2025 09:38:15.189 | 96.168 | 68 | 100 | 70 | 52 | 26.25 | 9.285 | 6.932 | 134.503 | 28.43 | 28.228 | 27.294 | 603.564 | 25.607 | 26.2 | 1307.572 | 26.913 | 27.152 | 38.495 | 25.001 | 2.6 | 1.8 | 0.6 | 0.1 | 0.2
732 | 30/07/2025 09:38:16.824 | 96.576 | 67 | 100 | 70 | 53 | 28.981 | 9.428 | 6.938 | 133.408 | 28.397 | 28.226 | 27.284 | 603.496 | 25.447 | 26.213 | 1312.235 | 27.048 | 27.161 | 38.665 | 24.001 | 2.6 | 1.2 | 0.6 | 0.1 | 0.2
733 | 30/07/2025 09:38:18.458 | 97.944 | 69 | 100 | 70 | 53 | 25.882 | 9.277 | 6.935 | 133.329 | 28.408 | 28.23 | 27.295 | 603.681 | 25.475 | 26.215 | 1308.61 | 27.057 | 27.171 | 38.464 | 27.001 | 2.9 | 1.2 | 0.7 | 0 | 0.2
734 | 30/07/2025 09:38:20.095 | 97.992 | 69 | 100 | 70 | 54 | 28.853 | 9.309 | 6.935 | 133.197 | 28.388 | 28.235 | 27.262 | 603.539 | 25.442 | 26.215 | 1308.332 | 27.081 | 27.181 | 38.566 | 27.001 | 2.9 | 1.2 | 0.7 | 0 | 0.2
735 | 30/07/2025 09:38:21.732 | 99.24 | 70 | 100 | 71 | 53 | 29.967 | 9.294 | 6.935 | 133.198 | 28.394 | 28.2 | 27.291 | 603.574 | 25.611 | 26.225 | 1311.959 | 27.065 | 27.145 | 38.187 | 26.001 | 2.9 | 0.7 | 0.7 | 0 | 0.2
736 | 30/07/2025 09:38:23.376 | 99.096 | 71 | 100 | 69 | 52 | 27.311 | 9.379 | 6.935 | 132.951 | 28.388 | 28.241 | 27.295 | 603.723 | 25.591 | 26.211 | 1317.797 | 27.052 | 27.157 | 38.587 | 25.001 | 3.1 | 2.3 | 0.9 | 0.5 | 0.2
737 | 30/07/2025 09:38:25.010 | 99.96 | 70 | 100 | 71 | 53 | 26.689 | 9.507 | 6.938 | 133.348 | 28.366 | 28.231 | 27.281 | 603.566 | 25.604 | 26.236 | 1320.42 | 27.073 | 27.175 | 38.598 | 26.001 | 3.1 | 1.2 | 0.9 | 0.5 | 0.2
738 | 30/07/2025 09:38:26.643 | 99.576 | 71 | 100 | 71 | 53 | 28.47 | 9.429 | 6.934 | 133.212 | 28.373 | 28.229 | 27.263 | 603.574 | 25.59 | 26.215 | 1318.274 | 26.941 | 27.173 | 38.514 | 34.001 | 2.3 | 1.6 | 0.6 | 0.5 | 0.2
739 | 30/07/2025 09:38:28.276 | 100.56 | 71 | 99 | 71 | 53 | 25.929 | 9.455 | 6.99 | 133.139 | 28.381 | 28.21 | 27.279 | 603.412 | 25.598 | 26.227 | 1315.679 | 27.089 | 27.152 | 38.491 | 28.001 | 2.3 | 2 | 0.6 | 0.5 | 0.2
740 | 30/07/2025 09:38:29.917 | 100.824 | 72 | 100 | 73 | 53 | 29.255 | 9.447 | 7.004 | 133.227 | 28.393 | 28.215 | 27.319 | 603.859 | 25.464 | 26.21 | 1317.834 | 27.063 | 27.139 | 38.273 | 28.001 | 2.3 | 2 | 0.6 | 0.5 | 0.2
741 | 30/07/2025 09:38:31.550 | 101.544 | 72 | 100 | 70 | 52 | 29.907 | 9.438 | 7.006 | 132.887 | 28.397 | 28.246 | 27.294 | 603.593 | 25.528 | 26.22 | 1306.684 | 27.049 | 27.188 | 38.639 | 27.001 | 3 | 0.6 | 0.1 | 0.5 | 0.3
742 | 30/07/2025 09:38:33.184 | 101.52 | 71 | 100 | 70 | 53 | 26.647 | 9.299 | 7.006 | 133.602 | 28.41 | 28.225 | 27.277 | 603.47 | 25.6 | 26.236 | 1304.219 | 27.052 | 27.165 | 38.558 | 26.001 | 3 | 0.9 | 0.1 | 0.5 | 0.3
743 | 30/07/2025 09:38:34.817 | 102.096 | 73 | 100 | 70 | 53 | 29.945 | 9.284 | 7.006 | 133.16 | 28.412 | 28.233 | 27.251 | 603.427 | 25.591 | 26.206 | 1307.554 | 27.102 | 27.189 | 38.531 | 24.001 | 3.1 | 0.6 | 0.4 | 0.8 | 0.2
744 | 30/07/2025 09:38:36.454 | 102.384 | 74 | 100 | 70 | 53 | 27.765 | 9.509 | 7.006 | 133.299 | 28.414 | 28.213 | 27.295 | 603.64 | 25.61 | 26.221 | 1295.681 | 27.066 | 27.158 | 38.491 | 26.001 | 3.1 | 0.7 | 0.4 | 0.8 | 0.2
745 | 30/07/2025 09:38:38.089 | 100.944 | 72 | 100 | 70 | 52 | 26.2 | 9.432 | 6.936 | 133.081 | 28.408 | 28.226 | 27.289 | 603.598 | 25.584 | 26.204 | 1287.937 | 27.059 | 27.156 | 38.232 | 26.001 | 3.1 | 0.7 | 0.4 | 0.8 | 0.2
746 | 30/07/2025 09:38:39.721 | 100.848 | 71 | 100 | 70 | 52 | 29.566 | 9.43 | 6.939 | 133.045 | 28.412 | 28.23 | 27.293 | 603.537 | 25.586 | 26.222 | 1282.615 | 27.051 | 27.159 | 38.612 | 26.001 | 4.7 | 0.8 | 0.3 | 0 | 0.1
747 | 30/07/2025 09:38:41.358 | 100.872 | 72 | 100 | 70 | 52 | 29.785 | 9.488 | 6.935 | 133.386 | 28.427 | 28.234 | 27.28 | 603.587 | 25.612 | 26.191 | 1280.188 | 27.073 | 27.163 | 38.729 | 24.001 | 4.7 | 2.1 | 0.3 | 0 | 0.1
748 | 30/07/2025 09:38:42.990 | 100.44 | 71 | 100 | 70 | 52 | 26.305 | 9.43 | 6.902 | 133.125 | 28.419 | 28.23 | 27.278 | 603.638 | 25.578 | 26.194 | 1286.497 | 27.081 | 27.173 | 38.345 | 27.001 | 3 | 2.1 | 0.1 | 0.5 | 0.1
749 | 30/07/2025 09:38:44.623 | 100.08 | 71 | 100 | 71 | 52 | 29.948 | 9.502 | 6.898 | 133.241 | 28.426 | 28.206 | 27.308 | 603.709 | 25.573 | 26.193 | 1283.213 | 27.061 | 27.146 | 38.168 | 23.001 | 3 | 2.3 | 0.1 | 0.5 | 0.1
750 | 30/07/2025 09:38:46.256 | 99.696 | 72 | 100 | 70 | 52 | 27.377 | 9.486 | 6.9 | 132.977 | 28.397 | 28.232 | 27.285 | 603.662 | 25.566 | 26.188 | 1287.232 | 27.073 | 27.163 | 38.469 | 23.001 | 4.6 | 1.3 | 0.6 | 0 | 0.1
751 | 30/07/2025 09:38:47.924 | 100.176 | 72 | 100 | 70 | 52 | 26.709 | 9.681 | 6.903 | 133.435 | 28.411 | 28.229 | 27.287 | 603.566 | 25.605 | 26.196 | 1297.936 | 27.044 | 27.154 | 38.709 | 23.001 | 4.6 | 1.3 | 0.6 | 0 | 0.1
752 | 30/07/2025 09:38:49.559 | 99.768 | 70 | 100 | 71 | 52 | 29.769 | 9.289 | 6.901 | 133.406 | 28.398 | 28.23 | 27.275 | 603.62 | 25.589 | 26.202 | 1299.963 | 27.072 | 27.166 | 38.619 | 22.001 | 4.6 | 0.9 | 0.6 | 0 | 0.1
753 | 30/07/2025 09:38:51.192 | 99.72 | 70 | 100 | 71 | 52 | 29.544 | 9.287 | 6.901 | 134.726 | 28.413 | 28.209 | 27.296 | 603.454 | 25.6 | 26.231 | 1298.186 | 27.081 | 27.152 | 38.4 | 29.001 | 1.2 | 1 | 0.6 | 0.5 | 0.2
754 | 30/07/2025 09:38:52.827 | 99.072 | 70 | 100 | 70 | 54 | 29.292 | 9.284 | 6.899 | 134.637 | 28.388 | 28.202 | 27.291 | 603.803 | 25.602 | 26.208 | 1290.311 | 27.07 | 27.153 | 38.254 | 25.001 | 1.2 | 1.2 | 0.6 | 0.5 | 0.2
755 | 30/07/2025 09:38:54.462 | 99.216 | 70 | 100 | 71 | 53 | 29.961 | 9.372 | 6.869 | 134.471 | 28.401 | 28.235 | 27.274 | 603.582 | 25.606 | 26.242 | 1306.256 | 26.922 | 27.164 | 38.705 | 30.001 | 2.1 | 0.9 | 0.6 | 0.5 | 0.1
756 | 30/07/2025 09:38:56.097 | 99.192 | 71 | 100 | 71 | 52 | 26.795 | 9.285 | 6.866 | 134.792 | 28.39 | 28.224 | 27.283 | 603.75 | 25.605 | 26.215 | 1318.143 | 26.902 | 27.166 | 38.45 | 30.001 | 2.1 | 0.9 | 0.6 | 0.5 | 0.1
757 | 30/07/2025 09:38:57.734 | 99.072 | 71 | 100 | 70 | 52 | 27.295 | 9.458 | 6.901 | 134.565 | 28.378 | 28.237 | 27.254 | 602.813 | 25.602 | 26.229 | 1312.871 | 27.092 | 27.169 | 38.567 | 31.001 | 2.1 | 1.6 | 0.6 | 0.5 | 0.1
758 | 30/07/2025 09:38:59.370 | 99 | 70 | 100 | 71 | 52 | 29.877 | 9.576 | 6.9 | 134.734 | 28.402 | 28.202 | 27.307 | 602.441 | 25.606 | 26.225 | 1320.407 | 27.062 | 27.145 | 38.23 | 30.001 | 1.1 | 0.8 | 0.6 | 0.5 | 0.2
759 | 30/07/2025 09:39:01.006 | 98.736 | 70 | 100 | 71 | 52 | 29.096 | 9.43 | 6.9 | 134.443 | 28.371 | 28.232 | 27.3 | 602.43 | 25.595 | 26.211 | 1325.852 | 27.057 | 27.161 | 38.475 | 29.001 | 1.1 | 0.6 | 0.6 | 0.5 | 0.2
760 | 30/07/2025 09:39:02.642 | 98.64 | 70 | 100 | 70 | 52 | 29.557 | 9.424 | 6.868 | 134.747 | 28.394 | 28.225 | 27.287 | 602.446 | 25.618 | 26.222 | 1327.748 | 27.04 | 27.164 | 38.644 | 29.001 | 2.9 | 0.7 | 0.7 | 1.1 | 0.3
761 | 30/07/2025 09:39:04.278 | 98.64 | 72 | 100 | 71 | 52 | 29.82 | 9.599 | 6.866 | 134.703 | 28.391 | 28.229 | 27.266 | 602.434 | 25.599 | 26.218 | 1321.469 | 27.065 | 27.172 | 38.416 | 32.001 | 2.9 | 1.3 | 0.7 | 1.1 | 0.3
762 | 30/07/2025 09:39:05.914 | 98.352 | 70 | 100 | 71 | 53 | 26.217 | 9.401 | 6.868 | 134.704 | 28.402 | 28.222 | 27.262 | 602.264 | 25.609 | 26.235 | 1317.806 | 27.082 | 27.164 | 38.535 | 32.001 | 2.9 | 1.3 | 0.7 | 1.1 | 0.3
763 | 30/07/2025 09:39:07.549 | 98.472 | 70 | 100 | 69 | 52 | 27.624 | 9.579 | 6.848 | 134.635 | 28.399 | 28.215 | 27.307 | 602.553 | 25.612 | 26.21 | 1305.238 | 27.062 | 27.141 | 38.16 | 23.001 | 2.8 | 0.8 | 0 | 0.4 | 0.3
764 | 30/07/2025 09:39:09.186 | 98.736 | 71 | 100 | 70 | 51 | 29.903 | 9.577 | 6.85 | 134.288 | 28.41 | 28.242 | 27.28 | 602.372 | 25.587 | 26.207 | 1300.122 | 26.917 | 27.168 | 38.609 | 30.001 | 2.8 | 1.6 | 0 | 0.4 | 0.3
765 | 30/07/2025 09:39:10.820 | 98.088 | 70 | 100 | 70 | 51 | 26.568 | 9.441 | 6.829 | 134.759 | 28.419 | 28.239 | 27.298 | 602.449 | 25.591 | 26.199 | 1300.287 | 27.023 | 27.17 | 38.547 | 27.001 | 3 | 1.7 | 0.6 | 0.5 | 0.3
766 | 30/07/2025 09:39:12.453 | 98.808 | 71 | 100 | 71 | 52 | 29.722 | 9.574 | 6.83 | 134.71 | 28.409 | 28.222 | 27.261 | 602.199 | 25.587 | 26.215 | 1297.424 | 27.104 | 27.17 | 38.399 | 28.001 | 3 | 1.3 | 0.6 | 0.5 | 0.3
767 | 30/07/2025 09:39:14.089 | 98.712 | 71 | 100 | 72 | 52 | 29.447 | 9.46 | 6.827 | 134.813 | 28.427 | 28.215 | 27.283 | 602.337 | 25.598 | 26.205 | 1285.691 | 27.066 | 27.16 | 38.427 | 28.001 | 3 | 1.3 | 0.6 | 0.5 | 0.3
768 | 30/07/2025 09:39:15.724 | 98.904 | 70 | 100 | 71 | 52 | 25.914 | 9.355 | 6.826 | 134.576 | 28.401 | 28.22 | 27.294 | 602.468 | 25.589 | 26.186 | 1282.397 | 26.924 | 27.155 | 38.208 | 27.001 | 1.7 | 0.7 | 0 | 1.1 | 0.3
769 | 30/07/2025 09:39:17.361 | 98.976 | 70 | 100 | 71 | 52 | 28.279 | 9.573 | 6.852 | 134.567 | 28.412 | 28.235 | 27.296 | 602.252 | 25.581 | 26.208 | 1287.62 | 26.893 | 27.161 | 38.617 | 29.001 | 1.7 | 1.3 | 0 | 1.1 | 0.3
770 | 30/07/2025 09:39:18.997 | 99.024 | 71 | 100 | 70 | 55 | 26.739 | 9.577 | 6.861 | 134.723 | 28.399 | 28.239 | 27.29 | 602.458 | 25.578 | 26.2 | 1290.827 | 26.911 | 27.188 | 38.552 | 29.001 | 1.1 | 0.6 | 0.1 | 0.6 | 0.3
771 | 30/07/2025 09:39:20.632 | 98.424 | 70 | 100 | 71 | 51 | 27.158 | 9.775 | 6.867 | 134.692 | 28.413 | 28.227 | 27.242 | 602.16 | 25.606 | 26.208 | 1288.296 | 26.954 | 27.171 | 38.569 | 30.001 | 1.1 | 0.3 | 0.1 | 0.6 | 0.3
772 | 30/07/2025 09:39:22.267 | 97.8 | 70 | 100 | 70 | 53 | 29.833 | 9.483 | 6.865 | 134.756 | 28.408 | 28.206 | 27.294 | 602.471 | 25.59 | 26.31 | 1287.251 | 26.92 | 27.159 | 38.289 | 30.001 | 3.4 | 0 | 0 | 0.5 | 0.3
773 | 30/07/2025 09:39:23.901 | 98.16 | 70 | 100 | 70 | 52 | 29.078 | 9.29 | 6.865 | 134.364 | 28.397 | 28.23 | 27.27 | 603.51 | 25.601 | 26.215 | 1290.035 | 26.938 | 27.155 | 38.39 | 30.001 | 3.4 | 0 | 0 | 0.5 | 0.3
774 | 30/07/2025 09:39:25.535 | 98.16 | 70 | 100 | 70 | 52 | 25.873 | 9.568 | 6.867 | 134.947 | 28.415 | 28.229 | 27.289 | 603.719 | 25.624 | 26.338 | 1301.646 | 27.04 | 27.161 | 38.512 | 30.001 | 3.4 | 0.6 | 0 | 0.5 | 0.3
775 | 30/07/2025 09:39:27.173 | 97.896 | 70 | 100 | 71 | 52 | 28.843 | 9.431 | 6.901 | 134.797 | 28.388 | 28.232 | 27.276 | 603.676 | 25.601 | 26.223 | 1307.848 | 27.08 | 27.169 | 38.588 | 29.001 | 1.6 | 0.1 | 0.6 | 0.3 | 0.3
776 | 30/07/2025 09:39:28.808 | 97.92 | 71 | 100 | 70 | 52 | 26.331 | 9.285 | 6.9 | 134.947 | 28.41 | 28.222 | 27.269 | 602.907 | 25.606 | 26.34 | 1307.728 | 27.069 | 27.165 | 38.361 | 29.001 | 1.6 | 1.8 | 0.6 | 0.3 | 0.3
777 | 30/07/2025 09:39:30.442 | 98.304 | 70 | 100 | 72 | 53 | 27.81 | 9.421 | 6.934 | 134.715 | 28.387 | 28.205 | 27.294 | 602.568 | 25.594 | 26.227 | 1307.124 | 26.933 | 27.164 | 38.241 | 26.001 | 3.4 | 2.2 | 0 | 1.4 | 0.2
778 | 30/07/2025 09:39:32.078 | 98.664 | 70 | 100 | 71 | 52 | 29.948 | 9.515 | 6.938 | 134.656 | 28.371 | 28.231 | 27.271 | 602.436 | 25.593 | 26.357 | 1315.795 | 26.977 | 27.149 | 38.619 | 26.001 | 3.4 | 2.2 | 0 | 1.4 | 0.2
779 | 30/07/2025 09:39:33.714 | 98.4 | 69 | 100 | 70 | 52 | 28.529 | 9.575 | 6.936 | 134.8 | 28.387 | 28.227 | 27.31 | 602.445 | 25.601 | 26.223 | 1312.738 | 27.05 | 27.168 | 38.553 | 28.001 | 3.4 | 1.5 | 0 | 1.4 | 0.2
780 | 30/07/2025 09:39:35.371 | 98.856 | 70 | 100 | 71 | 52 | 25.999 | 9.576 | 6.937 | 134.693 | 28.369 | 28.231 | 27.264 | 602.235 | 25.596 | 26.368 | 1317.747 | 27.084 | 27.179 | 38.352 | 23.001 | 3.6 | 0.8 | 0 | 0.5 | 0.3
781 | 30/07/2025 09:39:37.007 | 98.616 | 71 | 100 | 71 | 52 | 29.331 | 9.578 | 6.945 | 134.894 | 28.405 | 28.211 | 27.292 | 602.394 | 25.608 | 26.346 | 1326.25 | 27.065 | 27.149 | 38.173 | 25.001 | 3.6 | 0.6 | 0 | 0.5 | 0.3
782 | 30/07/2025 09:39:38.641 | 98.928 | 70 | 100 | 70 | 51 | 25.982 | 9.581 | 6.988 | 134.654 | 28.391 | 28.21 | 27.28 | 602.265 | 25.594 | 26.366 | 1326.58 | 26.948 | 27.139 | 38.325 | 26.001 | 3.6 | 0.9 | 0.6 | 0.5 | 0.3
783 | 30/07/2025 09:39:40.275 | 99.144 | 73 | 100 | 71 | 50 | 28.325 | 9.485 | 6.953 | 134.713 | 28.417 | 28.237 | 27.281 | 602.89 | 25.613 | 26.346 | 1325.541 | 27.04 | 27.169 | 38.574 | 31.001 | 3.6 | 0.6 | 0.6 | 0.5 | 0.3
784 | 30/07/2025 09:39:41.919 | 98.832 | 69 | 100 | 71 | 51 | 29.962 | 9.707 | 6.901 | 134.617 | 28.414 | 28.235 | 27.261 | 603.598 | 25.589 | 26.337 | 1318.407 | 27.07 | 27.18 | 38.346 | 31.001 | 3.6 | 0.6 | 0.6 | 0.5 | 0.3
785 | 30/07/2025 09:39:43.554 | 98.16 | 71 | 100 | 70 | 50 | 27.837 | 9.435 | 6.902 | 134.735 | 28.417 | 28.218 | 27.253 | 603.488 | 25.586 | 26.352 | 1331.789 | 26.938 | 27.161 | 38.295 | 26.001 | 2.3 | 1 | 0 | 1.9 | 0.2
786 | 30/07/2025 09:39:45.189 | 97.824 | 69 | 100 | 70 | 53 | 26.181 | 9.571 | 6.898 | 134.762 | 28.413 | 28.211 | 27.313 | 603.735 | 25.582 | 26.343 | 1337.222 | 26.913 | 27.139 | 38.412 | 26.001 | 2.3 | 0.5 | 0 | 1.9 | 0.2
787 | 30/07/2025 09:39:46.822 | 97.608 | 70 | 100 | 70 | 52 | 29.021 | 9.509 | 6.901 | 134.641 | 28.415 | 28.22 | 27.293 | 603.521 | 25.597 | 26.347 | 1330.961 | 26.909 | 27.141 | 38.399 | 24.001 | 3.7 | 1.4 | 1.2 | 0.1 | 0.2
788 | 30/07/2025 09:39:48.457 | 98.304 | 72 | 100 | 71 | 53 | 25.909 | 9.413 | 6.9 | 134.717 | 28.412 | 28.235 | 27.285 | 602.469 | 25.582 | 26.338 | 1328.965 | 26.884 | 27.166 | 38.489 | 28.001 | 3.7 | 1.9 | 1.2 | 0.1 | 0.2
789 | 30/07/2025 09:39:50.093 | 98.376 | 71 | 99 | 71 | 52 | 28.829 | 9.429 | 6.902 | 134.768 | 28.395 | 28.226 | 27.258 | 602.156 | 25.574 | 26.348 | 1327.489 | 26.973 | 27.167 | 38.365 | 28.001 | 3.7 | 1.9 | 1.2 | 0.1 | 0.2
790 | 30/07/2025 09:39:51.727 | 98.208 | 70 | 100 | 70 | 52 | 29.996 | 9.416 | 6.899 | 134.863 | 28.413 | 28.222 | 27.272 | 602.385 | 25.606 | 26.327 | 1320.521 | 26.95 | 27.153 | 38.345 | 26.001 | 2.4 | 0.5 | 0.9 | 0.7 | 0.2
791 | 30/07/2025 09:39:53.362 | 97.992 | 70 | 100 | 72 | 50 | 27.267 | 9.236 | 6.901 | 134.528 | 28.396 | 28.223 | 27.288 | 602.701 | 25.587 | 26.331 | 1327.082 | 26.924 | 27.153 | 38.295 | 24.001 | 2.4 | 0.6 | 0.9 | 0.7 | 0.2
792 | 30/07/2025 09:39:54.998 | 98.448 | 70 | 100 | 70 | 52 | 26.624 | 9.48 | 6.937 | 134.575 | 28.405 | 28.244 | 27.273 | 602.318 | 25.597 | 26.341 | 1327.762 | 26.888 | 27.162 | 38.664 | 24.001 | 3.8 | 1.7 | 0.6 | 0.5 | 0.2
793 | 30/07/2025 09:39:56.631 | 98.232 | 70 | 100 | 70 | 53 | 28.441 | 9.577 | 6.936 | 134.733 | 28.402 | 28.24 | 27.285 | 602.441 | 25.593 | 26.348 | 1327.581 | 26.913 | 27.187 | 38.492 | 28.001 | 3.8 | 1 | 0.6 | 0.5 | 0.2
794 | 30/07/2025 09:39:58.265 | 98.352 | 71 | 100 | 70 | 53 | 25.95 | 9.282 | 6.935 | 134.802 | 28.55 | 28.219 | 27.253 | 603.384 | 25.614 | 26.346 | 1325.189 | 27.072 | 27.16 | 38.395 | 28.001 | 3.8 | 1 | 0.6 | 0.5 | 0.2
795 | 30/07/2025 09:39:59.900 | 98.208 | 70 | 100 | 70 | 52 | 29.226 | 9.582 | 6.934 | 134.724 | 28.545 | 28.212 | 27.293 | 603.735 | 25.605 | 26.356 | 1319.781 | 26.92 | 27.159 | 38.16 | 27.001 | 3.1 | 1.7 | 0 | 0 | 0.2
796 | 30/07/2025 09:40:01.536 | 98.568 | 70 | 100 | 71 | 53 | 29.96 | 9.579 | 6.935 | 134.551 | 28.528 | 28.225 | 27.278 | 603.513 | 25.597 | 26.374 | 1322.657 | 27.08 | 27.152 | 38.556 | 26.001 | 3.1 | 1 | 0 | 0 | 0.2
797 | 30/07/2025 09:40:03.170 | 97.368 | 69 | 100 | 70 | 52 | 26.777 | 9.485 | 6.936 | 134.767 | 28.558 | 28.229 | 27.28 | 603.606 | 25.608 | 26.35 | 1325.417 | 27.027 | 27.158 | 38.484 | 27.001 | 2.4 | 0.9 | 0.1 | 0 | 0.2
798 | 30/07/2025 09:40:04.803 | 98.28 | 69 | 100 | 70 | 53 | 29.957 | 9.502 | 6.937 | 134.778 | 28.535 | 28.228 | 27.278 | 603.518 | 25.608 | 26.388 | 1322.703 | 27.062 | 27.177 | 38.464 | 24.001 | 2.4 | 0.8 | 0.1 | 0 | 0.2
799 | 30/07/2025 09:40:06.441 | 98.16 | 70 | 100 | 70 | 52 | 27.968 | 9.44 | 6.9 | 134.748 | 28.537 | 28.228 | 27.266 | 603.548 | 25.62 | 26.353 | 1327.782 | 27.079 | 27.158 | 38.627 | 26.001 | 2.8 | 1.3 | 0.3 | 0.6 | 0.2
800 | 30/07/2025 09:40:08.076 | 98.88 | 71 | 100 | 70 | 53 | 26.313 | 9.446 | 6.864 | 134.63 | 28.515 | 28.212 | 27.291 | 603.677 | 25.595 | 26.361 | 1337.185 | 27.081 | 27.157 | 38.177 | 26.001 | 2.8 | 1.3 | 0.3 | 0.6 | 0.2
801 | 30/07/2025 09:40:09.710 | 98.88 | 72 | 100 | 70 | 53 | 29.611 | 9.575 | 6.865 | 133.201 | 28.533 | 28.229 | 27.271 | 603.569 | 25.602 | 26.358 | 1330.012 | 26.977 | 27.154 | 38.611 | 27.001 | 2.8 | 0.6 | 0.3 | 0.6 | 0.2
802 | 30/07/2025 09:40:11.346 | 99.12 | 70 | 100 | 69 | 52 | 29.831 | 9.576 | 6.901 | 133.328 | 28.537 | 28.246 | 27.299 | 603.703 | 25.587 | 26.36 | 1330.481 | 27.049 | 27.166 | 38.548 | 28.001 | 1.6 | 2.2 | 0 | 0.8 | 0.3
803 | 30/07/2025 09:40:12.982 | 98.832 | 70 | 100 | 69 | 53 | 28.85 | 9.575 | 6.9 | 133.571 | 28.553 | 28.228 | 27.264 | 603.544 | 25.6 | 26.352 | 1334.384 | 27.074 | 27.158 | 38.602 | 33.001 | 1.6 | 1 | 0 | 0.8 | 0.3
804 | 30/07/2025 09:40:14.617 | 99.12 | 72 | 100 | 70 | 52 | 29.969 | 9.488 | 6.901 | 133.225 | 28.556 | 28.224 | 27.26 | 603.5 | 25.595 | 26.342 | 1329.424 | 27.073 | 27.164 | 38.338 | 29.001 | 1 | 1.7 | 0.7 | 0.6 | 0.2
805 | 30/07/2025 09:40:16.252 | 99.144 | 71 | 100 | 71 | 53 | 27.325 | 9.584 | 6.902 | 133.065 | 28.561 | 28.216 | 27.291 | 603.555 | 25.594 | 26.37 | 1324.97 | 27.077 | 27.14 | 38.286 | 29.001 | 1 | 1.7 | 0.7 | 0.6 | 0.2
806 | 30/07/2025 09:40:17.889 | 99.24 | 71 | 100 | 71 | 52 | 26.593 | 9.546 | 6.9 | 133.061 | 28.569 | 28.246 | 27.293 | 603.677 | 25.609 | 26.343 | 1327.653 | 26.894 | 27.166 | 38.588 | 26.001 | 1 | 1.5 | 0.7 | 0.6 | 0.2
807 | 30/07/2025 09:40:19.525 | 99.312 | 71 | 100 | 72 | 52 | 29.833 | 9.557 | 6.901 | 133.24 | 28.545 | 28.237 | 27.28 | 603.531 | 25.595 | 26.347 | 1319.998 | 27.082 | 27.174 | 38.571 | 25.001 | 1.2 | 1.6 | 0.9 | 0 | 0.2
808 | 30/07/2025 09:40:21.161 | 98.4 | 71 | 100 | 70 | 52 | 29.592 | 9.576 | 6.9 | 133.338 | 28.558 | 28.225 | 27.251 | 602.248 | 25.597 | 26.339 | 1324.313 | 27.082 | 27.153 | 38.472 | 27.001 | 1.2 | 0.8 | 0.9 | 0 | 0.2
809 | 30/07/2025 09:40:22.798 | 98.424 | 70 | 100 | 70 | 52 | 29.324 | 9.575 | 6.901 | 133.163 | 28.558 | 28.211 | 27.286 | 602.343 | 25.565 | 26.347 | 1317.642 | 26.968 | 27.165 | 38.264 | 26.001 | 2.4 | 0.8 | 0 | 0.5 | 0.2
810 | 30/07/2025 09:40:24.434 | 98.832 | 71 | 100 | 70 | 52 | 30.015 | 9.436 | 6.899 | 133.289 | 28.562 | 28.226 | 27.288 | 602.344 | 25.599 | 26.343 | 1317.51 | 26.906 | 27.139 | 38.376 | 28.001 | 2.4 | 0.7 | 0 | 0.5 | 0.2
811 | 30/07/2025 09:40:26.072 | 98.952 | 71 | 100 | 71 | 52 | 26.811 | 9.575 | 6.902 | 133.267 | 28.552 | 28.246 | 27.302 | 602.407 | 25.594 | 26.323 | 1310.027 | 27.044 | 27.186 | 38.493 | 28.001 | 2.4 | 0.7 | 0 | 0.5 | 0.2
812 | 30/07/2025 09:40:27.709 | 99.12 | 71 | 100 | 70 | 52 | 27.201 | 9.484 | 6.936 | 133.194 | 28.547 | 28.223 | 27.257 | 602.138 | 25.577 | 26.346 | 1310.703 | 27.081 | 27.158 | 38.495 | 23.001 | 2 | 0.9 | 0.6 | 0.9 | 0.2
813 | 30/07/2025 09:40:29.345 | 99.288 | 72 | 100 | 71 | 52 | 29.884 | 9.727 | 6.9 | 133.229 | 28.554 | 28.22 | 27.292 | 602.304 | 25.601 | 26.336 | 1298.452 | 26.993 | 27.161 | 38.263 | 27.001 | 2 | 1.3 | 0.6 | 0.9 | 0.2
814 | 30/07/2025 09:40:30.980 | 98.736 | 70 | 100 | 70 | 52 | 26.174 | 9.47 | 6.901 | 133.256 | 28.545 | 28.209 | 27.276 | 603.471 | 25.599 | 26.336 | 1297.754 | 27.07 | 27.146 | 38.255 | 25.001 | 3 | 2.2 | 0.1 | 0.9 | 0.3
815 | 30/07/2025 09:40:32.614 | 98.52 | 70 | 100 | 71 | 52 | 29.554 | 9.563 | 6.927 | 134.564 | 28.552 | 28.227 | 27.293 | 603.572 | 25.587 | 26.336 | 1295.312 | 27.059 | 27.148 | 38.378 | 30.001 | 3 | 1.1 | 0.1 | 0.9 | 0.3
816 | 30/07/2025 09:40:34.250 | 98.328 | 70 | 100 | 70 | 52 | 29.822 | 9.476 | 6.936 | 134.749 | 28.536 | 28.24 | 27.272 | 603.475 | 25.579 | 26.371 | 1308.312 | 27.048 | 27.179 | 38.551 | 30.001 | 3 | 1.1 | 0.1 | 0.9 | 0.3
817 | 30/07/2025 09:40:35.885 | 98.16 | 70 | 100 | 71 | 52 | 26.286 | 9.489 | 6.935 | 134.886 | 28.549 | 28.225 | 27.268 | 603.425 | 25.622 | 26.365 | 1317.837 | 27.072 | 27.153 | 38.374 | 27.001 | 2.9 | 1.4 | 0.6 | 0.5 | 0.3
818 | 30/07/2025 09:40:37.519 | 98.064 | 70 | 100 | 71 | 52 | 27.744 | 9.732 | 6.903 | 134.656 | 28.531 | 28.22 | 27.274 | 603.555 | 25.604 | 26.354 | 1321.959 | 27.067 | 27.154 | 38.339 | 32.001 | 2.9 | 0.6 | 0.6 | 0.5 | 0.3
819 | 30/07/2025 09:40:39.156 | 97.992 | 70 | 100 | 71 | 53 | 29.976 | 9.342 | 6.901 | 134.504 | 28.53 | 28.231 | 27.287 | 603.613 | 25.585 | 26.373 | 1324.928 | 27.075 | 27.147 | 38.48 | 24.001 | 3.1 | 2.2 | 0.9 | 0 | 0.3
820 | 30/07/2025 09:40:40.792 | 97.512 | 70 | 100 | 70 | 52 | 26.8 | 9.291 | 6.934 | 134.397 | 28.512 | 28.248 | 27.281 | 603.534 | 25.585 | 26.355 | 1324.774 | 27.058 | 27.168 | 38.468 | 25.001 | 3.1 | 1.5 | 0.9 | 0 | 0.3
821 | 30/07/2025 09:40:42.428 | 97.488 | 70 | 100 | 70 | 52 | 29.807 | 9.428 | 6.937 | 135.056 | 28.518 | 28.23 | 27.284 | 603.453 | 25.605 | 26.37 | 1325.532 | 27.05 | 27.175 | 38.626 | 26.001 | 1.9 | 0.7 | 0 | 0.7 | 0.3
822 | 30/07/2025 09:40:44.063 | 97.32 | 70 | 100 | 70 | 51 | 29.578 | 9.447 | 6.986 | 134.834 | 28.536 | 28.222 | 27.245 | 603.504 | 25.596 | 26.36 | 1327.724 | 27.081 | 27.163 | 38.423 | 26.001 | 1.9 | 0.7 | 0 | 0.7 | 0.3
823 | 30/07/2025 09:40:45.697 | 97.296 | 70 | 100 | 70 | 52 | 26.029 | 9.345 | 6.987 | 134.589 | 28.525 | 28.206 | 27.286 | 603.485 | 25.589 | 26.35 | 1322.102 | 27.095 | 27.161 | 38.409 | 23.001 | 1.9 | 0.9 | 0 | 0.7 | 0.3
824 | 30/07/2025 09:40:47.332 | 97.416 | 71 | 100 | 71 | 53 | 28.358 | 9.543 | 6.987 | 134.706 | 28.539 | 28.23 | 27.276 | 603.55 | 25.605 | 26.353 | 1332.314 | 27.042 | 27.14 | 38.552 | 26.001 | 1 | 1.2 | 0.7 | 0.5 | 0.3
825 | 30/07/2025 09:40:48.966 | 97.752 | 70 | 100 | 70 | 53 | 26.785 | 9.576 | 6.944 | 134.26 | 28.542 | 28.237 | 27.279 | 603.512 | 25.584 | 26.361 | 1337.241 | 27.074 | 27.167 | 38.468 | 24.001 | 1 | 0.6 | 0.7 | 0.5 | 0.3
826 | 30/07/2025 09:40:50.600 | 98.304 | 71 | 100 | 71 | 52 | 27.236 | 9.8 | 6.935 | 135.026 | 28.557 | 28.231 | 27.269 | 603.614 | 25.605 | 26.363 | 1332.351 | 27.068 | 27.158 | 38.647 | 26.001 | 1.6 | 1.9 | 0.6 | 0 | 0.3
827 | 30/07/2025 09:40:52.234 | 98.376 | 70 | 100 | 71 | 51 | 29.922 | 9.437 | 6.987 | 133.473 | 28.549 | 28.223 | 27.257 | 603.549 | 25.604 | 26.345 | 1320.181 | 27.082 | 27.253 | 38.473 | 26.001 | 1.6 | 1.9 | 0.6 | 0 | 0.3
828 | 30/07/2025 09:40:53.889 | 98.736 | 71 | 100 | 70 | 52 | 29.202 | 9.505 | 6.988 | 133.154 | 28.56 | 28.205 | 27.29 | 603.678 | 25.59 | 26.359 | 1315.581 | 27.073 | 27.132 | 38.375 | 25.001 | 1.6 | 1.8 | 0.6 | 0 | 0.3
829 | 30/07/2025 09:40:55.520 | 98.856 | 71 | 100 | 71 | 52 | 25.953 | 9.555 | 6.987 | 133.101 | 28.559 | 28.236 | 27.302 | 603.743 | 25.586 | 26.329 | 1315.144 | 27.047 | 27.168 | 38.624 | 27.001 | 3.6 | 2 | 0.6 | 0.5 | 0.2
830 | 30/07/2025 09:40:57.159 | 98.568 | 70 | 100 | 71 | 52 | 28.963 | 9.474 | 6.937 | 134.673 | 28.546 | 28.244 | 27.261 | 603.503 | 25.57 | 26.329 | 1307.701 | 27.073 | 27.179 | 38.596 | 28.001 | 3.6 | 0.8 | 0.6 | 0.5 | 0.2
831 | 30/07/2025 09:40:58.794 | 97.92 | 70 | 100 | 71 | 53 | 26.41 | 9.282 | 6.935 | 134.822 | 28.545 | 28.228 | 27.285 | 603.545 | 25.598 | 26.336 | 1317.256 | 27.072 | 27.169 | 38.397 | 25.001 | 2.8 | 2.4 | 0 | 0.5 | 0.1
832 | 30/07/2025 09:41:00.429 | 97.368 | 70 | 100 | 70 | 51 | 27.765 | 9.31 | 6.936 | 134.644 | 28.542 | 28.211 | 27.413 | 603.439 | 25.586 | 26.342 | 1312.434 | 27.091 | 27.163 | 38.537 | 27.001 | 2.8 | 1.2 | 0 | 0.5 | 0.1
833 | 30/07/2025 09:41:02.065 | 97.152 | 71 | 100 | 70 | 54 | 29.953 | 9.393 | 6.933 | 134.691 | 28.559 | 28.223 | 27.432 | 603.62 | 25.598 | 26.333 | 1313.536 | 27.06 | 27.144 | 38.32 | 27.001 | 2.8 | 1.2 | 0 | 0.5 | 0.1
834 | 30/07/2025 09:41:03.698 | 97.08 | 70 | 100 | 71 | 52 | 28.584 | 9.282 | 6.936 | 134.549 | 28.539 | 28.242 | 27.434 | 603.577 | 25.592 | 26.328 | 1319.438 | 27.046 | 27.181 | 38.652 | 25.001 | 3.1 | 1.5 | 0 | 0.5 | 0.2
835 | 30/07/2025 09:41:05.333 | 97.368 | 70 | 100 | 71 | 51 | 25.976 | 9.422 | 6.99 | 134.826 | 28.541 | 28.232 | 27.276 | 603.462 | 25.602 | 26.351 | 1308.308 | 27.065 | 27.159 | 38.55 | 23.001 | 3.1 | 1.8 | 0 | 0.5 | 0.2
836 | 30/07/2025 09:41:06.972 | 97.344 | 70 | 100 | 70 | 52 | 29.591 | 9.288 | 6.988 | 134.675 | 28.553 | 28.237 | 27.392 | 603.548 | 25.603 | 26.348 | 1295.93 | 27.083 | 27.176 | 38.515 | 34.001 | 3.1 | 0.1 | 0.6 | 1.5 | 0.2
837 | 30/07/2025 09:41:08.607 | 97.128 | 70 | 100 | 70 | 52 | 26.023 | 9.429 | 6.935 | 134.668 | 28.554 | 28.211 | 27.435 | 603.618 | 25.597 | 26.344 | 1280.549 | 27.065 | 27.148 | 38.603 | 28.001 | 3.1 | 1.2 | 0.6 | 1.5 | 0.2
838 | 30/07/2025 09:41:10.242 | 96.936 | 70 | 100 | 70 | 52 | 28.254 | 9.437 | 6.98 | 134.549 | 28.55 | 28.241 | 27.438 | 603.635 | 25.606 | 26.362 | 1285.321 | 27.055 | 27.181 | 38.445 | 28.001 | 3.1 | 1.2 | 0.6 | 1.5 | 0.2
839 | 30/07/2025 09:41:11.876 | 96.336 | 69 | 100 | 70 | 52 | 30.007 | 9.428 | 7.036 | 134.72 | 28.528 | 28.235 | 27.422 | 602.347 | 25.581 | 26.361 | 1285.622 | 27.061 | 27.169 | 38.63 | 25.001 | 1.5 | 0.3 | 0.4 | 0.8 | 0.3
840 | 30/07/2025 09:41:13.512 | 96.336 | 68 | 100 | 71 | 52 | 27.991 | 9.504 | 6.935 | 134.932 | 28.533 | 28.241 | 27.405 | 602.208 | 25.622 | 26.356 | 1301.643 | 27.071 | 27.166 | 38.544 | 21.001 | 1.5 | 3.3 | 0.4 | 0.8 | 0.3
841 | 30/07/2025 09:41:15.144 | 96.744 | 68 | 100 | 70 | 53 | 26.24 | 9.444 | 6.935 | 134.657 | 28.504 | 28.218 | 27.416 | 602.374 | 25.592 | 26.351 | 1305.259 | 27.078 | 27.167 | 38.348 | 27.001 | 2.3 | 1.1 | 0.9 | 0.7 | 0.3
842 | 30/07/2025 09:41:16.782 | 96.72 | 69 | 100 | 70 | 51 | 29.083 | 9.551 | 6.933 | 134.722 | 28.537 | 28.217 | 27.448 | 602.429 | 25.617 | 26.352 | 1311.348 | 27.063 | 27.143 | 38.255 | 26.001 | 2.3 | 0.9 | 0.9 | 0.7 | 0.3
843 | 30/07/2025 09:41:18.416 | 96.696 | 69 | 100 | 70 | 51 | 25.881 | 9.284 | 6.936 | 134.478 | 28.524 | 28.25 | 27.425 | 602.4 | 25.587 | 26.348 | 1312.643 | 27.07 | 27.164 | 38.706 | 22.001 | 2 | 1.4 | 0.6 | 0.1 | 0.2
844 | 30/07/2025 09:41:20.055 | 97.056 | 69 | 100 | 70 | 52 | 28.825 | 9.495 | 6.936 | 134.889 | 28.537 | 28.232 | 27.419 | 602.274 | 25.593 | 26.354 | 1312.134 | 27.053 | 27.157 | 38.726 | 22.001 | 2 | 1.4 | 0.6 | 0.1 | 0.2
845 | 30/07/2025 09:41:21.691 | 97.176 | 70 | 100 | 71 | 52 | 29.978 | 9.411 | 6.934 | 134.782 | 28.562 | 28.234 | 27.419 | 602.288 | 25.595 | 26.351 | 1318.335 | 27.082 | 27.161 | 38.411 | 20.001 | 2 | 1.4 | 0.6 | 0.1 | 0.2
846 | 30/07/2025 09:41:23.327 | 97.368 | 70 | 100 | 71 | 52 | 27.328 | 9.501 | 6.935 | 134.553 | 28.555 | 28.206 | 27.422 | 602.406 | 25.581 | 26.359 | 1317.663 | 27.093 | 27.162 | 38.141 | 25.001 | 2.6 | 1.1 | 0.6 | 0 | 0.2
847 | 30/07/2025 09:41:24.961 | 97.68 | 69 | 100 | 70 | 51 | 29.951 | 9.562 | 6.934 | 134.579 | 28.554 | 28.22 | 27.43 | 602.391 | 25.584 | 26.355 | 1317.668 | 27.067 | 27.144 | 38.35 | 24.001 | 2.6 | 1.5 | 0.6 | 0 | 0.2
848 | 30/07/2025 09:41:26.595 | 97.608 | 71 | 100 | 69 | 52 | 28.646 | 9.432 | 6.938 | 134.5 | 28.546 | 28.228 | 27.424 | 602.416 | 25.59 | 26.36 | 1322.831 | 27.054 | 27.161 | 38.673 | 28.001 | 2.4 | 0.9 | 0.6 | 0.5 | 0.2
849 | 30/07/2025 09:41:28.228 | 98.112 | 71 | 100 | 70 | 51 | 26.016 | 9.405 | 6.936 | 135.024 | 28.566 | 28.23 | 27.415 | 602.377 | 25.599 | 26.354 | 1324.999 | 27.055 | 27.159 | 38.613 | 28.001 | 2.4 | 0.9 | 0.6 | 0.5 | 0.2
850 | 30/07/2025 09:41:29.861 | 97.944 | 70 | 100 | 70 | 52 | 29.381 | 9.461 | 7.005 | 133.221 | 28.546 | 28.227 | 27.401 | 602.214 | 25.579 | 26.338 | 1314.222 | 27.089 | 27.28 | 38.561 | 25.001 | 2.4 | 1 | 0.6 | 0.5 | 0.2
851 | 30/07/2025 09:41:31.496 | 97.536 | 70 | 100 | 71 | 52 | 29.996 | 9.43 | 6.996 | 133.186 | 28.558 | 28.208 | 27.428 | 602.281 | 25.592 | 26.332 | 1301.365 | 27.075 | 27.181 | 38.378 | 26.001 | 3 | 1.6 | 1.2 | 0.5 | 0.2
852 | 30/07/2025 09:41:33.128 | 97.944 | 71 | 100 | 71 | 52 | 28.395 | 9.548 | 6.935 | 132.909 | 28.544 | 28.242 | 27.432 | 602.252 | 25.566 | 26.324 | 1297.535 | 27.074 | 27.153 | 38.604 | 27.001 | 3 | 1.7 | 1.2 | 0.5 | 0.2
853 | 30/07/2025 09:41:34.763 | 98.208 | 71 | 100 | 69 | 52 | 29.997 | 9.576 | 6.936 | 133.267 | 28.551 | 28.233 | 27.42 | 602.44 | 25.593 | 26.329 | 1298.152 | 27.029 | 27.156 | 38.847 | 27.001 | 4.8 | 0.8 | 0 | 0.2 | 0.1
854 | 30/07/2025 09:41:36.397 | 98.064 | 70 | 100 | 71 | 53 | 28.07 | 9.576 | 6.935 | 133.311 | 28.553 | 28.238 | 27.423 | 603.582 | 25.582 | 26.316 | 1288.909 | 27.07 | 27.318 | 38.469 | 27.001 | 4.8 | 0.1 | 0 | 0.2 | 0.1
855 | 30/07/2025 09:41:38.031 | 97.248 | 70 | 100 | 70 | 52 | 26.192 | 9.507 | 6.937 | 133.117 | 28.539 | 28.213 | 27.417 | 602.134 | 25.584 | 26.344 | 1287.719 | 27.089 | 27.165 | 38.381 | 27.001 | 4.8 | 0.1 | 0 | 0.2 | 0.1
856 | 30/07/2025 09:41:39.666 | 97.248 | 69 | 100 | 71 | 52 | 29.599 | 9.507 | 6.934 | 133.183 | 28.558 | 28.222 | 27.438 | 602.394 | 25.607 | 26.346 | 1290.238 | 27.06 | 27.133 | 38.291 | 29.001 | 2.3 | 1.7 | 0 | 0.2 | 0.2
857 | 30/07/2025 09:41:41.303 | 97.56 | 72 | 100 | 70 | 53 | 29.947 | 9.456 | 6.936 | 133.136 | 28.521 | 28.247 | 27.416 | 602.299 | 25.591 | 26.355 | 1287.734 | 27.055 | 27.179 | 38.594 | 29.001 | 2.3 | 1 | 0 | 0.2 | 0.2
858 | 30/07/2025 09:41:42.939 | 97.344 | 70 | 100 | 70 | 52 | 28.812 | 9.276 | 6.936 | 133.316 | 28.544 | 28.237 | 27.433 | 602.416 | 25.611 | 26.355 | 1283.439 | 27.04 | 27.162 | 38.717 | 31.001 | 2.4 | 1.7 | 0.1 | 0.6 | 0.2
859 | 30/07/2025 09:41:44.574 | 97.512 | 70 | 100 | 71 | 52 | 30.089 | 9.56 | 6.937 | 133.094 | 28.528 | 28.24 | 27.401 | 602.202 | 25.595 | 26.361 | 1296.533 | 27.096 | 27.194 | 38.537 | 27.001 | 2.4 | 2.1 | 0.1 | 0.6 | 0.2
860 | 30/07/2025 09:41:46.207 | 97.32 | 70 | 100 | 70 | 52 | 27.444 | 9.731 | 6.935 | 133.381 | 28.535 | 28.2 | 27.414 | 602.291 | 25.606 | 26.367 | 1305.163 | 27.07 | 27.152 | 38.349 | 27.001 | 2.4 | 2.1 | 0.1 | 0.6 | 0.2
861 | 30/07/2025 09:41:47.844 | 97.2 | 71 | 100 | 69 | 52 | 26.738 | 9.578 | 6.933 | 133.086 | 28.52 | 28.233 | 27.432 | 602.485 | 25.598 | 26.356 | 1311.988 | 27.066 | 27.149 | 38.293 | 25.001 | 2.4 | 1.7 | 0 | 0.1 | 0.3
862 | 30/07/2025 09:41:49.479 | 96.984 | 70 | 100 | 70 | 52 | 29.779 | 9.279 | 6.938 | 133.254 | 28.52 | 28.231 | 27.427 | 602.196 | 25.59 | 26.364 | 1317.732 | 27.049 | 27.166 | 38.487 | 30.001 | 2.4 | 0.3 | 0 | 0.1 | 0.3
863 | 30/07/2025 09:41:51.112 | 97.008 | 71 | 100 | 70 | 52 | 29.548 | 9.424 | 6.934 | 133.442 | 28.534 | 28.233 | 27.411 | 602.267 | 25.607 | 26.34 | 1317.699 | 27.071 | 27.156 | 38.57 | 27.001 | 4.5 | 0.7 | 0.6 | 0.2 | 0.2
864 | 30/07/2025 09:41:52.750 | 96.744 | 69 | 100 | 70 | 52 | 29.296 | 9.458 | 6.936 | 133.234 | 28.528 | 28.227 | 27.399 | 602.164 | 25.588 | 26.365 | 1310.753 | 27.079 | 27.161 | 38.505 | 24.001 | 4.5 | 1.4 | 0.6 | 0.2 | 0.2
865 | 30/07/2025 09:41:54.384 | 96.624 | 70 | 100 | 70 | 52 | 29.986 | 9.483 | 6.935 | 133.355 | 28.549 | 28.21 | 27.447 | 602.47 | 25.593 | 26.335 | 1309.966 | 27.059 | 27.14 | 38.104 | 30.001 | 2.4 | 1.6 | 0 | 0.3 | 0.2
866 | 30/07/2025 09:41:56.019 | 96.768 | 70 | 100 | 70 | 52 | 26.707 | 9.536 | 6.936 | 132.97 | 28.539 | 28.254 | 27.43 | 602.331 | 25.583 | 26.346 | 1307.265 | 27.061 | 27.167 | 38.36 | 30.001 | 2.4 | 1.6 | 0 | 0.3 | 0.2
867 | 30/07/2025 09:41:57.656 | 96.864 | 70 | 100 | 70 | 52 | 27.183 | 9.429 | 6.936 | 134.753 | 28.55 | 28.226 | 27.417 | 602.256 | 25.598 | 26.358 | 1297.657 | 27.033 | 27.172 | 38.428 | 26.001 | 2.4 | 1.3 | 0 | 0.3 | 0.2
868 | 30/07/2025 09:41:59.295 | 96.504 | 71 | 100 | 69 | 52 | 29.93 | 9.555 | 6.935 | 134.716 | 28.557 | 28.238 | 27.41 | 602.296 | 25.579 | 26.349 | 1288.585 | 27.07 | 27.162 | 38.502 | 24.001 | 2.3 | 1.1 | 1.2 | 0 | 0.3
869 | 30/07/2025 09:42:00.930 | 96.72 | 71 | 100 | 71 | 53 | 26.244 | 9.517 | 6.935 | 134.765 | 28.57 | 28.223 | 27.411 | 602.319 | 25.599 | 26.357 | 1286.26 | 27.069 | 27.154 | 38.45 | 27.001 | 2.3 | 0.8 | 1.2 | 0 | 0.3
870 | 30/07/2025 09:42:02.565 | 96.456 | 70 | 100 | 71 | 52 | 29.66 | 9.163 | 6.977 | 134.522 | 28.54 | 28.217 | 27.46 | 602.263 | 25.574 | 26.337 | 1283.046 | 27.065 | 27.147 | 38.252 | 24.001 | 2.3 | 0.7 | 0 | 0.1 | 0.3
871 | 30/07/2025 09:42:04.200 | 97.032 | 69 | 100 | 70 | 52 | 29.949 | 9.484 | 6.985 | 134.451 | 28.541 | 28.232 | 27.424 | 602.367 | 25.577 | 26.362 | 1277.475 | 27.049 | 27.16 | 38.705 | 24.001 | 2.3 | 0.7 | 0 | 0.1 | 0.3
872 | 30/07/2025 09:42:05.836 | 96.576 | 70 | 100 | 71 | 52 | 26.467 | 9.305 | 6.935 | 134.875 | 28.559 | 28.232 | 27.424 | 600.911 | 25.577 | 26.329 | 1272.804 | 27.053 | 27.171 | 38.431 | 30.001 | 2.3 | 0.3 | 0 | 0.1 | 0.3
873 | 30/07/2025 09:42:07.471 | 96.36 | 70 | 100 | 71 | 51 | 27.834 | 9.581 | 6.976 | 133.141 | 28.543 | 28.232 | 27.401 | 600.725 | 25.574 | 26.332 | 1277.151 | 27.091 | 27.325 | 38.467 | 28.001 | 2.3 | 1.4 | 0.6 | 0 | 0.2
874 | 30/07/2025 09:42:09.105 | 97.176 | 70 | 100 | 70 | 52 | 29.966 | 9.393 | 6.986 | 133.221 | 28.552 | 28.201 | 27.427 | 600.9 | 25.603 | 26.337 | 1285.444 | 27.065 | 27.292 | 38.299 | 30.001 | 2.3 | 0.9 | 0.6 | 0 | 0.2
875 | 30/07/2025 09:42:10.738 | 96.864 | 70 | 100 | 70 | 52 | 26.727 | 9.285 | 6.986 | 132.894 | 28.532 | 28.231 | 27.429 | 602.242 | 25.586 | 26.337 | 1285.171 | 27.076 | 27.3 | 38.29 | 30.001 | 1.2 | 1 | 0.6 | 0.6 | 0.3
876 | 30/07/2025 09:42:12.374 | 97.344 | 72 | 100 | 71 | 51 | 29.884 | 9.429 | 6.988 | 133.205 | 28.561 | 28.233 | 27.432 | 602.342 | 25.615 | 26.344 | 1287.658 | 27.027 | 27.172 | 38.717 | 24.001 | 1.2 | 1.7 | 0.6 | 0.6 | 0.3
877 | 30/07/2025 09:42:14.010 | 98.088 | 71 | 100 | 71 | 52 | 29.613 | 9.509 | 6.988 | 133.298 | 28.545 | 28.237 | 27.419 | 602.32 | 25.599 | 26.33 | 1290.343 | 27.071 | 27.318 | 38.583 | 24.001 | 1.2 | 1.7 | 0.6 | 0.6 | 0.3
878 | 30/07/2025 09:42:15.645 | 98.16 | 71 | 100 | 70 | 51 | 26.181 | 9.447 | 6.989 | 133.205 | 28.549 | 28.218 | 27.415 | 602.165 | 25.598 | 26.369 | 1296.2 | 27.076 | 27.302 | 38.427 | 24.001 | 1.6 | 1.3 | 0.6 | 1.1 | 0.2
879 | 30/07/2025 09:42:17.279 | 98.016 | 71 | 100 | 71 | 52 | 28.317 | 9.502 | 6.986 | 133.246 | 28.539 | 28.222 | 27.45 | 602.495 | 25.612 | 26.361 | 1297.191 | 27.07 | 27.285 | 38.296 | 24.001 | 1.6 | 1.5 | 0.6 | 1.1 | 0.2
880 | 30/07/2025 09:42:18.918 | 98.352 | 71 | 100 | 70 | 52 | 27.012 | 9.574 | 6.987 | 133.005 | 28.545 | 28.236 | 27.433 | 602.325 | 25.595 | 26.361 | 1299.794 | 27.061 | 27.149 | 38.58 | 30.001 | 2.5 | 2.3 | 0.6 | 1.1 | 0.2
881 | 30/07/2025 09:42:20.555 | 97.944 | 70 | 100 | 71 | 51 | 27.197 | 9.578 | 6.988 | 133.289 | 28.528 | 28.24 | 27.446 | 602.358 | 25.6 | 26.348 | 1297.641 | 27.04 | 27.311 | 38.412 | 27.001 | 2.5 | 0.7 | 0.6 | 1.1 | 0.2
882 | 30/07/2025 09:42:22.199 | 98.112 | 70 | 100 | 70 | 53 | 29.934 | 9.291 | 6.989 | 133.236 | 28.536 | 28.232 | 27.408 | 602.172 | 25.586 | 26.375 | 1297.081 | 27.09 | 27.322 | 38.667 | 27.001 | 2.5 | 0.7 | 0.6 | 1.1 | 0.2
883 | 30/07/2025 09:42:23.833 | 98.016 | 71 | 100 | 71 | 52 | 29.186 | 9.573 | 6.987 | 133.434 | 28.536 | 28.21 | 27.421 | 602.316 | 25.597 | 26.359 | 1297.671 | 27.066 | 27.301 | 38.348 | 30.001 | 3.7 | 0.9 | 0.9 | 0.5 | 0.3
884 | 30/07/2025 09:42:25.467 | 98.208 | 71 | 99 | 71 | 52 | 25.898 | 9.32 | 6.986 | 132.956 | 28.529 | 28.237 | 27.432 | 602.382 | 25.598 | 26.349 | 1311.343 | 27.064 | 27.292 | 38.284 | 26.001 | 3.7 | 1.1 | 0.9 | 0.5 | 0.3
885 | 30/07/2025 09:42:27.104 | 97.704 | 70 | 100 | 70 | 53 | 29.887 | 9.319 | 7.004 | 133.085 | 28.54 | 28.235 | 27.419 | 602.391 | 25.609 | 26.355 | 1317.527 | 27.048 | 27.297 | 38.616 | 32.001 | 3.5 | 1.8 | 0.6 | 0.8 | 0.2
886 | 30/07/2025 09:42:28.743 | 98.04 | 72 | 100 | 70 | 54 | 26.344 | 9.431 | 7.006 | 133.158 | 28.541 | 28.235 | 27.413 | 603.57 | 25.594 | 26.359 | 1306.751 | 27.058 | 27.32 | 38.515 | 27.001 | 3.5 | 1.4 | 0.6 | 0.8 | 0.2
887 | 30/07/2025 09:42:30.387 | 98.136 | 70 | 100 | 71 | 55 | 27.688 | 9.285 | 6.99 | 133.273 | 28.54 | 28.226 | 27.389 | 603.439 | 25.592 | 26.366 | 1305.099 | 27.078 | 27.15 | 38.706 | 27.001 | 2.9 | 1 | 0 | 0.5 | 0.2
888 | 30/07/2025 09:42:32.020 | 98.088 | 72 | 100 | 70 | 52 | 29.99 | 9.287 | 6.986 | 133.184 | 28.545 | 28.211 | 27.451 | 603.666 | 25.592 | 26.334 | 1323.596 | 27.063 | 27.139 | 38.147 | 27.001 | 2.9 | 1 | 0 | 0.5 | 0.2
889 | 30/07/2025 09:42:33.659 | 98.232 | 71 | 100 | 71 | 52 | 28.631 | 9.483 | 6.986 | 132.797 | 28.556 | 28.242 | 27.426 | 603.522 | 25.58 | 26.343 | 1332.163 | 27.084 | 27.288 | 38.353 | 22.001 | 2.9 | 1.3 | 0 | 0.5 | 0.2
890 | 30/07/2025 09:42:35.296 | 98.472 | 71 | 100 | 69 | 52 | 26.03 | 9.285 | 7.005 | 133.416 | 28.565 | 28.23 | 27.421 | 603.521 | 25.609 | 26.352 | 1330.039 | 27.03 | 27.17 | 38.487 | 27.001 | 2 | 0.6 | 0.9 | 0.5 | 0.2
891 | 30/07/2025 09:42:36.933 | 98.208 | 72 | 100 | 70 | 52 | 29.632 | 9.283 | 7.006 | 133.347 | 28.55 | 28.226 | 27.421 | 603.385 | 25.582 | 26.363 | 1327.835 | 27.084 | 27.315 | 38.477 | 30.001 | 2 | 2 | 0.9 | 0.5 | 0.2
892 | 30/07/2025 09:42:38.568 | 97.992 | 72 | 100 | 69 | 52 | 26.074 | 9.497 | 7.035 | 133.439 | 28.567 | 28.224 | 27.406 | 603.496 | 25.591 | 26.334 | 1325.131 | 27.059 | 27.311 | 38.562 | 27.001 | 3.2 | 1.6 | 0.2 | 0.5 | 0.2
893 | 30/07/2025 09:42:40.204 | 97.728 | 72 | 100 | 70 | 52 | 28.382 | 9.582 | 7.009 | 133.245 | 28.541 | 28.221 | 27.436 | 603.599 | 25.578 | 26.34 | 1307.157 | 27.065 | 27.183 | 38.199 | 27.001 | 3.2 | 1.6 | 0.2 | 0.5 | 0.2
894 | 30/07/2025 09:42:41.840 | 97.368 | 71 | 100 | 71 | 54 | 30.073 | 9.502 | 7.007 | 132.892 | 28.555 | 28.238 | 27.418 | 603.458 | 25.582 | 26.344 | 1309.813 | 27.039 | 27.273 | 38.651 | 30.001 | 3.2 | 0.9 | 0.2 | 0.5 | 0.2
895 | 30/07/2025 09:42:43.477 | 96.96 | 70 | 100 | 71 | 52 | 28.115 | 9.561 | 7.034 | 134.66 | 28.563 | 28.231 | 27.437 | 603.619 | 25.591 | 26.331 | 1307.878 | 27.05 | 27.205 | 38.452 | 26.001 | 3.1 | 1.7 | 0 | 0.1 | 0.3
896 | 30/07/2025 09:42:45.113 | 97.08 | 70 | 99 | 70 | 53 | 29.955 | 9.578 | 7.034 | 134.779 | 28.539 | 28.222 | 27.398 | 603.467 | 25.592 | 26.35 | 1310.884 | 27.071 | 27.288 | 38.492 | 30.001 | 3.1 | 1.3 | 0 | 0.1 | 0.3
897 | 30/07/2025 09:42:46.748 | 96.216 | 69 | 100 | 71 | 52 | 29.259 | 9.461 | 7.034 | 134.754 | 28.548 | 28.222 | 27.424 | 602.388 | 25.602 | 26.335 | 1310.591 | 27.068 | 27.155 | 38.233 | 25.001 | 2.7 | 2.4 | 0 | 1 | 0.2
898 | 30/07/2025 09:42:48.382 | 96.12 | 70 | 100 | 71 | 53 | 25.998 | 9.499 | 7.035 | 134.505 | 28.542 | 28.227 | 27.426 | 603.555 | 25.593 | 26.353 | 1317.708 | 27.084 | 27.141 | 38.28 | 26.001 | 2.7 | 3.3 | 0 | 1 | 0.2
899 | 30/07/2025 09:42:50.019 | 96.024 | 70 | 100 | 71 | 53 | 28.937 | 9.31 | 7.035 | 134.763 | 28.553 | 28.237 | 27.42 | 602.52 | 25.604 | 26.347 | 1333.649 | 27.029 | 27.311 | 38.657 | 26.001 | 2.7 | 3.3 | 0 | 1 | 0.2
900 | 30/07/2025 09:42:51.656 | 95.88 | 70 | 100 | 69 | 52 | 30.131 | 9.442 | 7.034 | 134.919 | 28.53 | 28.234 | 27.415 | 602.433 | 25.597 | 26.362 | 1346.925 | 27.067 | 27.31 | 38.45 | 25.001 | 1.9 | 1.4 | 0.6 | 0.2 | 0.2
901 | 30/07/2025 09:42:53.296 | 96.168 | 70 | 100 | 71 | 52 | 27.628 | 9.572 | 7.016 | 134.651 | 28.531 | 28.221 | 27.404 | 602.213 | 25.589 | 26.364 | 1338.801 | 27.073 | 27.308 | 38.574 | 30.001 | 1.9 | 1.3 | 0.6 | 0.2 | 0.2
902 | 30/07/2025 09:42:54.931 | 96.36 | 70 | 100 | 71 | 51 | 30.023 | 9.436 | 7.004 | 134.74 | 28.523 | 28.223 | 27.43 | 602.625 | 25.597 | 26.362 | 1332.933 | 27.074 | 27.323 | 38.24 | 24.001 | 1.3 | 0.6 | 0 | 0.1 | 0.3
903 | 30/07/2025 09:42:56.566 | 96.768 | 70 | 100 | 69 | 53 | 28.736 | 9.577 | 7.006 | 134.558 | 28.533 | 28.231 | 27.416 | 603.509 | 25.609 | 26.358 | 1327.281 | 27.064 | 27.284 | 38.379 | 25.001 | 1.3 | 2.6 | 0 | 0.1 | 0.3
904 | 30/07/2025 09:42:58.200 | 97.056 | 70 | 100 | 71 | 52 | 25.991 | 9.458 | 7.006 | 134.714 | 28.532 | 28.239 | 27.451 | 603.715 | 25.597 | 26.349 | 1334.394 | 27.026 | 27.306 | 38.517 | 25.001 | 1.3 | 2.6 | 0 | 0.1 | 0.3
905 | 30/07/2025 09:42:59.836 | 96.96 | 70 | 100 | 71 | 51 | 29.311 | 9.434 | 6.937 | 134.616 | 28.534 | 28.24 | 27.402 | 603.462 | 25.588 | 26.357 | 1334.852 | 27.085 | 27.314 | 38.478 | 22.001 | 2.7 | 2 | 0.6 | 0.8 | 0.3
906 | 30/07/2025 09:43:01.472 | 97.032 | 70 | 100 | 71 | 53 | 30.062 | 9.522 | 6.934 | 134.746 | 28.546 | 28.22 | 27.433 | 602.576 | 25.61 | 26.354 | 1337.555 | 27.062 | 27.302 | 38.329 | 26.001 | 2.7 | 0.9 | 0.6 | 0.8 | 0.3
907 | 30/07/2025 09:43:03.107 | 96.864 | 69 | 100 | 71 | 53 | 28.301 | 9.506 | 6.936 | 134.557 | 28.547 | 28.19 | 27.435 | 602.334 | 25.589 | 26.359 | 1339.85 | 27.073 | 27.297 | 38.202 | 28.001 | 2.9 | 0.8 | 0 | 0.3 | 0.4
908 | 30/07/2025 09:43:04.743 | 96.912 | 69 | 100 | 70 | 52 | 30.025 | 9.423 | 6.948 | 134.551 | 28.551 | 28.236 | 27.424 | 602.491 | 25.602 | 26.347 | 1339.382 | 27.052 | 27.298 | 38.711 | 26.001 | 2.9 | 0.4 | 0 | 0.3 | 0.4
909 | 30/07/2025 09:43:06.376 | 96.888 | 71 | 100 | 71 | 52 | 28.059 | 9.574 | 6.988 | 133.195 | 28.561 | 28.243 | 27.421 | 602.237 | 25.581 | 26.34 | 1327.877 | 27.057 | 27.324 | 38.32 | 25.001 | 3.8 | 0.7 | 0.6 | 0 | 0.3
910 | 30/07/2025 09:43:08.011 | 96.504 | 70 | 100 | 71 | 51 | 26.26 | 9.501 | 6.99 | 133.341 | 28.562 | 28.231 | 27.396 | 603.435 | 25.602 | 26.357 | 1320.781 | 27.077 | 27.308 | 38.386 | 25.001 | 3.8 | 0.7 | 0.6 | 0 | 0.3
911 | 30/07/2025 09:43:09.648 | 95.952 | 70 | 100 | 71 | 52 | 29.647 | 9.5 | 6.987 | 133.271 | 28.558 | 28.214 | 27.441 | 602.46 | 25.575 | 26.351 | 1324.82 | 27.065 | 27.3 | 38.197 | 22.001 | 3.8 | 1.4 | 0.6 | 0 | 0.3
912 | 30/07/2025 09:43:11.283 | 95.52 | 69 | 100 | 71 | 52 | 29.984 | 9.48 | 6.987 | 132.952 | 28.544 | 28.238 | 27.415 | 602.283 | 25.565 | 26.353 | 1320.106 | 27.086 | 27.295 | 38.409 | 25.001 | 3.2 | 1.9 | 0 | 0.2 | 0.3
913 | 30/07/2025 09:43:12.919 | 96.288 | 70 | 100 | 70 | 52 | 28.879 | 9.575 | 6.988 | 133.218 | 28.546 | 28.25 | 27.434 | 602.502 | 25.583 | 26.338 | 1318.653 | 27.046 | 27.307 | 38.333 | 23.001 | 3.2 | 0.8 | 0 | 0.2 | 0.3
914 | 30/07/2025 09:43:14.557 | 96.696 | 70 | 100 | 70 | 52 | 30.136 | 9.369 | 6.99 | 133.193 | 28.555 | 28.234 | 27.409 | 602.268 | 25.573 | 26.343 | 1322.005 | 27.069 | 27.316 | 38.572 | 21.001 | 2 | 1.5 | 0.6 | 0.1 | 0.2
915 | 30/07/2025 09:43:16.193 | 96.6 | 70 | 100 | 70 | 52 | 27.373 | 9.495 | 6.986 | 133.345 | 28.553 | 28.232 | 27.395 | 602.308 | 25.598 | 26.325 | 1329.904 | 27.073 | 27.307 | 38.603 | 21.001 | 2 | 1.5 | 0.6 | 0.1 | 0.2
916 | 30/07/2025 09:43:17.827 | 96.696 | 70 | 100 | 71 | 53 | 26.74 | 9.731 | 6.97 | 133.182 | 28.543 | 28.213 | 27.446 | 602.49 | 25.577 | 26.325 | 1327.227 | 27.071 | 27.303 | 38.227 | 24.001 | 2 | 1.1 | 0.6 | 0.1 | 0.2
917 | 30/07/2025 09:43:19.462 | 97.104 | 70 | 100 | 72 | 52 | 29.878 | 9.506 | 6.938 | 133.169 | 28.532 | 28.233 | 27.425 | 602.272 | 25.592 | 26.333 | 1324.992 | 27.051 | 27.299 | 38.54 | 27.001 | 1.4 | 1.4 | 0.9 | 0.9 | 0.3
918 | 30/07/2025 09:43:21.097 | 97.296 | 71 | 100 | 69 | 52 | 29.709 | 9.511 | 6.936 | 133.396 | 28.549 | 28.24 | 27.431 | 602.486 | 25.588 | 26.341 | 1329.653 | 27.044 | 27.318 | 38.412 | 28.001 | 1.4 | 0.9 | 0.9 | 0.9 | 0.3
919 | 30/07/2025 09:43:22.733 | 97.272 | 70 | 100 | 71 | 52 | 29.366 | 9.427 | 6.935 | 133.351 | 28.547 | 28.227 | 27.394 | 602.19 | 25.612 | 26.362 | 1330.126 | 27.064 | 27.307 | 38.551 | 25.001 | 2.5 | 1 | 0.6 | 1.1 | 0.3
920 | 30/07/2025 09:43:24.374 | 96.888 | 71 | 100 | 68 | 52 | 30.102 | 9.427 | 6.935 | 133.245 | 28.532 | 28.223 | 27.422 | 602.24 | 25.609 | 26.345 | 1330.148 | 27.067 | 27.309 | 38.332 | 26.001 | 2.5 | 1.2 | 0.6 | 1.1 | 0.3
921 | 30/07/2025 09:43:26.010 | 96.552 | 70 | 100 | 71 | 52 | 27.008 | 9.451 | 6.934 | 133.121 | 28.532 | 28.224 | 27.435 | 602.24 | 25.595 | 26.374 | 1329.54 | 27.09 | 27.292 | 38.25 | 26.001 | 2.5 | 1.2 | 0.6 | 1.1 | 0.3
922 | 30/07/2025 09:43:27.647 | 96.84 | 69 | 100 | 70 | 52 | 27.285 | 9.262 | 6.935 | 132.995 | 28.543 | 28.239 | 27.434 | 602.387 | 25.614 | 26.358 | 1325.191 | 27.04 | 27.311 | 38.729 | 25.001 | 3.6 | 1.8 | 0.6 | 0.1 | 0.4
923 | 30/07/2025 09:43:29.283 | 96.792 | 70 | 100 | 71 | 51 | 29.982 | 9.576 | 6.851 | 133.258 | 28.518 | 28.25 | 27.415 | 602.334 | 25.593 | 26.353 | 1312.297 | 27.068 | 27.32 | 38.398 | 31.001 | 3.6 | 2.3 | 0.6 | 0.1 | 0.4
924 | 30/07/2025 09:43:30.915 | 96.816 | 71 | 100 | 71 | 52 | 26.291 | 9.554 | 6.848 | 133.454 | 28.531 | 28.236 | 27.403 | 602.39 | 25.602 | 26.348 | 1307.719 | 27.079 | 27.309 | 38.554 | 24.001 | 1.6 | 2.2 | 0 | 0 | 0.3
925 | 30/07/2025 09:43:32.548 | 96.96 | 71 | 100 | 70 | 52 | 29.667 | 9.447 | 6.865 | 133.247 | 28.659 | 28.216 | 27.414 | 602.412 | 25.591 | 26.363 | 1295.462 | 27.076 | 27.313 | 38.35 | 20.001 | 1.6 | 1.4 | 0 | 0 | 0.3
926 | 30/07/2025 09:43:34.181 | 97.104 | 71 | 100 | 70 | 52 | 29.992 | 9.447 | 6.865 | 133.163 | 28.669 | 28.226 | 27.423 | 602.316 | 25.596 | 26.358 | 1299.697 | 27.046 | 27.286 | 38.323 | 20.001 | 1.6 | 1.4 | 0 | 0 | 0.3
927 | 30/07/2025 09:43:35.815 | 97.056 | 70 | 100 | 70 | 52 | 26.505 | 9.446 | 6.901 | 133.196 | 28.669 | 28.241 | 27.431 | 602.371 | 25.596 | 26.352 | 1297.738 | 27.039 | 27.315 | 38.658 | 25.001 | 2.6 | 1.5 | 0.9 | 0.8 | 0.3
928 | 30/07/2025 09:43:37.449 | 97.056 | 71 | 100 | 72 | 52 | 27.685 | 9.576 | 6.902 | 133.305 | 28.556 | 28.235 | 27.419 | 602.198 | 25.595 | 26.369 | 1284.512 | 27.082 | 27.311 | 38.441 | 24.001 | 2.6 | 0.8 | 0.9 | 0.8 | 0.3
929 | 30/07/2025 09:43:39.084 | 97.176 | 70 | 100 | 71 | 52 | 27.598 | 9.578 | 6.9 | 133.097 | 28.684 | 28.23 | 27.384 | 600.767 | 25.593 | 26.348 | 1284.191 | 27.08 | 27.312 | 38.482 | 26.001 | 1.8 | 1.2 | 0.6 | 0 | 0.3
930 | 30/07/2025 09:43:40.720 | 96.864 | 70 | 100 | 70 | 51 | 26.675 | 9.494 | 6.867 | 133.064 | 28.698 | 28.222 | 27.421 | 600.947 | 25.586 | 26.369 | 1289.476 | 27.073 | 27.296 | 38.252 | 26.001 | 1.8 | 1.5 | 0.6 | 0 | 0.3
931 | 30/07/2025 09:43:42.355 | 97.512 | 71 | 100 | 70 | 52 | 29.873 | 9.601 | 6.865 | 133.105 | 28.697 | 28.239 | 27.427 | 601.049 | 25.592 | 26.338 | 1292.76 | 27.054 | 27.295 | 38.449 | 28.001 | 5 | 1.7 | 0.8 | 0.5 | 0.3
932 | 30/07/2025 09:43:43.987 | 96.984 | 71 | 100 | 71 | 52 | 29.728 | 9.578 | 6.901 | 133.124 | 28.701 | 28.256 | 27.417 | 600.876 | 25.576 | 26.348 | 1282.98 | 27.05 | 27.324 | 38.551 | 28.001 | 5 | 1.7 | 0.8 | 0.5 | 0.3
933 | 30/07/2025 09:43:45.620 | 97.248 | 70 | 100 | 70 | 52 | 26.058 | 9.476 | 6.933 | 133.247 | 28.695 | 28.226 | 27.391 | 600.758 | 25.599 | 26.345 | 1289.356 | 27.078 | 27.309 | 38.408 | 27.001 | 5 | 1 | 0.8 | 0.5 | 0.3
934 | 30/07/2025 09:43:47.252 | 96.744 | 70 | 100 | 70 | 51 | 28.305 | 9.503 | 6.935 | 133.267 | 28.684 | 28.215 | 27.425 | 600.875 | 25.577 | 26.336 | 1293.109 | 27.069 | 27.3 | 38.254 | 28.001 | 1.6 | 3.6 | 0 | 0.1 | 0.2
935 | 30/07/2025 09:43:48.888 | 97.224 | 70 | 100 | 71 | 52 | 26.837 | 9.577 | 6.934 | 133.31 | 28.696 | 28.217 | 27.432 | 600.928 | 25.587 | 26.336 | 1290.167 | 27.061 | 27.279 | 38.295 | 23.001 | 1.6 | 2 | 0 | 0.1 | 0.2
936 | 30/07/2025 09:43:50.524 | 97.248 | 70 | 100 | 71 | 52 | 27.186 | 9.435 | 6.935 | 133.029 | 28.683 | 28.255 | 27.424 | 600.946 | 25.561 | 26.33 | 1301.289 | 27.045 | 27.315 | 38.597 | 26.001 | 5.1 | 0.8 | 0 | 0.3 | 0.2
937 | 30/07/2025 09:43:52.162 | 97.128 | 71 | 100 | 69 | 52 | 29.971 | 9.751 | 6.903 | 133.169 | 28.692 | 28.233 | 27.419 | 600.772 | 25.585 | 26.335 | 1289.936 | 27.06 | 27.298 | 38.472 | 26.001 | 5.1 | 0.8 | 0 | 0.3 | 0.2
938 | 30/07/2025 09:43:53.797 | 96.888 | 71 | 100 | 70 | 51 | 29.307 | 9.315 | 6.934 | 133.272 | 28.701 | 28.231 | 27.41 | 600.866 | 25.6 | 26.328 | 1280.452 | 27.074 | 27.303 | 38.476 | 24.001 | 5.1 | 0.7 | 0 | 0.3 | 0.2
939 | 30/07/2025 09:43:55.431 | 97.272 | 72 | 100 | 71 | 52 | 25.905 | 9.286 | 6.934 | 133.139 | 28.685 | 28.222 | 27.423 | 600.942 | 25.598 | 26.345 | 1272.415 | 27.073 | 27.298 | 38.186 | 24.001 | 3.1 | 2 | 0 | 0.5 | 0.2
940 | 30/07/2025 09:43:57.066 | 97.392 | 71 | 100 | 70 | 52 | 30.075 | 9.285 | 6.934 | 133.208 | 28.68 | 28.227 | 27.442 | 600.949 | 25.592 | 26.353 | 1270.109 | 27.069 | 27.279 | 38.195 | 26.001 | 3.1 | 2.1 | 0 | 0.5 | 0.2
941 | 30/07/2025 09:43:58.699 | 97.152 | 71 | 100 | 70 | 52 | 26.525 | 9.503 | 6.936 | 133.04 | 28.691 | 28.253 | 27.421 | 600.847 | 25.602 | 26.37 | 1260.254 | 27.053 | 27.334 | 38.55 | 23.001 | 5 | 1.3 | 0 | 0.5 | 0.3
942 | 30/07/2025 09:44:00.334 | 96.672 | 71 | 100 | 70 | 51 | 27.904 | 9.779 | 7.005 | 133.475 | 28.687 | 28.237 | 27.405 | 600.791 | 25.597 | 26.35 | 1265.372 | 27.065 | 27.307 | 38.556 | 26.001 | 5 | 1.8 | 0 | 0.5 | 0.3
943 | 30/07/2025 09:44:01.969 | 96.648 | 71 | 100 | 70 | 51 | 30.036 | 9.504 | 7.006 | 133.287 | 28.661 | 28.225 | 27.421 | 600.801 | 25.587 | 26.357 | 1267.449 | 27.07 | 27.309 | 38.195 | 26.001 | 5 | 1.8 | 0 | 0.5 | 0.3
944 | 30/07/2025 09:44:03.603 | 96.744 | 70 | 100 | 70 | 51 | 28.806 | 9.433 | 7.005 | 133.116 | 28.668 | 28.212 | 27.432 | 600.771 | 25.585 | 26.383 | 1272.426 | 27.076 | 27.291 | 38.298 | 35.001 | 3.5 | 1.6 | 0.6 | 0.8 | 0.4
945 | 30/07/2025 09:44:05.237 | 96.48 | 69 | 100 | 70 | 52 | 26.083 | 9.282 | 6.988 | 133.253 | 28.674 | 28.239 | 27.44 | 602.457 | 25.607 | 26.35 | 1285.041 | 27.04 | 27.316 | 38.651 | 32.001 | 3.5 | 1.5 | 0.6 | 0.8 | 0.4
946 | 30/07/2025 09:44:06.872 | 96.264 | 70 | 100 | 70 | 52 | 29.781 | 9.522 | 6.988 | 133.219 | 28.671 | 28.234 | 27.416 | 602.152 | 25.601 | 26.36 | 1287.641 | 27.029 | 27.311 | 38.586 | 28.001 | 2.2 | 1.7 | 0.6 | 1 | 0.3
947 | 30/07/2025 09:44:08.509 | 96.528 | 71 | 100 | 70 | 51 | 26.219 | 9.579 | 6.987 | 133.344 | 28.674 | 28.239 | 27.401 | 602.262 | 25.607 | 26.346 | 1288.213 | 27.069 | 27.314 | 38.541 | 30.001 | 2.2 | 2.2 | 0.6 | 1 | 0.3
948 | 30/07/2025 09:44:10.142 | 96.528 | 70 | 100 | 70 | 52 | 28.452 | 9.493 | 6.987 | 133.06 | 28.692 | 28.212 | 27.424 | 602.313 | 25.6 | 26.351 | 1290.187 | 27.092 | 27.309 | 38.43 | 30.001 | 2.2 | 2.2 | 0.6 | 1 | 0.3
949 | 30/07/2025 09:44:11.777 | 96.72 | 71 | 100 | 70 | 52 | 30.111 | 9.615 | 6.985 | 133.283 | 28.712 | 28.232 | 27.428 | 602.396 | 25.611 | 26.361 | 1297.503 | 27.071 | 27.286 | 38.291 | 27.001 | 3.2 | 1.2 | 0 | 1.1 | 0.2
950 | 30/07/2025 09:44:13.415 | 96.648 | 70 | 100 | 70 | 53 | 28.288 | 9.458 | 6.988 | 133.231 | 28.692 | 28.242 | 27.434 | 602.424 | 25.583 | 26.344 | 1300.107 | 27.042 | 27.321 | 38.557 | 24.001 | 3.2 | 1.9 | 0 | 1.1 | 0.2
951 | 30/07/2025 09:44:15.049 | 96.696 | 71 | 100 | 71 | 52 | 29.965 | 9.728 | 6.987 | 133.471 | 28.718 | 28.238 | 27.419 | 602.229 | 25.604 | 26.349 | 1298.485 | 27.046 | 27.314 | 38.515 | 30.001 | 3.6 | 1.4 | 0.1 | 0.7 | 0.2
952 | 30/07/2025 09:44:16.683 | 96.432 | 70 | 100 | 70 | 52 | 29.372 | 9.579 | 6.935 | 133.134 | 28.693 | 28.235 | 27.403 | 602.297 | 25.576 | 26.345 | 1311.543 | 27.08 | 27.318 | 38.634 | 23.001 | 3.6 | 0 | 0.1 | 0.7 | 0.2
953 | 30/07/2025 09:44:18.320 | 96.864 | 71 | 100 | 71 | 52 | 25.987 | 9.442 | 6.935 | 133.151 | 28.695 | 28.2 | 27.42 | 602.425 | 25.586 | 26.356 | 1316.076 | 27.074 | 27.294 | 38.338 | 26.001 | 2.3 | 1.2 | 0.6 | 0.5 | 0.2
954 | 30/07/2025 09:44:19.958 | 96.72 | 72 | 100 | 71 | 52 | 28.843 | 9.469 | 6.935 | 133.249 | 28.689 | 28.243 | 27.433 | 602.49 | 25.59 | 26.33 | 1317.792 | 27.054 | 27.291 | 38.476 | 26.001 | 2.3 | 1.2 | 0.6 | 0.5 | 0.2
955 | 30/07/2025 09:44:21.593 | 96.888 | 71 | 100 | 71 | 53 | 30.172 | 9.497 | 6.936 | 133.179 | 28.69 | 28.234 | 27.412 | 602.246 | 25.572 | 26.338 | 1327.003 | 27.051 | 27.326 | 38.628 | 29.001 | 2.3 | 1.1 | 0.6 | 0.5 | 0.2
956 | 30/07/2025 09:44:23.231 | 96.504 | 71 | 100 | 70 | 53 | 27.696 | 9.431 | 6.935 | 133.909 | 28.684 | 28.238 | 27.417 | 602.392 | 25.578 | 26.333 | 1337.358 | 27.063 | 27.304 | 38.583 | 31.001 | 1.6 | 0.7 | 0 | 0.5 | 0.2
957 | 30/07/2025 09:44:24.865 | 96.768 | 71 | 100 | 70 | 53 | 30.044 | 9.292 | 6.936 | 134.622 | 28.684 | 28.227 | 27.391 | 602.021 | 25.58 | 26.335 | 1327.729 | 27.099 | 27.31 | 38.525 | 28.001 | 1.6 | 1.2 | 0 | 0.5 | 0.2
958 | 30/07/2025 09:44:26.501 | 96.288 | 71 | 100 | 70 | 53 | 28.628 | 9.29 | 6.933 | 134.68 | 28.702 | 28.215 | 27.447 | 602.455 | 25.619 | 26.332 | 1325.215 | 27.068 | 27.288 | 38.395 | 27.001 | 2.2 | 0.7 | 0.6 | 0 | 0.2
959 | 30/07/2025 09:44:28.138 | 96.984 | 71 | 100 | 70 | 52 | 26.05 | 9.732 | 6.934 | 134.626 | 28.678 | 28.255 | 27.436 | 602.343 | 25.595 | 26.334 | 1322.639 | 27.063 | 27.315 | 38.524 | 27.001 | 2.2 | 0.7 | 0.6 | 0 | 0.2
960 | 30/07/2025 09:44:29.772 | 97.176 | 72 | 100 | 70 | 52 | 29.308 | 9.576 | 6.903 | 134.692 | 28.685 | 28.236 | 27.417 | 601.3 | 25.61 | 26.358 | 1327.848 | 27.051 | 27.307 | 38.699 | 25.001 | 2.2 | 0.9 | 0.6 | 0 | 0.2
961 | 30/07/2025 09:44:31.408 | 97.44 | 72 | 100 | 70 | 53 | 30.16 | 9.575 | 6.9 | 133.227 | 28.689 | 28.233 | 27.396 | 601.087 | 25.605 | 26.339 | 1342.607 | 27.081 | 27.303 | 38.429 | 24.001 | 2.2 | 1 | 0 | 0.1 | 0.1
962 | 30/07/2025 09:44:33.043 | 97.224 | 70 | 100 | 70 | 54 | 28.358 | 9.577 | 6.901 | 133.251 | 28.675 | 28.21 | 27.413 | 602.015 | 25.605 | 26.359 | 1331.745 | 27.076 | 27.304 | 38.407 | 27.001 | 2.2 | 0.8 | 0 | 0.1 | 0.1
963 | 30/07/2025 09:44:34.678 | 97.416 | 71 | 100 | 71 | 53 | 30.048 | 9.525 | 6.913 | 133.292 | 28.676 | 28.226 | 27.44 | 602.424 | 25.596 | 26.363 | 1317.473 | 27.062 | 27.286 | 38.096 | 28.001 | 2.4 | 0.8 | 0.9 | 0.2 | 0.1
964 | 30/07/2025 09:44:36.313 | 96.984 | 72 | 100 | 70 | 52 | 28.137 | 9.442 | 6.937 | 132.895 | 28.653 | 28.235 | 27.405 | 602.175 | 25.593 | 26.366 | 1317.424 | 27.059 | 27.319 | 38.432 | 28.001 | 2.4 | 1 | 0.9 | 0.2 | 0.1
965 | 30/07/2025 09:44:37.948 | 97.2 | 72 | 100 | 71 | 53 | 26.4 | 9.577 | 6.935 | 133.563 | 28.678 | 28.238 | 27.411 | 602.207 | 25.605 | 26.353 | 1327.435 | 27.051 | 27.307 | 38.521 | 28.001 | 2.4 | 1 | 0.9 | 0.2 | 0.1
966 | 30/07/2025 09:44:39.583 | 96.936 | 71 | 100 | 71 | 52 | 29.757 | 9.56 | 6.935 | 133.189 | 28.671 | 28.227 | 27.405 | 602.304 | 25.586 | 26.352 | 1329.903 | 27.08 | 27.306 | 38.382 | 27.001 | 3.3 | 1.8 | 0.2 | 0.6 | 0.2
967 | 30/07/2025 09:44:41.222 | 97.512 | 72 | 100 | 70 | 53 | 26.003 | 9.355 | 6.934 | 133.252 | 28.691 | 28.219 | 27.433 | 602.342 | 25.6 | 26.337 | 1337.023 | 27.063 | 27.289 | 38.383 | 24.001 | 3.3 | 1.4 | 0.2 | 0.6 | 0.2
968 | 30/07/2025 09:44:42.858 | 97.872 | 74 | 100 | 70 | 53 | 28.923 | 9.497 | 6.934 | 133.047 | 28.668 | 28.244 | 27.432 | 602.245 | 25.592 | 26.35 | 1334.519 | 27.077 | 27.292 | 38.271 | 26.001 | 3 | 1.9 | 0.6 | 0.2 | 0.2
969 | 30/07/2025 09:44:44.493 | 98.688 | 74 | 100 | 70 | 53 | 30.148 | 9.497 | 6.936 | 133.415 | 28.696 | 28.234 | 27.42 | 600.864 | 25.597 | 26.366 | 1338.198 | 27.033 | 27.309 | 38.494 | 34.001 | 3 | 1.6 | 0.6 | 0.2 | 0.2
970 | 30/07/2025 09:44:46.130 | 98.304 | 73 | 100 | 70 | 53 | 27.741 | 9.578 | 6.935 | 133.264 | 28.688 | 28.241 | 27.418 | 600.85 | 25.585 | 26.346 | 1326.23 | 27.064 | 27.308 | 38.128 | 34.001 | 3 | 1.6 | 0.6 | 0.2 | 0.2
971 | 30/07/2025 09:44:47.768 | 99 | 74 | 100 | 70 | 52 | 26.742 | 9.578 | 6.953 | 133.104 | 28.691 | 28.211 | 27.408 | 600.753 | 25.588 | 26.358 | 1320.213 | 27.077 | 27.306 | 38.484 | 28.001 | 3.2 | 1.4 | 0.6 | 0 | 0.3
972 | 30/07/2025 09:44:49.405 | 98.52 | 74 | 100 | 70 | 52 | 29.911 | 9.431 | 6.984 | 133.211 | 28.706 | 28.231 | 27.427 | 600.964 | 25.608 | 26.357 | 1312.207 | 27.065 | 27.293 | 38.158 | 30.001 | 3.2 | 0.3 | 0.6 | 0 | 0.3
973 | 30/07/2025 09:44:51.041 | 98.208 | 73 | 100 | 71 | 53 | 26.065 | 9.575 | 6.989 | 132.81 | 28.686 | 28.23 | 27.421 | 600.776 | 25.576 | 26.363 | 1309.551 | 27.059 | 27.3 | 38.435 | 29.001 | 3.3 | 0.9 | 0.7 | 0 | 0.2
974 | 30/07/2025 09:44:52.677 | 98.4 | 74 | 100 | 71 | 53 | 29.425 | 9.614 | 6.986 | 133.384 | 28.713 | 28.237 | 27.422 | 600.923 | 25.604 | 26.348 | 1310.103 | 27.038 | 27.312 | 38.531 | 24.001 | 3.3 | 1.6 | 0.7 | 0 | 0.2
975 | 30/07/2025 09:44:54.312 | 98.544 | 74 | 100 | 70 | 53 | 30.245 | 9.579 | 6.935 | 133.02 | 28.687 | 28.251 | 27.401 | 600.69 | 25.576 | 26.33 | 1298.011 | 27.088 | 27.309 | 38.578 | 31.001 | 2.5 | 1.1 | 0.6 | 0.5 | 0.2
976 | 30/07/2025 09:44:55.948 | 99.048 | 75 | 100 | 70 | 52 | 26.98 | 9.536 | 6.935 | 134.609 | 28.685 | 28.214 | 27.415 | 599.516 | 25.568 | 26.333 | 1297.556 | 27.064 | 27.292 | 38.291 | 31.001 | 2.5 | 1.1 | 0.6 | 0.5 | 0.2
977 | 30/07/2025 09:44:57.586 | 98.904 | 74 | 100 | 70 | 53 | 27.137 | 9.679 | 6.933 | 134.612 | 28.687 | 28.235 | 27.425 | 599.667 | 25.584 | 26.32 | 1304.834 | 27.065 | 27.292 | 38.251 | 31.001 | 2.5 | 2.2 | 0.6 | 0.5 | 0.2
978 | 30/07/2025 09:44:59.224 | 99.264 | 74 | 100 | 71 | 53 | 29.978 | 9.579 | 6.936 | 134.545 | 28.671 | 28.243 | 27.411 | 600.804 | 25.58 | 26.336 | 1292.586 | 27.066 | 27.323 | 38.499 | 26.001 | 4 | 2.3 | 0 | 0.5 | 0.1
979 | 30/07/2025 09:45:00.863 | 98.832 | 77 | 100 | 70 | 52 | 26.323 | 9.735 | 6.936 | 134.815 | 28.689 | 28.238 | 27.416 | 600.699 | 25.585 | 26.331 | 1297.428 | 27.049 | 27.319 | 38.492 | 31.001 | 4 | 1.4 | 0 | 0.5 | 0.1
980 | 30/07/2025 09:45:02.503 | 97.992 | 74 | 100 | 70 | 53 | 29.672 | 9.709 | 6.902 | 134.717 | 28.686 | 28.223 | 27.393 | 600.489 | 25.588 | 26.357 | 1289.414 | 27.085 | 27.305 | 38.538 | 25.001 | 2.8 | 2.1 | 1.2 | 1.2 | 0.1
981 | 30/07/2025 09:45:04.136 | 98.088 | 74 | 100 | 70 | 53 | 30.057 | 9.514 | 6.884 | 134.617 | 28.704 | 28.217 | 27.437 | 600.827 | 25.627 | 26.349 | 1285.393 | 27.064 | 27.299 | 38.28 | 25.001 | 2.8 | 2.1 | 1.2 | 1.2 | 0.1
982 | 30/07/2025 09:45:05.860 | 97.824 | 73 | 100 | 70 | 53 | 26.528 | 9.442 | 6.865 | 134.463 | 28.67 | 28.255 | 27.43 | 600.825 | 25.596 | 26.357 | 1301.385 | 27.06 | 27.32 | 38.379 | 25.001 | 2.8 | 2.3 | 1.2 | 1.2 | 0.1
983 | 30/07/2025 09:45:07.494 | 97.896 | 74 | 100 | 68 | 53 | 27.824 | 9.575 | 6.901 | 134.681 | 28.671 | 28.235 | 27.418 | 600.807 | 25.591 | 26.366 | 1317.747 | 27.051 | 27.303 | 38.467 | 21.001 | 3.5 | 1.1 | 0.6 | 0.5 | 0.1
984 | 30/07/2025 09:45:09.131 | 97.584 | 74 | 100 | 71 | 53 | 30.035 | 9.715 | 6.898 | 134.645 | 28.682 | 28.239 | 27.402 | 600.713 | 25.591 | 26.362 | 1324.493 | 27.069 | 27.308 | 38.424 | 26.001 | 3.5 | 1.2 | 0.6 | 0.5 | 0.1
985 | 30/07/2025 09:45:10.771 | 97.824 | 73 | 100 | 71 | 52 | 27.048 | 9.584 | 6.933 | 134.754 | 28.675 | 28.226 | 27.398 | 600.766 | 25.599 | 26.373 | 1324.457 | 27.066 | 27.302 | 38.384 | 28.001 | 3 | 2.6 | 0 | 0 | 0.1
986 | 30/07/2025 09:45:12.411 | 97.896 | 73 | 100 | 71 | 52 | 29.902 | 9.588 | 6.937 | 134.646 | 28.657 | 28.225 | 27.43 | 599.91 | 25.589 | 26.355 | 1307.32 | 27.071 | 27.285 | 38.161 | 26.001 | 3 | 0.9 | 0 | 0 | 0.1
987 | 30/07/2025 09:45:14.047 | 97.512 | 73 | 100 | 70 | 52 | 29.735 | 9.537 | 7.007 | 134.409 | 28.659 | 28.235 | 27.42 | 599.463 | 25.605 | 26.362 | 1319.739 | 27.051 | 27.317 | 38.693 | 26.001 | 3 | 0.9 | 0 | 0 | 0.1
988 | 30/07/2025 09:45:15.683 | 97.68 | 73 | 100 | 72 | 52 | 26.132 | 9.544 | 7.006 | 134.88 | 28.679 | 28.232 | 27.428 | 600.959 | 25.609 | 26.352 | 1323.628 | 27.052 | 27.314 | 38.483 | 22.001 | 2.9 | 0.7 | 0.7 | 0 | 0.1
989 | 30/07/2025 09:45:17.319 | 98.208 | 74 | 100 | 69 | 52 | 28.364 | 9.726 | 7.006 | 134.663 | 28.674 | 28.221 | 27.412 | 600.665 | 25.591 | 26.36 | 1320.078 | 27.084 | 27.329 | 38.521 | 24.001 | 2.9 | 1.9 | 0.7 | 0 | 0.1
990 | 30/07/2025 09:45:18.962 | 98.136 | 75 | 100 | 70 | 52 | 27.073 | 9.729 | 6.986 | 134.655 | 28.681 | 28.221 | 27.436 | 600.828 | 25.598 | 26.356 | 1317.527 | 27.064 | 27.305 | 38.298 | 28.001 | 1.5 | 1.6 | 0 | 0.6 | 0.1
991 | 30/07/2025 09:45:20.597 | 98.304 | 74 | 100 | 70 | 52 | 27.306 | 9.509 | 6.987 | 134.271 | 28.698 | 28.239 | 27.416 | 600.826 | 25.587 | 26.356 | 1311.862 | 27.089 | 27.298 | 38.324 | 25.001 | 1.5 | 2.2 | 0 | 0.6 | 0.1
992 | 30/07/2025 09:45:22.236 | 98.064 | 74 | 100 | 71 | 53 | 29.958 | 9.639 | 7.006 | 134.795 | 28.702 | 28.231 | 27.418 | 600.833 | 25.599 | 26.353 | 1317.826 | 27.04 | 27.311 | 38.582 | 25.001 | 1.5 | 2.2 | 0 | 0.6 | 0.1
993 | 30/07/2025 09:45:23.873 | 98.376 | 73 | 100 | 70 | 54 | 29.437 | 9.578 | 7.03 | 134.726 | 28.693 | 28.247 | 27.403 | 600.778 | 25.58 | 26.352 | 1312.738 | 27.072 | 27.318 | 38.414 | 27.001 | 2.3 | 1.5 | 0.9 | 1.5 | 0.1
994 | 30/07/2025 09:45:25.511 | 98.616 | 74 | 100 | 71 | 54 | 26.131 | 9.436 | 7.029 | 134.45 | 28.691 | 28.213 | 27.412 | 600.804 | 25.577 | 26.352 | 1303.176 | 27.08 | 27.312 | 38.311 | 28.001 | 2.3 | 0.8 | 0.9 | 1.5 | 0.1
995 | 30/07/2025 09:45:27.146 | 99.432 | 74 | 100 | 71 | 53 | 28.935 | 9.29 | 7.003 | 134.668 | 28.708 | 28.225 | 27.428 | 601.101 | 25.58 | 26.337 | 1303.618 | 27.064 | 27.285 | 38.347 | 25.001 | 1.6 | 1.1 | 1 | 1.2 | 0.1
996 | 30/07/2025 09:45:28.783 | 99.456 | 72 | 100 | 71 | 53 | 26.558 | 9.284 | 7.006 | 134.269 | 28.688 | 28.235 | 27.421 | 600.804 | 25.574 | 26.344 | 1308.227 | 27.054 | 27.295 | 38.484 | 32.001 | 1.6 | 1.2 | 1 | 1.2 | 0.1
997 | 30/07/2025 09:45:30.418 | 99.048 | 73 | 99 | 71 | 52 | 27.764 | 9.569 | 6.936 | 134.79 | 28.691 | 28.241 | 27.432 | 600.881 | 25.585 | 26.317 | 1315.497 | 27.033 | 27.311 | 38.522 | 30.001 | 1.4 | 1.4 | 0.1 | 0 | 0.2
998 | 30/07/2025 09:45:32.053 | 98.304 | 74 | 100 | 70 | 53 | 30.03 | 9.484 | 6.936 | 134.738 | 28.681 | 28.252 | 27.396 | 600.672 | 25.583 | 26.335 | 1307.535 | 27.096 | 27.329 | 38.588 | 30.001 | 1.4 | 1.4 | 0.1 | 0 | 0.2
999 | 30/07/2025 09:45:33.688 | 97.944 | 71 | 100 | 70 | 51 | 28.788 | 9.58 | 6.935 | 134.72 | 28.693 | 28.215 | 27.424 | 600.799 | 25.591 | 26.345 | 1292.971 | 27.08 | 27.306 | 38.376 | 31.001 | 1.4 | 1.3 | 0.1 | 0 | 0.2
1000 | 30/07/2025 09:45:35.322 | 97.872 | 72 | 100 | 70 | 53 | 26.046 | 9.356 | 6.933 | 134.555 | 28.696 | 28.24 | 27.421 | 600.893 | 25.59 | 26.338 | 1287.877 | 27.061 | 27.293 | 38.385 | 26.001 | 2 | 1.4 | 1.2 | 0.5 | 0.3
1001 | 30/07/2025 09:45:36.958 | 98.232 | 72 | 100 | 71 | 53 | 29.798 | 9.281 | 6.936 | 134.479 | 28.695 | 28.239 | 27.421 | 600.894 | 25.607 | 26.341 | 1290.488 | 27.044 | 27.293 | 38.815 | 23.001 | 2 | 1.1 | 1.2 | 0.5 | 0.3
1002 | 30/07/2025 09:45:38.593 | 98.472 | 72 | 100 | 71 | 52 | 26.229 | 9.283 | 6.935 | 134.933 | 28.676 | 28.243 | 27.417 | 600.799 | 25.592 | 26.357 | 1296.672 | 27.057 | 27.323 | 38.493 | 24.001 | 3.2 | 1.9 | 0 | 0 | 0.3
1003 | 30/07/2025 09:45:40.227 | 97.968 | 73 | 100 | 70 | 53 | 28.327 | 9.437 | 6.853 | 134.737 | 28.677 | 28.226 | 27.394 | 600.695 | 25.605 | 26.369 | 1300.15 | 27.08 | 27.31 | 38.444 | 24.001 | 3.2 | 1.9 | 0 | 0 | 0.3
1004 | 30/07/2025 09:45:41.863 | 98.376 | 72 | 100 | 70 | 53 | 30.166 | 9.43 | 6.847 | 134.831 | 28.665 | 28.217 | 27.443 | 601.014 | 25.605 | 26.354 | 1310.944 | 27.066 | 27.286 | 38.217 | 26.001 | 3.2 | 1.9 | 0 | 0 | 0.3
1005 | 30/07/2025 09:45:43.501 | 98.736 | 72 | 100 | 70 | 52 | 28.171 | 9.286 | 6.865 | 134.42 | 28.665 | 28.243 | 27.412 | 600.799 | 25.592 | 26.364 | 1317.325 | 27.073 | 27.309 | 38.604 | 28.001 | 2.6 | 2.8 | 0.6 | 0 | 0.3
1006 | 30/07/2025 09:45:45.139 | 98.616 | 71 | 100 | 70 | 53 | 26.278 | 9.328 | 6.889 | 134.852 | 28.666 | 28.23 | 27.414 | 600.809 | 25.599 | 26.362 | 1319.64 | 27.022 | 27.314 | 38.462 | 27.001 | 2.6 | 0.8 | 0.6 | 0 | 0.3
1007 | 30/07/2025 09:45:46.776 | 99.048 | 73 | 100 | 72 | 52 | 29.272 | 9.429 | 6.902 | 134.648 | 28.65 | 28.238 | 27.397 | 600.706 | 25.586 | 26.353 | 1323.792 | 27.08 | 27.319 | 38.56 | 29.001 | 3.1 | 1.7 | 0 | 0.7 | 0.2
1008 | 30/07/2025 09:45:48.413 | 99 | 73 | 100 | 70 | 53 | 25.94 | 9.575 | 6.901 | 134.899 | 28.677 | 28.223 | 27.401 | 600.724 | 25.613 | 26.36 | 1330.404 | 27.068 | 27.313 | 38.484 | 26.001 | 3.1 | 2 | 0 | 0.7 | 0.2
1009 | 30/07/2025 09:45:50.053 | 98.976 | 71 | 100 | 70 | 52 | 28.819 | 9.607 | 6.897 | 134.724 | 28.682 | 28.217 | 27.419 | 600.832 | 25.585 | 26.354 | 1328.65 | 27.072 | 27.301 | 38.289 | 26.001 | 3.1 | 2 | 0 | 0.7 | 0.2
1010 | 30/07/2025 09:45:51.692 | 99.168 | 74 | 100 | 70 | 52 | 30.181 | 9.578 | 6.937 | 134.468 | 28.676 | 28.236 | 27.415 | 602.266 | 25.593 | 26.364 | 1327.284 | 27.048 | 27.314 | 38.439 | 28.001 | 2.6 | 1.1 | 0.6 | 0.5 | 0.3
1011 | 30/07/2025 09:45:53.328 | 99.096 | 73 | 100 | 70 | 52 | 27.641 | 9.473 | 6.936 | 134.759 | 28.689 | 28.236 | 27.423 | 602.353 | 25.614 | 26.351 | 1322.83 | 27.054 | 27.315 | 38.44 | 26.001 | 2.6 | 2.5 | 0.6 | 0.5 | 0.3
1012 | 30/07/2025 09:45:54.963 | 98.256 | 73 | 100 | 70 | 52 | 30.002 | 9.428 | 6.936 | 134.746 | 28.683 | 28.233 | 27.397 | 602.103 | 25.586 | 26.352 | 1322.634 | 27.071 | 27.303 | 38.717 | 25.001 | 4.2 | 1.8 | 0.1 | 2 | 0.2
1013 | 30/07/2025 09:45:56.609 | 97.992 | 72 | 100 | 70 | 54 | 28.906 | 9.296 | 6.934 | 134.729 | 28.709 | 28.213 | 27.425 | 602.41 | 25.584 | 26.352 | 1325.112 | 27.06 | 27.307 | 38.316 | 27.001 | 4.2 | 1.9 | 0.1 | 2 | 0.2
1014 | 30/07/2025 09:45:58.244 | 98.352 | 73 | 100 | 71 | 52 | 26.126 | 9.435 | 6.936 | 134.384 | 28.69 | 28.222 | 27.413 | 602.25 | 25.584 | 26.341 | 1319.889 | 27.086 | 27.3 | 38.331 | 27.001 | 4.2 | 1.9 | 0.1 | 2 | 0.2
1015 | 30/07/2025 09:45:59.879 | 98.136 | 72 | 100 | 71 | 53 | 29.418 | 9.574 | 6.937 | 134.708 | 28.705 | 28.24 | 27.416 | 602.312 | 25.597 | 26.349 | 1320.167 | 27.032 | 27.317 | 38.564 | 31.001 | 2.5 | 1.1 | 0.6 | 0.5 | 0.3
1016 | 30/07/2025 09:46:01.517 | 98.544 | 72 | 100 | 70 | 53 | 30.206 | 9.59 | 6.935 | 134.789 | 28.673 | 28.238 | 27.405 | 602.146 | 25.581 | 26.337 | 1317.727 | 27.052 | 27.308 | 38.505 | 24.001 | 2.5 | 1 | 0.6 | 0.5 | 0.3
1017 | 30/07/2025 09:46:03.150 | 98.664 | 73 | 100 | 70 | 53 | 28.425 | 9.575 | 6.934 | 134.823 | 28.693 | 28.233 | 27.397 | 602.269 | 25.597 | 26.326 | 1310.351 | 27.073 | 27.309 | 38.529 | 25.001 | 2.5 | 1 | 0.3 | 0 | 0.3
1018 | 30/07/2025 09:46:04.788 | 99.648 | 74 | 100 | 71 | 53 | 30.152 | 9.734 | 6.934 | 134.693 | 28.677 | 28.216 | 27.426 | 602.395 | 25.576 | 26.322 | 1300.16 | 27.073 | 27.312 | 38.371 | 30.001 | 2.5 | 2 | 0.3 | 0 | 0.3
1019 | 30/07/2025 09:46:06.424 | 99.504 | 74 | 100 | 71 | 52 | 28.287 | 9.308 | 6.935 | 134.481 | 28.686 | 28.24 | 27.416 | 602.204 | 25.588 | 26.338 | 1300.089 | 27.063 | 27.286 | 38.606 | 26.001 | 3.3 | 2.9 | 0.9 | 0.5 | 0.3
1020 | 30/07/2025 09:46:08.060 | 99.6 | 74 | 100 | 70 | 53 | 26.359 | 9.578 | 6.935 | 134.714 | 28.694 | 28.237 | 27.428 | 602.562 | 25.595 | 26.309 | 1302.766 | 27.029 | 27.311 | 38.534 | 26.001 | 3.3 | 2.9 | 0.9 | 0.5 | 0.3
1021 | 30/07/2025 09:46:09.698 | 99.72 | 74 | 100 | 70 | 53 | 29.768 | 9.575 | 6.936 | 134.673 | 28.688 | 28.25 | 27.407 | 603.356 | 25.595 | 26.342 | 1305.698 | 27.099 | 27.315 | 38.368 | 27.001 | 3.3 | 0.6 | 0.9 | 0.5 | 0.3
1022 | 30/07/2025 09:46:11.336 | 99.864 | 73 | 99 | 70 | 52 | 30.108 | 9.43 | 6.935 | 134.903 | 28.683 | 28.217 | 27.42 | 603.486 | 25.595 | 26.354 | 1309.698 | 27.063 | 27.307 | 38.476 | 32.001 | 2.1 | 0.9 | 1.2 | 0.9 | 0.3
1023 | 30/07/2025 09:46:12.969 | 99.6 | 74 | 100 | 70 | 53 | 26.624 | 9.459 | 6.935 | 134.581 | 28.671 | 28.231 | 27.433 | 603.516 | 25.596 | 26.351 | 1307.089 | 27.063 | 27.293 | 38.174 | 32.001 | 2.1 | 1.5 | 1.2 | 0.9 | 0.3
1024 | 30/07/2025 09:46:14.609 | 99.552 | 73 | 100 | 70 | 53 | 30.234 | 9.423 | 6.935 | 134.455 | 28.701 | 28.238 | 27.42 | 603.509 | 25.616 | 26.358 | 1305.596 | 27.05 | 27.303 | 38.608 | 25.001 | 2.8 | 1.3 | 0 | 0 | 0.2
1025 | 30/07/2025 09:46:16.245 | 99.816 | 72 | 100 | 72 | 53 | 27.672 | 9.582 | 6.936 | 134.588 | 28.681 | 28.25 | 27.414 | 603.565 | 25.598 | 26.362 | 1297.747 | 27.055 | 27.32 | 38.607 | 25.001 | 2.8 | 1.3 | 0 | 0 | 0.2
1026 | 30/07/2025 09:46:17.881 | 99.432 | 73 | 100 | 70 | 53 | 26.764 | 9.479 | 6.936 | 134.728 | 28.654 | 28.228 | 27.382 | 603.333 | 25.59 | 26.367 | 1292.302 | 27.071 | 27.299 | 38.5 | 28.001 | 2.8 | 1.6 | 0 | 0 | 0.2
1027 | 30/07/2025 09:46:19.517 | 98.424 | 72 | 100 | 70 | 52 | 29.903 | 9.288 | 6.934 | 134.679 | 28.67 | 28.223 | 27.437 | 603.605 | 25.604 | 26.344 | 1297.792 | 27.059 | 27.289 | 38.306 | 28.001 | 3.3 | 1.6 | 0.6 | 0.2 | 0.3
1028 | 30/07/2025 09:46:21.158 | 98.424 | 73 | 100 | 70 | 52 | 29.783 | 9.433 | 6.935 | 134.414 | 28.663 | 28.253 | 27.423 | 603.474 | 25.586 | 26.354 | 1297.258 | 27.077 | 27.306 | 38.439 | 29.001 | 3.3 | 2.3 | 0.6 | 0.2 | 0.3
1029 | 30/07/2025 09:46:22.792 | 98.232 | 72 | 100 | 71 | 53 | 29.322 | 9.562 | 6.935 | 134.565 | 28.663 | 28.246 | 27.432 | 603.595 | 25.588 | 26.353 | 1295.702 | 27.03 | 27.313 | 38.519 | 29.001 | 2.5 | 1.4 | 0.7 | 1.2 | 0.3
1030 | 30/07/2025 09:46:24.428 | 97.584 | 73 | 100 | 70 | 53 | 30.229 | 9.724 | 6.937 | 134.661 | 28.664 | 28.235 | 27.411 | 603.413 | 25.591 | 26.364 | 1292.854 | 27.072 | 27.315 | 38.455 | 25.001 | 2.5 | 0.8 | 0.7 | 1.2 | 0.3
1031 | 30/07/2025 09:46:26.066 | 98.352 | 72 | 100 | 71 | 52 | 27.152 | 9.426 | 6.935 | 134.786 | 28.692 | 28.225 | 27.403 | 603.441 | 25.616 | 26.348 | 1281.789 | 27.073 | 27.302 | 38.467 | 25.001 | 2.5 | 0.8 | 0.7 | 1.2 | 0.3
1032 | 30/07/2025 09:46:27.702 | 98.448 | 72 | 100 | 70 | 53 | 27.251 | 9.424 | 6.934 | 134.574 | 28.679 | 28.218 | 27.424 | 602.337 | 25.575 | 26.353 | 1288.84 | 27.068 | 27.304 | 38.239 | 33.001 | 3 | 2.5 | 0.6 | 0.5 | 0.2
1033 | 30/07/2025 09:46:29.341 | 98.808 | 73 | 100 | 70 | 54 | 30.003 | 9.357 | 6.938 | 134.449 | 28.689 | 28.241 | 27.406 | 602.286 | 25.595 | 26.359 | 1287.992 | 27.051 | 27.298 | 38.752 | 27.001 | 3 | 1.2 | 0.6 | 0.5 | 0.2
1034 | 30/07/2025 09:46:30.978 | 98.832 | 73 | 100 | 71 | 52 | 26.352 | 9.41 | 6.937 | 134.504 | 28.684 | 28.256 | 27.406 | 602.284 | 25.588 | 26.348 | 1285.979 | 27.054 | 27.325 | 38.521 | 22.001 | 4.2 | 0.6 | 0.6 | 0.5 | 0.2
1035 | 30/07/2025 09:46:32.613 | 99.312 | 74 | 100 | 71 | 51 | 29.721 | 9.571 | 6.937 | 134.799 | 28.692 | 28.239 | 27.404 | 602.203 | 25.584 | 26.356 | 1292.011 | 27.068 | 27.303 | 38.662 | 28.001 | 4.2 | 0.6 | 0.6 | 0.5 | 0.2
1036 | 30/07/2025 09:46:34.251 | 99.384 | 74 | 100 | 69 | 52 | 30.123 | 9.576 | 6.934 | 134.761 | 28.688 | 28.221 | 27.413 | 602.211 | 25.576 | 26.344 | 1285.326 | 27.064 | 27.303 | 38.41 | 28.001 | 4.2 | 0.6 | 0.6 | 0.5 | 0.2
1037 | 30/07/2025 09:46:35.887 | 100.032 | 75 | 100 | 71 | 53 | 26.513 | 9.301 | 6.935 | 134.465 | 28.688 | 28.227 | 27.416 | 602.294 | 25.583 | 26.341 | 1292.366 | 27.087 | 27.294 | 38.202 | 26.001 | 2.6 | 2.1 | 0.6 | 0.6 | 0.3
1038 | 30/07/2025 09:46:37.520 | 99.912 | 74 | 100 | 71 | 52 | 27.833 | 9.452 | 6.9 | 134.71 | 28.701 | 28.237 | 27.408 | 602.337 | 25.589 | 26.335 | 1298.557 | 27.047 | 27.309 | 38.536 | 27.001 | 2.6 | 1.1 | 0.6 | 0.6 | 0.3
1039 | 30/07/2025 09:46:39.159 | 100.248 | 74 | 100 | 69 | 52 | 30.073 | 9.431 | 6.872 | 134.731 | 28.679 | 28.244 | 27.4 | 602.311 | 25.572 | 26.326 | 1310.631 | 27.068 | 27.314 | 38.423 | 26.001 | 2.1 | 1.3 | 0.6 | 0 | 0.3
1040 | 30/07/2025 09:46:40.795 | 99.984 | 74 | 100 | 71 | 52 | 26.756 | 9.438 | 6.848 | 134.789 | 28.689 | 28.237 | 27.397 | 602.318 | 25.587 | 26.333 | 1317.567 | 27.075 | 27.31 | 38.413 | 27.001 | 2.1 | 1 | 0.6 | 0 | 0.3
1041 | 30/07/2025 09:46:42.428 | 100.128 | 75 | 100 | 70 | 53 | 29.99 | 9.295 | 6.849 | 134.596 | 28.675 | 28.219 | 27.42 | 602.331 | 25.587 | 26.315 | 1317.513 | 27.076 | 27.319 | 38.343 | 28.001 | 2 | 1.2 | 0 | 0.5 | 0.3
1042 | 30/07/2025 09:46:44.064 | 99.96 | 74 | 100 | 71 | 52 | 29.861 | 9.551 | 6.849 | 134.422 | 28.685 | 28.231 | 27.418 | 602.176 | 25.593 | 26.345 | 1314.996 | 27.057 | 27.279 | 38.464 | 28.001 | 2 | 1.2 | 0 | 0.5 | 0.3
1043 | 30/07/2025 09:46:45.700 | 99.816 | 74 | 100 | 70 | 53 | 26.28 | 9.437 | 6.865 | 134.698 | 28.671 | 28.234 | 27.42 | 602.309 | 25.593 | 26.335 | 1317.794 | 27.025 | 27.304 | 38.531 | 26.001 | 2 | 1.1 | 0 | 0.5 | 0.3
1044 | 30/07/2025 09:46:47.336 | 100.056 | 75 | 100 | 70 | 53 | 28.462 | 9.679 | 6.867 | 134.607 | 28.67 | 28.242 | 27.391 | 602.134 | 25.595 | 26.352 | 1309.902 | 27.091 | 27.309 | 38.444 | 29.001 | 3.5 | 2.2 | 0.6 | 0.1 | 0.3
1045 | 30/07/2025 09:46:48.971 | 99.888 | 73 | 99 | 71 | 53 | 27.155 | 9.577 | 6.866 | 134.789 | 28.668 | 28.229 | 27.395 | 602.18 | 25.597 | 26.347 | 1304.68 | 27.075 | 27.297 | 38.393 | 32.001 | 3.5 | 2.3 | 0.6 | 0.1 | 0.3
1046 | 30/07/2025 09:46:50.606 | 100.128 | 75 | 100 | 70 | 52 | 27.282 | 9.444 | 6.865 | 134.614 | 28.669 | 28.202 | 27.426 | 602.289 | 25.584 | 26.364 | 1305.248 | 27.074 | 27.295 | 38.125 | 31.001 | 2.9 | 2 | 0.6 | 0.2 | 0.3
1047 | 30/07/2025 09:46:52.242 | 99.576 | 74 | 100 | 71 | 53 | 30.008 | 9.426 | 6.865 | 134.514 | 28.673 | 28.244 | 27.42 | 602.268 | 25.608 | 26.349 | 1299.925 | 27.047 | 27.302 | 38.469 | 31.001 | 2.9 | 2 | 0.6 | 0.2 | 0.3
1048 | 30/07/2025 09:46:53.877 | 100.08 | 74 | 100 | 70 | 52 | 29.457 | 9.581 | 6.934 | 134.791 | 28.656 | 28.236 | 27.422 | 603.476 | 25.58 | 26.347 | 1309.789 | 27.05 | 27.324 | 38.65 | 23.001 | 2.9 | 1.7 | 0.6 | 0.2 | 0.3
1049 | 30/07/2025 09:46:55.513 | 99.792 | 73 | 100 | 72 | 53 | 26.022 | 9.576 | 6.936 | 134.716 | 28.665 | 28.231 | 27.384 | 603.203 | 25.596 | 26.354 | 1307.479 | 27.077 | 27.3 | 38.619 | 28.001 | 1.9 | 2.1 | 0 | 0.1 | 0.2
1050 | 30/07/2025 09:46:57.152 | 100.224 | 74 | 100 | 70 | 52 | 28.86 | 9.587 | 6.935 | 134.736 | 28.673 | 28.221 | 27.43 | 602.352 | 25.592 | 26.344 | 1306.956 | 27.068 | 27.297 | 38.19 | 31.001 | 1.9 | 1.1 | 0 | 0.1 | 0.2
1051 | 30/07/2025 09:46:58.789 | 99.96 | 74 | 100 | 69 | 53 | 26.62 | 9.583 | 6.931 | 134.731 | 28.674 | 28.215 | 27.425 | 602.292 | 25.597 | 26.361 | 1314.905 | 27.064 | 27.285 | 38.231 | 30.001 | 3.7 | 1.6 | 0 | 0.9 | 0.3
1052 | 30/07/2025 09:47:00.425 | 100.128 | 74 | 100 | 70 | 52 | 27.743 | 9.583 | 6.866 | 134.403 | 28.68 | 28.251 | 27.416 | 602.427 | 25.593 | 26.349 | 1317.594 | 27.043 | 27.311 | 38.625 | 31.001 | 3.7 | 2.4 | 0 | 0.9 | 0.3
1053 | 30/07/2025 09:47:02.058 | 100.056 | 75 | 100 | 70 | 55 | 30.076 | 9.578 | 6.868 | 134.653 | 28.702 | 28.236 | 27.409 | 602.171 | 25.586 | 26.361 | 1317.906 | 27.064 | 27.315 | 38.547 | 31.001 | 3.7 | 2.4 | 0 | 0.9 | 0.3
1054 | 30/07/2025 09:47:03.692 | 100.584 | 74 | 100 | 70 | 53 | 28.843 | 9.433 | 6.865 | 134.77 | 28.716 | 28.232 | 27.416 | 602.307 | 25.603 | 26.343 | 1319.053 | 27.06 | 27.304 | 38.608 | 26.001 | 1.9 | 0.7 | 1.3 | 0.5 | 0.4
1055 | 30/07/2025 09:47:05.326 | 100.344 | 74 | 100 | 70 | 53 | 26.099 | 9.581 | 6.899 | 134.526 | 28.685 | 28.211 | 27.418 | 602.322 | 25.582 | 26.355 | 1317.422 | 27.077 | 27.298 | 38.199 | 23.001 | 1.9 | 1.8 | 1.3 | 0.5 | 0.4
1056 | 30/07/2025 09:47:06.960 | 100.368 | 75 | 100 | 70 | 53 | 29.867 | 9.578 | 6.889 | 134.617 | 28.705 | 28.226 | 27.432 | 602.476 | 25.578 | 26.332 | 1323.834 | 27.056 | 27.289 | 38.131 | 26.001 | 3.8 | 1.6 | 0.9 | 0 | 0.3
1057 | 30/07/2025 09:47:08.597 | 100.08 | 74 | 100 | 71 | 53 | 26.223 | 9.58 | 6.866 | 134.49 | 28.686 | 28.25 | 27.416 | 602.347 | 25.562 | 26.337 | 1321.629 | 27.066 | 27.323 | 38.524 | 30.001 | 3.8 | 1.3 | 0.9 | 0 | 0.3
1058 | 30/07/2025 09:47:10.233 | 99.504 | 74 | 100 | 71 | 52 | 28.291 | 9.576 | 6.932 | 134.835 | 28.687 | 28.228 | 27.406 | 602.173 | 25.584 | 26.337 | 1314.403 | 27.066 | 27.309 | 38.51 | 30.001 | 3.8 | 1.3 | 0.9 | 0 | 0.3
1059 | 30/07/2025 09:47:11.867 | 99.744 | 74 | 100 | 70 | 53 | 30.197 | 9.579 | 6.934 | 134.691 | 28.683 | 28.228 | 27.407 | 602.258 | 25.567 | 26.335 | 1317.648 | 27.065 | 27.31 | 38.462 | 30.001 | 2.3 | 1.9 | 0.9 | 0.8 | 0.3
1060 | 30/07/2025 09:47:13.503 | 100.224 | 75 | 100 | 71 | 51 | 28.349 | 9.464 | 6.937 | 134.51 | 28.683 | 28.22 | 27.416 | 602.235 | 25.583 | 26.339 | 1326.997 | 27.092 | 27.291 | 38.27 | 25.001 | 2.3 | 0.9 | 0.9 | 0.8 | 0.3
1061 | 30/07/2025 09:47:15.139 | 100.272 | 75 | 100 | 70 | 52 | 26.385 | 9.572 | 6.935 | 134.49 | 28.692 | 28.244 | 27.417 | 602.41 | 25.602 | 26.33 | 1329.636 | 27.042 | 27.303 | 38.699 | 30.001 | 5.4 | 0.9 | 0.9 | 0.5 | 0.2
1062 | 30/07/2025 09:47:16.778 | 99.936 | 76 | 100 | 70 | 53 | 29.522 | 9.81 | 6.938 | 134.733 | 28.682 | 28.239 | 27.41 | 602.271 | 25.588 | 26.35 | 1332.71 | 27.043 | 27.304 | 38.651 | 33.001 | 5.4 | 1.2 | 0.9 | 0.5 | 0.2
1063 | 30/07/2025 09:47:18.416 | 100.584 | 75 | 100 | 70 | 53 | 26.126 | 9.432 | 6.935 | 134.666 | 28.691 | 28.24 | 27.408 | 602.297 | 25.595 | 26.34 | 1318.494 | 27.064 | 27.306 | 38.436 | 26.001 | 1.1 | 1.5 | 0 | 0.1 | 0.2
1064 | 30/07/2025 09:47:20.051 | 100.104 | 74 | 100 | 70 | 52 | 29.058 | 9.49 | 6.935 | 134.648 | 28.677 | 28.225 | 27.418 | 602.367 | 25.59 | 26.338 | 1307.481 | 27.091 | 27.306 | 38.487 | 26.001 | 1.1 | 1.5 | 0 | 0.1 | 0.2
1065 | 30/07/2025 09:47:21.686 | 100.2 | 75 | 100 | 70 | 52 | 30.27 | 9.564 | 6.935 | 134.504 | 28.683 | 28.223 | 27.422 | 603.115 | 25.613 | 26.357 | 1302.272 | 27.061 | 27.288 | 38.304 | 30.001 | 1.1 | 1.3 | 0 | 0.1 | 0.2
1066 | 30/07/2025 09:47:23.320 | 100.464 | 75 | 100 | 70 | 53 | 27.713 | 9.577 | 6.935 | 134.624 | 28.659 | 28.244 | 27.422 | 603.511 | 25.605 | 26.362 | 1314.119 | 27.025 | 27.31 | 38.557 | 24.001 | 3.9 | 0.6 | 0.6 | 0.3 | 0.3
1067 | 30/07/2025 09:47:24.958 | 100.512 | 74 | 100 | 70 | 52 | 30.116 | 9.575 | 6.935 | 134.869 | 28.682 | 28.235 | 27.418 | 603.58 | 25.612 | 26.357 | 1312.016 | 27.04 | 27.307 | 38.745 | 28.001 | 3.9 | 1.1 | 0.6 | 0.3 | 0.3
1068 | 30/07/2025 09:47:26.593 | 100.512 | 76 | 100 | 70 | 52 | 28.926 | 9.511 | 6.857 | 134.719 | 28.661 | 28.232 | 27.391 | 602.359 | 25.583 | 26.361 | 1317.11 | 27.08 | 27.318 | 38.385 | 30.001 | 2.8 | 1.4 | 0.1 | 0.5 | 0.2
1069 | 30/07/2025 09:47:28.230 | 100.704 | 75 | 100 | 70 | 53 | 26.198 | 9.447 | 6.85 | 134.655 | 28.66 | 28.224 | 27.424 | 602.276 | 25.588 | 26.38 | 1322.32 | 27.068 | 27.307 | 38.309 | 30.001 | 2.8 | 1.4 | 0.1 | 0.5 | 0.2
1070 | 30/07/2025 09:47:29.866 | 100.752 | 76 | 100 | 71 | 53 | 29.325 | 9.36 | 6.827 | 134.442 | 28.66 | 28.245 | 27.432 | 602.171 | 25.592 | 26.348 | 1315.919 | 27.049 | 27.298 | 38.487 | 28.001 | 2.8 | 0.9 | 0.1 | 0.5 | 0.2
1071 | 30/07/2025 09:47:31.501 | 101.184 | 75 | 100 | 70 | 54 | 30.284 | 9.474 | 6.829 | 134.567 | 28.665 | 28.263 | 27.398 | 602.322 | 25.592 | 26.358 | 1318.458 | 27.047 | 27.314 | 38.526 | 27.001 | 2.8 | 0.1 | 0 | 0 | 0.2
1072 | 30/07/2025 09:47:33.136 | 101.112 | 76 | 100 | 70 | 53 | 28.32 | 9.207 | 6.827 | 134.767 | 28.683 | 28.239 | 27.415 | 602.277 | 25.586 | 26.339 | 1318.517 | 27.059 | 27.301 | 38.616 | 25.001 | 2.8 | 0 | 0 | 0 | 0.2
1073 | 30/07/2025 09:47:34.772 | 100.512 | 75 | 100 | 71 | 51 | 30.172 | 9.289 | 6.828 | 134.564 | 28.685 | 28.241 | 27.391 | 602.228 | 25.585 | 26.347 | 1306.455 | 27.093 | 27.313 | 38.479 | 29.001 | 1.8 | 1.5 | 0 | 0.5 | 0.2
1074 | 30/07/2025 09:47:36.407 | 99.6 | 73 | 100 | 70 | 52 | 28.372 | 9.431 | 6.826 | 134.783 | 28.697 | 28.223 | 27.437 | 602.392 | 25.598 | 26.353 | 1292.991 | 27.064 | 27.287 | 38.137 | 30.001 | 1.8 | 1 | 0 | 0.5 | 0.2
1075 | 30/07/2025 09:47:38.042 | 99.192 | 74 | 100 | 70 | 52 | 26.368 | 9.416 | 6.849 | 134.599 | 28.692 | 28.245 | 27.426 | 602.399 | 25.578 | 26.351 | 1295.144 | 27.048 | 27.315 | 38.331 | 30.001 | 1.8 | 1 | 0 | 0.5 | 0.2
1076 | 30/07/2025 09:47:39.677 | 98.688 | 74 | 100 | 70 | 52 | 29.678 | 9.421 | 6.879 | 134.667 | 28.691 | 28.242 | 27.396 | 602.03 | 25.591 | 26.366 | 1287.741 | 27.054 | 27.314 | 38.598 | 27.001 | 1.1 | 1.8 | 0.7 | 0.6 | 0.2
1077 | 30/07/2025 09:47:41.310 | 98.208 | 73 | 100 | 70 | 52 | 30.115 | 9.575 | 6.898 | 134.647 | 28.679 | 28.229 | 27.401 | 602.233 | 25.593 | 26.341 | 1287.989 | 27.079 | 27.302 | 38.461 | 24.001 | 1.1 | 2.3 | 0.7 | 0.6 | 0.2
1078 | 30/07/2025 09:47:42.946 | 97.92 | 73 | 100 | 71 | 52 | 28.801 | 9.575 | 6.901 | 134.65 | 28.68 | 28.212 | 27.406 | 602.272 | 25.581 | 26.353 | 1294.525 | 27.07 | 27.306 | 38.386 | 25.001 | 3.5 | 2.3 | 0 | 0.6 | 0.2
1079 | 30/07/2025 09:47:44.583 | 97.896 | 73 | 100 | 71 | 52 | 30.284 | 9.494 | 6.899 | 134.509 | 28.684 | 28.232 | 27.432 | 602.407 | 25.573 | 26.326 | 1306.776 | 27.065 | 27.279 | 38.369 | 27.001 | 3.5 | 1.5 | 0 | 0.6 | 0.2
1080 | 30/07/2025 09:47:46.219 | 98.208 | 73 | 100 | 71 | 52 | 27.681 | 9.431 | 6.901 | 134.597 | 28.691 | 28.249 | 27.415 | 602.267 | 25.583 | 26.332 | 1312.448 | 27.068 | 27.312 | 38.586 | 27.001 | 3.5 | 1.5 | 0 | 0.6 | 0.2
1081 | 30/07/2025 09:47:47.855 | 98.232 | 72 | 100 | 70 | 52 | 26.726 | 9.574 | 6.9 | 134.901 | 28.704 | 28.235 | 27.395 | 602.199 | 25.594 | 26.33 | 1311.992 | 27.067 | 27.301 | 38.508 | 30.001 | 2.6 | 1.6 | 0.6 | 0.8 | 0.2
1082 | 30/07/2025 09:47:49.494 | 97.728 | 71 | 100 | 70 | 52 | 29.947 | 9.433 | 6.9 | 134.579 | 28.682 | 28.231 | 27.411 | 602.315 | 25.579 | 26.328 | 1312.044 | 27.081 | 27.311 | 38.343 | 25.001 | 2.6 | 0.7 | 0.6 | 0.8 | 0.2
1083 | 30/07/2025 09:47:51.129 | 97.512 | 72 | 100 | 70 | 52 | 29.915 | 9.524 | 6.937 | 134.616 | 28.671 | 28.215 | 27.415 | 603.099 | 25.59 | 26.343 | 1309.615 | 27.071 | 27.282 | 38.079 | 26.001 | 1.8 | 1.4 | 0.6 | 0.5 | 0.1
1084 | 30/07/2025 09:47:52.766 | 97.2 | 72 | 100 | 71 | 52 | 29.396 | 9.509 | 6.935 | 134.488 | 28.676 | 28.241 | 27.421 | 603.491 | 25.586 | 26.342 | 1314.431 | 27.059 | 27.304 | 38.378 | 27.001 | 1.8 | 2.2 | 0.6 | 0.5 | 0.1
1085 | 30/07/2025 09:47:54.402 | 97.32 | 72 | 100 | 71 | 52 | 30.261 | 9.499 | 6.938 | 134.702 | 28.676 | 28.234 | 27.399 | 603.449 | 25.596 | 26.35 | 1307.472 | 27.019 | 27.311 | 38.45 | 30.001 | 0.9 | 1.4 | 0.6 | 0 | 0.2
1086 | 30/07/2025 09:47:56.039 | 96.864 | 71 | 100 | 71 | 52 | 27.135 | 9.448 | 6.925 | 134.76 | 28.681 | 28.24 | 27.396 | 603.523 | 25.588 | 26.37 | 1308.569 | 27.067 | 27.315 | 38.289 | 30.001 | 0.9 | 1.4 | 0.6 | 0 | 0.2
1087 | 30/07/2025 09:47:57.676 | 96.936 | 70 | 100 | 71 | 52 | 27.363 | 9.297 | 6.9 | 134.547 | 28.668 | 28.224 | 27.404 | 603.51 | 25.598 | 26.366 | 1306.886 | 27.092 | 27.31 | 38.487 | 24.001 | 0.9 | 1.5 | 0.6 | 0 | 0.2
1088 | 30/07/2025 09:47:59.314 | 96.768 | 71 | 100 | 70 | 52 | 30.022 | 9.425 | 6.934 | 134.666 | 28.656 | 28.235 | 27.415 | 603.623 | 25.61 | 26.359 | 1306.035 | 27.068 | 27.277 | 38.422 | 30.001 | 1.9 | 1.5 | 0.6 | 0.3 | 0.1
1089 | 30/07/2025 09:48:00.950 | 96.24 | 70 | 100 | 71 | 52 | 26.399 | 9.287 | 6.936 | 134.36 | 28.661 | 28.24 | 27.416 | 603.466 | 25.6 | 26.365 | 1310.549 | 27.068 | 27.303 | 38.4 | 27.001 | 1.9 | 1.2 | 0.6 | 0.3 | 0.1
1090 | 30/07/2025 09:48:02.584 | 96.504 | 70 | 100 | 70 | 52 | 29.768 | 9.281 | 6.935 | 134.879 | 28.672 | 28.239 | 27.412 | 603.532 | 25.604 | 26.357 | 1312.457 | 27.033 | 27.313 | 38.605 | 29.001 | 2.5 | 1 | 0.6 | 0 | 0.1
1091 | 30/07/2025 09:48:04.218 | 96.432 | 71 | 100 | 70 | 53 | 30.173 | 9.457 | 6.958 | 134.749 | 28.65 | 28.23 | 27.386 | 603.429 | 25.588 | 26.354 | 1317.532 | 27.09 | 27.32 | 38.563 | 29.001 | 2.5 | 1 | 0.6 | 0 | 0.1
1092 | 30/07/2025 09:48:05.852 | 96.48 | 71 | 100 | 71 | 52 | 26.778 | 9.581 | 6.987 | 134.654 | 28.679 | 28.204 | 27.431 | 603.521 | 25.583 | 26.358 | 1322.473 | 27.07 | 27.302 | 38.34 | 25.001 | 2.5 | 1.3 | 0.6 | 0 | 0.1
1093 | 30/07/2025 09:48:07.487 | 96.912 | 71 | 100 | 71 | 52 | 27.902 | 9.447 | 6.987 | 134.681 | 28.668 | 28.241 | 27.435 | 603.575 | 25.593 | 26.337 | 1327.429 | 27.06 | 27.29 | 38.389 | 25.001 | 2.2 | 1.4 | 0 | 0.5 | 0.2
1094 | 30/07/2025 09:48:09.122 | 97.128 | 71 | 100 | 71 | 52 | 27.856 | 9.234 | 6.987 | 134.659 | 28.692 | 28.235 | 27.405 | 603.399 | 25.594 | 26.348 | 1327.603 | 27.034 | 27.299 | 38.651 | 24.001 | 2.2 | 0.9 | 0 | 0.5 | 0.2
1095 | 30/07/2025 09:48:10.758 | 97.224 | 72 | 100 | 71 | 52 | 26.822 | 9.498 | 6.987 | 134.687 | 28.681 | 28.238 | 27.407 | 602.34 | 25.591 | 26.35 | 1318.331 | 27.055 | 27.312 | 38.571 | 26.001 | 1.4 | 1.3 | 1.2 | 0.5 | 0.3
1096 | 30/07/2025 09:48:12.393 | 97.056 | 71 | 100 | 70 | 53 | 29.985 | 9.5 | 6.994 | 134.714 | 28.681 | 28.226 | 27.376 | 603.336 | 25.58 | 26.361 | 1332.35 | 27.086 | 27.304 | 38.564 | 23.001 | 1.4 | 2.3 | 1.2 | 0.5 | 0.3
1097 | 30/07/2025 09:48:14.029 | 97.008 | 71 | 100 | 71 | 52 | 29.944 | 9.499 | 7.003 | 134.786 | 28.721 | 28.224 | 27.428 | 602.621 | 25.599 | 26.351 | 1339.165 | 27.067 | 27.29 | 38.376 | 23.001 | 1.4 | 2.3 | 1.2 | 0.5 | 0.3
1098 | 30/07/2025 09:48:15.666 | 97.248 | 72 | 100 | 71 | 53 | 26.391 | 9.581 | 7.006 | 134.553 | 28.688 | 28.255 | 27.417 | 602.252 | 25.582 | 26.342 | 1322.693 | 27.059 | 27.317 | 38.55 | 26.001 | 3.2 | 0.4 | 0.6 | 0.5 | 0.3
1099 | 30/07/2025 09:48:17.305 | 97.416 | 71 | 100 | 70 | 52 | 28.284 | 9.499 | 7.006 | 134.713 | 28.692 | 28.234 | 27.416 | 602.083 | 25.569 | 26.346 | 1320.053 | 27.044 | 27.305 | 38.531 | 24.001 | 3.2 | 1.5 | 0.6 | 0.5 | 0.3
1100 | 30/07/2025 09:48:18.941 | 97.272 | 71 | 100 | 70 | 52 | 27.193 | 9.432 | 7.006 | 134.744 | 28.68 | 28.253 | 27.394 | 602.254 | 25.569 | 26.325 | 1320.056 | 27.083 | 27.321 | 38.558 | 23.001 | 1.9 | 0.8 | 0.3 | 0.8 | 0.3
1101 | 30/07/2025 09:48:20.576 | 96.576 | 70 | 100 | 71 | 53 | 27.234 | 9.418 | 7.005 | 134.738 | 28.68 | 28.218 | 27.39 | 602.042 | 25.584 | 26.336 | 1327.364 | 27.08 | 27.295 | 38.433 | 27.001 | 1.9 | 1 | 0.3 | 0.8 | 0.3
1102 | 30/07/2025 09:48:22.209 | 96.192 | 71 | 100 | 71 | 53 | 30.075 | 9.45 | 6.985 | 134.784 | 28.689 | 28.228 | 27.426 | 602.489 | 25.581 | 26.326 | 1318.621 | 27.06 | 27.297 | 38.312 | 27.001 | 1.9 | 1 | 0.3 | 0.8 | 0.3
1103 | 30/07/2025 09:48:23.842 | 96.72 | 72 | 100 | 71 | 53 | 29.556 | 9.437 | 6.99 | 134.496 | 28.679 | 28.242 | 27.409 | 602.226 | 25.583 | 26.34 | 1322.464 | 27.047 | 27.311 | 38.639 | 26.001 | 1.2 | 2 | 0 | 1 | 0.2
1104 | 30/07/2025 09:48:25.481 | 96.528 | 70 | 100 | 71 | 53 | 26.098 | 9.501 | 6.998 | 134.817 | 28.696 | 28.235 | 27.396 | 602.216 | 25.611 | 26.337 | 1327.396 | 27.06 | 27.301 | 38.433 | 30.001 | 1.2 | 2 | 0 | 1 | 0.2
1105 | 30/07/2025 09:48:27.114 | 96.984 | 72 | 100 | 70 | 52 | 30.226 | 9.559 | 7.033 | 134.672 | 28.677 | 28.233 | 27.371 | 602.054 | 25.593 | 26.362 | 1322.919 | 27.082 | 27.313 | 38.507 | 27.001 | 2.7 | 1.1 | 0.5 | 1.1 | 0.3
1106 | 30/07/2025 09:48:28.753 | 97.248 | 72 | 100 | 70 | 52 | 26.56 | 9.43 | 7.032 | 134.732 | 28.693 | 28.218 | 27.406 | 602.266 | 25.612 | 26.347 | 1334.541 | 27.067 | 27.302 | 38.306 | 27.001 | 2.7 | 1.2 | 0.5 | 1.1 | 0.3
1107 | 30/07/2025 09:48:30.390 | 97.224 | 70 | 100 | 71 | 51 | 27.882 | 9.435 | 7.031 | 134.382 | 28.671 | 28.245 | 27.425 | 602.387 | 25.591 | 26.353 | 1327.359 | 27.08 | 27.294 | 38.577 | 29.001 | 1.9 | 2.2 | 0.6 | 0.5 | 0.3
1108 | 30/07/2025 09:48:32.026 | 97.392 | 70 | 100 | 71 | 53 | 30.147 | 9.48 | 7.006 | 134.702 | 28.67 | 28.242 | 27.411 | 602.284 | 25.596 | 26.356 | 1322.739 | 27.036 | 27.308 | 38.768 | 29.001 | 1.9 | 2.2 | 0.6 | 0.5 | 0.3
1109 | 30/07/2025 09:48:33.662 | 97.488 | 71 | 100 | 71 | 52 | 28.932 | 9.469 | 7.005 | 134.801 | 28.674 | 28.244 | 27.405 | 602.383 | 25.588 | 26.354 | 1325.514 | 27.059 | 27.308 | 38.527 | 28.001 | 1.9 | 1.9 | 0.6 | 0.5 | 0.3
1110 | 30/07/2025 09:48:35.298 | 97.512 | 72 | 100 | 70 | 52 | 26.16 | 9.581 | 7.036 | 134.665 | 28.645 | 28.21 | 27.397 | 602.156 | 25.584 | 26.357 | 1308.855 | 27.097 | 27.305 | 38.367 | 31.001 | 3.1 | 1.4 | 0.6 | 0.8 | 0.3
1111 | 30/07/2025 09:48:36.932 | 97.488 | 73 | 100 | 70 | 52 | 29.888 | 9.563 | 7.022 | 134.697 | 28.66 | 28.22 | 27.423 | 602.308 | 25.595 | 26.358 | 1307.29 | 27.068 | 27.307 | 38.459 | 24.001 | 3.1 | 1.7 | 0.6 | 0.8 | 0.3
1112 | 30/07/2025 09:48:38.567 | 97.848 | 72 | 100 | 70 | 52 | 26.3 | 9.285 | 6.988 | 134.581 | 28.66 | 28.232 | 27.412 | 602.224 | 25.593 | 26.367 | 1304.591 | 27.065 | 27.297 | 38.471 | 23.001 | 3 | 2.7 | 0 | 0.6 | 0.3
1113 | 30/07/2025 09:48:40.205 | 97.656 | 72 | 100 | 71 | 52 | 28.484 | 9.288 | 6.988 | 134.715 | 28.694 | 28.239 | 27.416 | 602.226 | 25.605 | 26.349 | 1295.364 | 27.038 | 27.316 | 38.733 | 23.001 | 3 | 2.7 | 0 | 0.6 | 0.3
1114 | 30/07/2025 09:48:41.843 | 97.992 | 73 | 100 | 69 | 53 | 30.261 | 9.486 | 6.987 | 134.662 | 28.679 | 28.251 | 27.392 | 602.318 | 25.582 | 26.35 | 1297.465 | 27.085 | 27.328 | 38.606 | 28.001 | 3 | 0.8 | 0 | 0.6 | 0.3
1115 | 30/07/2025 09:48:43.479 | 98.352 | 73 | 100 | 71 | 52 | 28.422 | 9.578 | 7.004 | 134.727 | 28.698 | 28.207 | 27.42 | 602.257 | 25.589 | 26.351 | 1302.108 | 27.068 | 27.298 | 38.375 | 24.001 | 3.6 | 1 | 0 | 0 | 0.3
1116 | 30/07/2025 09:48:45.115 | 97.968 | 71 | 100 | 71 | 52 | 26.384 | 9.554 | 7.003 | 134.627 | 28.689 | 28.238 | 27.415 | 602.354 | 25.581 | 26.342 | 1309.478 | 27.067 | 27.28 | 38.243 | 28.001 | 3.6 | 2.4 | 0 | 0 | 0.3
1117 | 30/07/2025 09:48:46.752 | 97.728 | 72 | 100 | 70 | 52 | 29.472 | 9.501 | 7.006 | 134.67 | 28.699 | 28.239 | 27.409 | 602.201 | 25.594 | 26.357 | 1307.406 | 27.046 | 27.308 | 38.489 | 28.001 | 1.1 | 1.2 | 0.1 | 1.2 | 0.2
1118 | 30/07/2025 09:48:48.391 | 96.984 | 73 | 100 | 70 | 52 | 26.157 | 9.486 | 6.987 | 134.828 | 28.69 | 28.239 | 27.405 | 601.467 | 25.581 | 26.347 | 1297.623 | 27.05 | 27.312 | 38.465 | 26.001 | 1.1 | 1.3 | 0.1 | 1.2 | 0.2
1119 | 30/07/2025 09:48:50.026 | 97.008 | 72 | 100 | 70 | 52 | 28.898 | 9.441 | 6.983 | 134.714 | 28.688 | 28.226 | 27.388 | 600.67 | 25.575 | 26.361 | 1297.851 | 27.079 | 27.304 | 38.593 | 26.001 | 1.1 | 1.3 | 0.1 | 1.2 | 0.2
1120 | 30/07/2025 09:48:51.661 | 97.536 | 73 | 100 | 72 | 52 | 30.323 | 9.436 | 6.933 | 134.775 | 28.692 | 28.216 | 27.426 | 600.842 | 25.578 | 26.334 | 1300.35 | 27.072 | 27.296 | 38.238 | 27.001 | 2.5 | 0.9 | 0.2 | 1.6 | 0.2
1121 | 30/07/2025 09:48:53.295 | 97.896 | 72 | 100 | 71 | 52 | 27.854 | 9.43 | 6.902 | 134.364 | 28.682 | 28.26 | 27.42 | 600.793 | 25.582 | 26.321 | 1305.239 | 27.067 | 27.321 | 38.562 | 27.001 | 2.5 | 1.7 | 0.2 | 1.6 | 0.2
1122 | 30/07/2025 09:48:54.954 | 97.824 | 73 | 100 | 71 | 53 | 30.158 | 9.338 | 6.901 | 133.28 | 28.692 | 28.245 | 27.412 | 600.906 | 25.585 | 26.325 | 1298.613 | 27.044 | 27.321 | 38.542 | 29.001 | 2.2 | 2.3 | 1.2 | 0 | 0.3
1123 | 30/07/2025 09:48:56.592 | 97.344 | 72 | 100 | 71 | 52 | 29.062 | 9.578 | 6.902 | 133.281 | 28.667 | 28.249 | 27.383 | 602.221 | 25.576 | 26.337 | 1297.683 | 27.069 | 27.314 | 38.712 | 25.001 | 2.2 | 1.7 | 1.2 | 0 | 0.3
1124 | 30/07/2025 09:48:58.227 | 97.704 | 73 | 100 | 71 | 52 | 26.109 | 9.5 | 6.9 | 133.429 | 28.691 | 28.226 | 27.41 | 602.113 | 25.603 | 26.334 | 1309.893 | 27.068 | 27.303 | 38.519 | 25.001 | 2.2 | 1.7 | 1.2 | 0 | 0.3
1125 | 30/07/2025 09:48:59.862 | 97.896 | 72 | 100 | 70 | 53 | 29.434 | 9.578 | 6.897 | 133.273 | 28.673 | 28.225 | 27.437 | 602.38 | 25.583 | 26.339 | 1307.207 | 27.069 | 27.296 | 38.366 | 26.001 | 2.3 | 0.8 | 0 | 0.5 | 0.3
1126 | 30/07/2025 09:49:01.495 | 98.208 | 72 | 100 | 70 | 51 | 30.41 | 9.578 | 6.937 | 133.118 | 28.675 | 28.24 | 27.405 | 602.114 | 25.576 | 26.364 | 1302.561 | 27.05 | 27.314 | 38.548 | 29.001 | 2.3 | 1.9 | 0 | 0.5 | 0.3
1127 | 30/07/2025 09:49:03.130 | 97.824 | 71 | 100 | 71 | 52 | 27.154 | 9.578 | 6.933 | 133.341 | 28.684 | 28.239 | 27.408 | 602.35 | 25.615 | 26.358 | 1314.742 | 27.058 | 27.314 | 38.55 | 25.001 | 4.6 | 0.9 | 0 | 0 | 0.2
1128 | 30/07/2025 09:49:04.765 | 98.352 | 72 | 100 | 69 | 52 | 30.271 | 9.438 | 6.977 | 133.359 | 28.665 | 28.237 | 27.392 | 602.016 | 25.584 | 26.368 | 1312.284 | 27.08 | 27.311 | 38.495 | 25.001 | 4.6 | 0.2 | 0 | 0 | 0.2
1129 | 30/07/2025 09:49:06.400 | 97.944 | 72 | 100 | 70 | 52 | 28.312 | 9.728 | 6.987 | 133.302 | 28.664 | 28.219 | 27.402 | 602.318 | 25.596 | 26.348 | 1320.285 | 27.065 | 27.298 | 38.262 | 27.001 | 3.3 | 1 | 0.9 | 0.5 | 0.2
1130 | 30/07/2025 09:49:08.042 | 98.904 | 74 | 100 | 70 | 52 | 26.411 | 9.633 | 6.986 | 132.967 | 28.652 | 28.244 | 27.417 | 602.654 | 25.576 | 26.365 | 1326.984 | 27.073 | 27.297 | 38.214 | 27.001 | 3.3 | 1 | 0.9 | 0.5 | 0.2
1131 | 30/07/2025 09:49:09.676 | 99.168 | 76 | 100 | 70 | 52 | 29.752 | 9.429 | 6.912 | 133.278 | 28.65 | 28.237 | 27.413 | 603.415 | 25.598 | 26.347 | 1329.567 | 27.031 | 27.309 | 38.505 | 27.001 | 3.3 | 1.7 | 0.9 | 0.5 | 0.2
1132 | 30/07/2025 09:49:11.309 | 99.024 | 74 | 99 | 70 | 51 | 30.251 | 9.544 | 6.9 | 133.263 | 28.676 | 28.243 | 27.388 | 602.476 | 25.582 | 26.353 | 1316.762 | 27.068 | 27.306 | 38.484 | 26.001 | 3.1 | 0.7 | 1.6 | 0 | 0.2
1133 | 30/07/2025 09:49:12.945 | 98.448 | 73 | 100 | 72 | 52 | 28.991 | 9.431 | 6.9 | 133.461 | 28.672 | 28.233 | 27.388 | 602.267 | 25.601 | 26.355 | 1306.515 | 27.076 | 27.298 | 38.54 | 24.001 | 3.1 | 1 | 1.6 | 0 | 0.2
1134 | 30/07/2025 09:49:14.580 | 98.28 | 73 | 100 | 71 | 52 | 30.311 | 9.294 | 6.899 | 133.144 | 28.668 | 28.204 | 27.402 | 603.453 | 25.581 | 26.344 | 1297.443 | 27.065 | 27.294 | 38.122 | 32.001 | 2.9 | 1.1 | 0.2 | 0 | 0.2
1135 | 30/07/2025 09:49:16.214 | 98.064 | 72 | 100 | 70 | 52 | 27.845 | 9.568 | 6.936 | 132.925 | 28.681 | 28.234 | 27.403 | 603.408 | 25.577 | 26.36 | 1299.752 | 27.067 | 27.286 | 38.414 | 32.001 | 2.9 | 1.1 | 0.2 | 0 | 0.2
1136 | 30/07/2025 09:49:17.849 | 97.68 | 74 | 100 | 71 | 51 | 26.883 | 9.509 | 6.935 | 133.201 | 28.691 | 28.238 | 27.423 | 603.572 | 25.598 | 26.34 | 1297.759 | 27.034 | 27.312 | 38.636 | 29.001 | 2.9 | 2 | 0.2 | 0 | 0.2
1137 | 30/07/2025 09:49:19.487 | 98.184 | 74 | 100 | 71 | 52 | 30.005 | 9.513 | 6.936 | 133.103 | 28.698 | 28.248 | 27.384 | 603.237 | 25.585 | 26.35 | 1299.974 | 27.093 | 27.322 | 38.493 | 25.001 | 1.4 | 2.1 | 0.6 | 0.5 | 0.2
1138 | 30/07/2025 09:49:21.125 | 98.904 | 73 | 100 | 71 | 52 | 29.962 | 9.433 | 6.9 | 133.338 | 28.703 | 28.217 | 27.416 | 603.501 | 25.59 | 26.361 | 1299.306 | 27.069 | 27.304 | 38.229 | 23.001 | 1.4 | 3.2 | 0.6 | 0.5 | 0.2
1139 | 30/07/2025 09:49:22.760 | 98.328 | 71 | 100 | 70 | 52 | 29.462 | 9.499 | 6.899 | 133.089 | 28.686 | 28.216 | 27.41 | 603.448 | 25.573 | 26.344 | 1300.098 | 27.097 | 27.3 | 38.218 | 24.001 | 1.8 | 0.4 | 0 | 0.7 | 0.2
1140 | 30/07/2025 09:49:24.398 | 98.784 | 74 | 100 | 70 | 51 | 30.354 | 9.43 | 6.934 | 133.175 | 28.709 | 28.244 | 27.412 | 603.427 | 25.582 | 26.339 | 1307.286 | 27.047 | 27.303 | 38.522 | 22.001 | 1.8 | 0.6 | 0 | 0.7 | 0.2
1141 | 30/07/2025 09:49:26.031 | 98.784 | 73 | 100 | 71 | 52 | 27.353 | 9.445 | 6.936 | 133.362 | 28.684 | 28.243 | 27.392 | 603.521 | 25.593 | 26.335 | 1283.502 | 27.054 | 27.313 | 38.45 | 22.001 | 1.8 | 0.6 | 0 | 0.7 | 0.2
1142 | 30/07/2025 09:49:27.667 | 98.856 | 74 | 100 | 70 | 52 | 27.285 | 9.579 | 6.937 | 133.136 | 28.689 | 28.232 | 27.39 | 603.37 | 25.587 | 26.338 | 1277.686 | 27.077 | 27.304 | 38.578 | 26.001 | 2.1 | 1.5 | 0 | 0.5 | 0.1
1143 | 30/07/2025 09:49:29.304 | 98.928 | 73 | 100 | 69 | 52 | 30.135 | 9.579 | 6.934 | 133.382 | 28.707 | 28.218 | 27.427 | 603.593 | 25.585 | 26.322 | 1278.875 | 27.055 | 27.291 | 38.244 | 27.001 | 2.1 | 1.6 | 0 | 0.5 | 0.1
1144 | 30/07/2025 09:49:30.941 | 98.904 | 74 | 100 | 71 | 52 | 26.461 | 9.438 | 6.935 | 133.121 | 28.674 | 28.221 | 27.395 | 603.46 | 25.581 | 26.331 | 1287.214 | 27.064 | 27.286 | 38.368 | 27.001 | 2 | 1.4 | 0 | 0.2 | 0.1
1145 | 30/07/2025 09:49:32.579 | 98.808 | 73 | 100 | 69 | 52 | 29.817 | 9.497 | 6.936 | 133.276 | 28.677 | 28.24 | 27.415 | 603.556 | 25.592 | 26.332 | 1297.303 | 27.047 | 27.315 | 38.473 | 25.001 | 2 | 1.1 | 0 | 0.2 | 0.1
1146 | 30/07/2025 09:49:34.216 | 99.264 | 76 | 100 | 70 | 52 | 30.27 | 9.588 | 6.936 | 133.202 | 28.68 | 28.234 | 27.384 | 603.277 | 25.592 | 26.343 | 1304.888 | 27.072 | 27.313 | 38.55 | 25.001 | 2 | 1.1 | 0 | 0.2 | 0.1
1147 | 30/07/2025 09:49:35.851 | 99.144 | 73 | 100 | 69 | 52 | 26.765 | 9.574 | 6.935 | 133.348 | 28.687 | 28.232 | 27.396 | 603.212 | 25.598 | 26.34 | 1300.168 | 27.052 | 27.315 | 38.415 | 26.001 | 2.5 | 2.5 | 0.1 | 0 | 0.2
1148 | 30/07/2025 09:49:37.488 | 98.976 | 74 | 100 | 71 | 52 | 27.828 | 9.446 | 6.932 | 133.259 | 28.665 | 28.225 | 27.417 | 603.571 | 25.589 | 26.356 | 1297.355 | 27.073 | 27.301 | 38.343 | 26.001 | 2.5 | 1.8 | 0.1 | 0 | 0.2
1149 | 30/07/2025 09:49:39.122 | 99.216 | 73 | 100 | 71 | 52 | 30.191 | 9.529 | 6.963 | 132.984 | 28.676 | 28.244 | 27.424 | 603.383 | 25.595 | 26.376 | 1304.802 | 27.056 | 27.307 | 38.552 | 27.001 | 2.7 | 0.7 | 1 | 0 | 0.2
1150 | 30/07/2025 09:49:40.756 | 99 | 73 | 100 | 70 | 52 | 26.779 | 9.457 | 6.987 | 133.229 | 28.656 | 28.25 | 27.419 | 602.596 | 25.595 | 26.356 | 1304.985 | 27.044 | 27.323 | 38.375 | 28.001 | 2.7 | 3.5 | 1 | 0 | 0.2
1151 | 30/07/2025 09:49:42.391 | 98.976 | 74 | 100 | 70 | 52 | 30.002 | 9.448 | 6.988 | 133.354 | 28.651 | 28.236 | 27.379 | 602.11 | 25.595 | 26.348 | 1297.483 | 27.069 | 27.306 | 38.57 | 24.001 | 2.3 | 1.8 | 0 | 0.2 | 0.3
1152 | 30/07/2025 09:49:44.026 | 99.096 | 74 | 100 | 72 | 52 | 29.999 | 9.474 | 6.986 | 133.245 | 28.67 | 28.222 | 27.431 | 603.556 | 25.592 | 26.349 | 1290.656 | 27.069 | 27.304 | 38.161 | 24.001 | 2.3 | 1.8 | 0 | 0.2 | 0.3
1153 | 30/07/2025 09:49:45.665 | 99.816 | 76 | 100 | 70 | 53 | 26.39 | 9.48 | 7.005 | 133.139 | 28.663 | 28.24 | 27.41 | 603.592 | 25.581 | 26.355 | 1294.601 | 27.085 | 27.289 | 38.311 | 30.001 | 2.3 | 1.9 | 0 | 0.2 | 0.3
1154 | 30/07/2025 09:49:47.302 | 99.528 | 74 | 100 | 70 | 52 | 28.472 | 9.332 | 7.007 | 133.406 | 28.679 | 28.242 | 27.412 | 603.005 | 25.594 | 26.348 | 1288.061 | 27.035 | 27.318 | 38.571 | 28.001 | 4.3 | 1.5 | 0.1 | 0.5 | 0.4
1155 | 30/07/2025 09:49:48.941 | 99.288 | 74 | 100 | 71 | 52 | 27.124 | 9.43 | 7.008 | 133.232 | 28.665 | 28.236 | 27.396 | 603.315 | 25.583 | 26.359 | 1287.805 | 27.051 | 27.319 | 38.638 | 26.001 | 4.3 | 1.5 | 0.1 | 0.5 | 0.4
1156 | 30/07/2025 09:49:50.577 | 99.576 | 75 | 100 | 70 | 52 | 27.335 | 9.284 | 7.003 | 133.367 | 28.692 | 28.236 | 27.383 | 603.342 | 25.615 | 26.345 | 1289.903 | 27.07 | 27.313 | 38.548 | 26.001 | 4 | 1.4 | 0.6 | 0.6 | 0.3
1157 | 30/07/2025 09:49:52.212 | 99.456 | 72 | 100 | 71 | 52 | 30.158 | 9.281 | 7.005 | 133.157 | 28.68 | 28.216 | 27.415 | 602.271 | 25.584 | 26.338 | 1287.247 | 27.079 | 27.307 | 38.35 | 26.001 | 4 | 1.4 | 0.6 | 0.6 | 0.3
1158 | 30/07/2025 09:49:53.848 | 99.552 | 74 | 100 | 70 | 52 | 29.566 | 9.425 | 7.006 | 133.108 | 28.699 | 28.239 | 27.409 | 602.198 | 25.593 | 26.359 | 1295.452 | 27.071 | 27.3 | 38.466 | 31.001 | 4 | 0.4 | 0.6 | 0.6 | 0.3
1159 | 30/07/2025 09:49:55.482 | 99.36 | 74 | 99 | 69 | 52 | 26.265 | 9.282 | 7.006 | 133.288 | 28.693 | 28.244 | 27.421 | 602.451 | 25.581 | 26.341 | 1297.909 | 27.031 | 27.315 | 38.422 | 26.001 | 2.3 | 2.5 | 0 | 0.6 | 0.2
1160 | 30/07/2025 09:49:57.118 | 99.504 | 74 | 100 | 70 | 53 | 29.016 | 9.432 | 7.006 | 133.239 | 28.688 | 28.237 | 27.365 | 602.182 | 25.567 | 26.348 | 1300.482 | 27.097 | 27.321 | 38.301 | 25.001 | 2.3 | 2.1 | 0 | 0.6 | 0.2
1161 | 30/07/2025 09:49:58.755 | 99 | 74 | 100 | 69 | 52 | 26.88 | 9.437 | 7.005 | 133.227 | 28.686 | 28.233 | 27.39 | 602.199 | 25.566 | 26.34 | 1317.56 | 27.079 | 27.303 | 38.496 | 28.001 | 3.4 | 1.5 | 0.9 | 1.1 | 0.2
1162 | 30/07/2025 09:50:00.390 | 99.504 | 75 | 100 | 70 | 52 | 27.861 | 9.358 | 6.986 | 133.051 | 28.679 | 28.212 | 27.413 | 602.216 | 25.568 | 26.345 | 1319.831 | 27.089 | 27.286 | 38.267 | 31.001 | 3.4 | 1.3 | 0.9 | 1.1 | 0.2
1163 | 30/07/2025 09:50:02.025 | 99.12 | 74 | 100 | 71 | 51 | 30.248 | 9.282 | 6.934 | 133.096 | 28.689 | 28.25 | 27.405 | 602.285 | 25.593 | 26.333 | 1305.083 | 27.053 | 27.302 | 38.738 | 31.001 | 3.4 | 1.3 | 0.9 | 1.1 | 0.2
1164 | 30/07/2025 09:50:03.660 | 98.952 | 74 | 100 | 70 | 52 | 29.234 | 9.43 | 6.953 | 134.726 | 28.679 | 28.246 | 27.414 | 602.24 | 25.581 | 26.323 | 1312.397 | 27.053 | 27.339 | 38.621 | 27.001 | 1.6 | 2.4 | 0 | 1.1 | 0.2
1165 | 30/07/2025 09:50:05.297 | 98.472 | 74 | 100 | 70 | 52 | 26.282 | 9.644 | 7.007 | 134.767 | 28.683 | 28.232 | 27.386 | 602.142 | 25.586 | 26.346 | 1317.747 | 27.069 | 27.305 | 38.766 | 27.001 | 1.6 | 3.1 | 0 | 1.1 | 0.2
1166 | 30/07/2025 09:50:06.936 | 98.616 | 73 | 100 | 71 | 52 | 30.07 | 9.605 | 7.004 | 134.69 | 28.674 | 28.232 | 27.386 | 602.255 | 25.581 | 26.338 | 1317.584 | 27.093 | 27.311 | 38.391 | 29.001 | 2.5 | 1.1 | 0 | 0.5 | 0.2
1167 | 30/07/2025 09:50:08.573 | 98.952 | 73 | 100 | 70 | 52 | 26.493 | 9.471 | 7.002 | 134.583 | 28.694 | 28.22 | 27.405 | 603.399 | 25.607 | 26.35 | 1316.067 | 27.075 | 27.282 | 38.442 | 28.001 | 2.5 | 1.8 | 0 | 0.5 | 0.2
1168 | 30/07/2025 09:50:10.208 | 99.024 | 73 | 100 | 69 | 53 | 28.474 | 9.526 | 7.033 | 134.563 | 28.685 | 28.243 | 27.422 | 602.743 | 25.597 | 26.355 | 1318.897 | 27.05 | 27.313 | 38.637 | 28.001 | 2.5 | 1.8 | 0 | 0.5 | 0.2
1169 | 30/07/2025 09:50:11.843 | 98.352 | 73 | 100 | 71 | 52 | 30.382 | 9.574 | 7.012 | 134.745 | 28.66 | 28.24 | 27.389 | 602.235 | 25.589 | 26.367 | 1307.759 | 27.083 | 27.311 | 38.469 | 26.001 | 3.2 | 0.5 | 1.2 | 0 | 0.2
1170 | 30/07/2025 09:50:13.479 | 98.544 | 74 | 100 | 70 | 52 | 28.458 | 9.426 | 6.935 | 134.919 | 28.68 | 28.229 | 27.4 | 603.342 | 25.605 | 26.357 | 1296.29 | 27.071 | 27.316 | 38.536 | 26.001 | 3.2 | 1.9 | 1.2 | 0 | 0.2
1171 | 30/07/2025 09:50:15.114 | 98.928 | 74 | 100 | 70 | 52 | 26.407 | 9.286 | 6.9 | 134.626 | 28.666 | 28.206 | 27.43 | 603.547 | 25.592 | 26.364 | 1301.536 | 27.077 | 27.306 | 38.089 | 22.001 | 2.1 | 1.4 | 0.3 | 0 | 0.1
1172 | 30/07/2025 09:50:16.749 | 98.376 | 72 | 100 | 70 | 52 | 29.539 | 9.283 | 6.899 | 134.504 | 28.663 | 28.233 | 27.427 | 603.524 | 25.597 | 26.355 | 1307.545 | 27.057 | 27.287 | 38.296 | 29.001 | 2.1 | 1.3 | 0.3 | 0 | 0.1
1173 | 30/07/2025 09:50:18.385 | 98.76 | 73 | 100 | 70 | 52 | 26.27 | 9.434 | 6.865 | 134.538 | 28.658 | 28.257 | 27.402 | 603.484 | 25.585 | 26.363 | 1307.298 | 27.044 | 27.33 | 38.734 | 28.001 | 3 | 0.4 | 0.1 | 0 | 0.1
1174 | 30/07/2025 09:50:20.019 | 99.048 | 74 | 100 | 69 | 51 | 28.984 | 9.576 | 6.866 | 134.917 | 28.657 | 28.24 | 27.391 | 603.344 | 25.592 | 26.35 | 1317.709 | 27.072 | 27.299 | 38.535 | 28.001 | 3 | 0.4 | 0.1 | 0 | 0.1
1175 | 30/07/2025 09:50:21.654 | 98.904 | 73 | 100 | 70 | 52 | 30.353 | 9.496 | 6.899 | 134.804 | 28.677 | 28.226 | 27.412 | 603.466 | 25.583 | 26.348 | 1319.733 | 27.067 | 27.299 | 38.335 | 35.001 | 3 | 1.1 | 0.1 | 0 | 0.1
1176 | 30/07/2025 09:50:23.289 | 98.904 | 73 | 100 | 70 | 52 | 27.857 | 9.582 | 6.934 | 134.488 | 28.684 | 28.23 | 27.41 | 603.585 | 25.578 | 26.357 | 1324.916 | 27.09 | 27.293 | 38.427 | 32.001 | 2.9 | 0.7 | 0.6 | 0.2 | 0.1
1177 | 30/07/2025 09:50:24.926 | 99.024 | 74 | 100 | 70 | 52 | 30.219 | 9.58 | 6.934 | 134.478 | 28.683 | 28.249 | 27.418 | 603.553 | 25.577 | 26.345 | 1332.253 | 27.054 | 27.299 | 38.498 | 27.001 | 2.9 | 1.6 | 0.6 | 0.2 | 0.1
1178 | 30/07/2025 09:50:26.562 | 99.336 | 76 | 100 | 70 | 52 | 29.032 | 9.574 | 6.903 | 134.733 | 28.692 | 28.237 | 27.4 | 603.452 | 25.584 | 26.365 | 1313.139 | 27.054 | 27.311 | 38.564 | 28.001 | 2.7 | 1.9 | 0.6 | 0.5 | 0.1
1179 | 30/07/2025 09:50:28.197 | 99.264 | 75 | 100 | 70 | 52 | 26.233 | 9.433 | 6.892 | 134.887 | 28.701 | 28.239 | 27.384 | 603.357 | 25.588 | 26.341 | 1319.436 | 27.079 | 27.301 | 38.422 | 28.001 | 2.7 | 1.9 | 0.6 | 0.5 | 0.1
1180 | 30/07/2025 09:50:29.832 | 98.616 | 73 | 100 | 71 | 52 | 29.387 | 9.289 | 6.864 | 134.763 | 28.681 | 28.217 | 27.426 | 603.568 | 25.58 | 26.346 | 1331.755 | 27.074 | 27.315 | 38.384 | 26.001 | 2.7 | 3.5 | 0.6 | 0.5 | 0.1
1181 | 30/07/2025 09:50:31.468 | 98.256 | 74 | 100 | 71 | 53 | 30.382 | 9.727 | 6.896 | 134.519 | 28.687 | 28.231 | 27.407 | 603.494 | 25.573 | 26.345 | 1329.395 | 27.056 | 27.292 | 38.386 | 27.001 | 2.9 | 3.4 | 0.2 | 0 | 0.1
1182 | 30/07/2025 09:50:33.104 | 98.28 | 72 | 99 | 71 | 54 | 28.402 | 9.728 | 6.902 | 134.367 | 28.678 | 28.25 | 27.408 | 603.38 | 25.575 | 26.342 | 1319.723 | 27.068 | 27.326 | 38.711 | 29.001 | 2.9 | 0.9 | 0.2 | 0 | 0.1
1183 | 30/07/2025 09:50:34.740 | 97.992 | 72 | 100 | 70 | 53 | 30.299 | 9.456 | 6.9 | 134.883 | 28.693 | 28.241 | 27.404 | 603.385 | 25.578 | 26.345 | 1312.313 | 27.045 | 27.316 | 36.72 | 25.001 | 3.7 | 0.6 | 0.9 | 0.5 | 0.1
1184 | 30/07/2025 09:50:36.377 | 97.632 | 73 | 100 | 70 | 52 | 28.652 | 9.574 | 6.9 | 134.636 | 28.672 | 28.233 | 27.385 | 603.39 | 25.571 | 26.31 | 1315.812 | 27.071 | 27.292 | 38.586 | 23.001 | 3.7 | 1.1 | 0.9 | 0.5 | 0.1
1185 | 30/07/2025 09:50:38.013 | 97.608 | 74 | 99 | 71 | 52 | 26.551 | 9.53 | 6.901 | 134.609 | 28.678 | 28.221 | 27.405 | 603.426 | 25.586 | 26.339 | 1325.019 | 27.077 | 27.288 | 38.314 | 23.001 | 3.7 | 1.1 | 0.9 | 0.5 | 0.1
1186 | 30/07/2025 09:50:39.653 | 97.152 | 72 | 100 | 70 | 52 | 29.902 | 9.463 | 6.899 | 134.548 | 28.704 | 28.248 | 27.432 | 603.632 | 25.598 | 26.331 | 1339.481 | 27.057 | 27.305 | 38.448 | 28.001 | 2.1 | 1.1 | 0.2 | 1.3 | 0.1
1187 | 30/07/2025 09:50:41.288 | 97.008 | 72 | 100 | 70 | 52 | 30.353 | 9.502 | 6.901 | 134.666 | 28.687 | 28.251 | 27.414 | 603.475 | 25.588 | 26.333 | 1337.099 | 27.063 | 27.334 | 38.469 | 30.001 | 2.1 | 2.1 | 0.2 | 1.3 | 0.1
1188 | 30/07/2025 09:50:42.925 | 97.104 | 72 | 100 | 70 | 52 | 29.019 | 9.453 | 6.901 | 134.897 | 28.683 | 28.24 | 27.408 | 603.506 | 25.601 | 26.343 | 1338.76 | 27.059 | 27.305 | 38.388 | 25.001 | 2.3 | 1.7 | 0.6 | 0.5 | 0.1
1189 | 30/07/2025 09:50:44.562 | 96.816 | 72 | 100 | 70 | 52 | 30.434 | 9.646 | 6.901 | 134.646 | 28.68 | 28.243 | 27.391 | 603.364 | 25.594 | 26.354 | 1327.664 | 27.094 | 27.314 | 38.591 | 29.001 | 2.3 | 2.3 | 0.6 | 0.5 | 0.1
1190 | 30/07/2025 09:50:46.199 | 97.488 | 72 | 100 | 70 | 52 | 27.946 | 9.58 | 6.899 | 134.71 | 28.671 | 28.221 | 27.409 | 603.486 | 25.596 | 26.353 | 1346.264 | 27.06 | 27.282 | 38.311 | 29.001 | 2.3 | 2.3 | 0.6 | 0.5 | 0.1
1191 | 30/07/2025 09:50:47.832 | 97.128 | 72 | 100 | 69 | 51 | 26.756 | 9.547 | 6.933 | 134.493 | 28.668 | 28.251 | 27.394 | 603.477 | 25.592 | 26.34 | 1342.516 | 27.052 | 27.308 | 38.703 | 25.001 | 2.5 | 1.1 | 0.9 | 0.5 | 0.2
1192 | 30/07/2025 09:50:49.466 | 97.824 | 73 | 100 | 70 | 53 | 30.001 | 9.335 | 6.936 | 134.755 | 28.656 | 28.237 | 27.383 | 603.328 | 25.584 | 26.361 | 1340.14 | 27.067 | 27.314 | 38.546 | 26.001 | 2.5 | 1.7 | 0.9 | 0.5 | 0.2
1193 | 30/07/2025 09:50:51.102 | 98.256 | 73 | 100 | 70 | 52 | 26.246 | 9.431 | 6.936 | 134.771 | 28.669 | 28.241 | 27.4 | 603.342 | 25.587 | 26.359 | 1330.539 | 27.073 | 27.313 | 38.659 | 33.001 | 2.4 | 1.5 | 0.9 | 0.8 | 0.2
1194 | 30/07/2025 09:50:52.742 | 97.152 | 73 | 100 | 71 | 53 | 29.449 | 9.351 | 6.937 | 134.546 | 28.647 | 28.216 | 27.402 | 603.382 | 25.596 | 26.369 | 1315.918 | 27.075 | 27.304 | 38.449 | 32.001 | 2.4 | 2.6 | 0.9 | 0.8 | 0.2
1195 | 30/07/2025 09:50:54.379 | 97.272 | 74 | 100 | 70 | 52 | 30.434 | 9.433 | 6.933 | 134.626 | 28.672 | 28.234 | 27.414 | 603.577 | 25.593 | 26.34 | 1317.661 | 27.063 | 27.288 | 38.358 | 27.001 | 3 | 1.1 | 0.7 | 0.2 | 0.2
1196 | 30/07/2025 09:50:56.009 | 97.584 | 73 | 100 | 70 | 52 | 27.354 | 9.578 | 6.936 | 134.575 | 28.67 | 28.252 | 27.407 | 603.438 | 25.587 | 26.356 | 1315.464 | 27.045 | 27.314 | 38.653 | 27.001 | 3 | 1.1 | 0.7 | 0.2 | 0.2
1197 | 30/07/2025 09:50:57.649 | 97.512 | 72 | 100 | 71 | 52 | 27.275 | 9.579 | 6.935 | 134.819 | 28.676 | 28.234 | 27.394 | 603.221 | 25.594 | 26.359 | 1319.347 | 27.058 | 27.306 | 38.444 | 32.001 | 3 | 0.6 | 0.7 | 0.2 | 0.2
1198 | 30/07/2025 09:50:59.286 | 97.464 | 72 | 100 | 71 | 52 | 30.146 | 9.579 | 6.987 | 133.26 | 28.672 | 28.229 | 27.399 | 603.314 | 25.57 | 26.352 | 1326.548 | 27.067 | 27.31 | 38.259 | 31.001 | 2.3 | 0 | 0.6 | 1.7 | 0.2
1199 | 30/07/2025 09:51:00.920 | 96.768 | 71 | 100 | 70 | 53 | 26.41 | 9.432 | 6.985 | 133.257 | 28.708 | 28.22 | 27.433 | 603.474 | 25.596 | 26.355 | 1324.926 | 27.057 | 27.301 | 38.219 | 29.001 | 2.3 | 1.8 | 0.6 | 1.7 | 0.2
1200 | 30/07/2025 09:51:02.557 | 96.672 | 71 | 100 | 71 | 52 | 29.763 | 9.355 | 6.986 | 132.888 | 28.685 | 28.25 | 27.408 | 603.437 | 25.589 | 26.345 | 1322.171 | 27.068 | 27.305 | 38.396 | 23.001 | 2.3 | 2.8 | 0.9 | 0.2 | 0.3
1201 | 30/07/2025 09:51:04.195 | 96.96 | 73 | 100 | 70 | 52 | 30.277 | 9.488 | 6.95 | 133.11 | 28.685 | 28.242 | 27.401 | 603.381 | 25.579 | 26.364 | 1322.84 | 27.032 | 27.307 | 38.693 | 23.001 | 2.3 | 2.8 | 0.9 | 0.2 | 0.3
1202 | 30/07/2025 09:51:05.828 | 97.584 | 73 | 100 | 71 | 52 | 26.81 | 9.506 | 6.935 | 133.279 | 28.69 | 28.246 | 27.365 | 603.535 | 25.568 | 26.327 | 1321.96 | 27.075 | 27.301 | 38.469 | 21.001 | 2.3 | 0.8 | 0.9 | 0.2 | 0.3
1203 | 30/07/2025 09:51:07.463 | 98.256 | 73 | 100 | 71 | 52 | 27.811 | 9.432 | 6.987 | 132.979 | 28.692 | 28.221 | 27.407 | 603.538 | 25.57 | 26.341 | 1311.146 | 27.085 | 27.313 | 38.38 | 26.001 | 3.6 | 1 | 0.1 | 0 | 0.3
1204 | 30/07/2025 09:51:09.099 | 98.856 | 74 | 100 | 70 | 53 | 30.224 | 9.424 | 6.952 | 133.057 | 28.686 | 28.229 | 27.407 | 603.398 | 25.584 | 26.328 | 1307.355 | 27.069 | 27.276 | 38.449 | 24.001 | 3.6 | 1.5 | 0.1 | 0 | 0.3
1205 | 30/07/2025 09:51:10.736 | 98.832 | 74 | 100 | 71 | 52 | 26.912 | 9.434 | 6.937 | 132.843 | 28.821 | 28.243 | 27.403 | 603.402 | 25.576 | 26.336 | 1307.372 | 27.065 | 27.31 | 38.619 | 27.001 | 2.8 | 1.5 | 0.6 | 0.4 | 0.3
1206 | 30/07/2025 09:51:12.372 | 99.48 | 72 | 100 | 70 | 51 | 30.058 | 9.426 | 6.966 | 133.344 | 28.835 | 28.235 | 27.408 | 603.481 | 25.593 | 26.335 | 1315.182 | 27.036 | 27.308 | 38.648 | 28.001 | 2.8 | 1.2 | 0.6 | 0.4 | 0.3
1207 | 30/07/2025 09:51:14.007 | 99.336 | 74 | 100 | 71 | 52 | 30.13 | 9.505 | 6.987 | 133.304 | 28.814 | 28.237 | 27.394 | 603.408 | 25.58 | 26.339 | 1316.953 | 27.081 | 27.32 | 38.501 | 28.001 | 2.8 | 1.2 | 0.6 | 0.4 | 0.3
1208 | 30/07/2025 09:51:15.643 | 99.888 | 74 | 100 | 70 | 52 | 26.489 | 9.507 | 6.935 | 133.077 | 28.826 | 28.215 | 27.395 | 603.416 | 25.605 | 26.359 | 1310.107 | 27.079 | 27.298 | 38.371 | 29.001 | 3.2 | 0.7 | 0.7 | 0.5 | 0.3
1209 | 30/07/2025 09:51:17.281 | 99.528 | 74 | 100 | 71 | 52 | 28.515 | 9.502 | 6.934 | 133.088 | 28.821 | 28.246 | 27.414 | 603.626 | 25.595 | 26.351 | 1303.723 | 27.052 | 27.295 | 38.451 | 26.001 | 3.2 | 1.8 | 0.7 | 0.5 | 0.3
1210 | 30/07/2025 09:51:18.916 | 98.928 | 74 | 100 | 71 | 51 | 27.292 | 9.427 | 6.936 | 133.067 | 28.804 | 28.239 | 27.395 | 603.295 | 25.579 | 26.353 | 1302.278 | 27.031 | 27.302 | 38.656 | 25.001 | 1 | 2.1 | 0.7 | 0.5 | 0.3
1211 | 30/07/2025 09:51:20.550 | 99.36 | 74 | 100 | 71 | 52 | 27.3 | 9.577 | 6.935 | 133.299 | 28.812 | 28.245 | 27.412 | 602.314 | 25.593 | 26.354 | 1304.923 | 27.055 | 27.299 | 38.464 | 27.001 | 1 | 0.6 | 0.7 | 0.5 | 0.3
1212 | 30/07/2025 09:51:22.186 | 99.648 | 74 | 100 | 70 | 53 | 30.2 | 9.577 | 6.936 | 133.235 | 28.815 | 28.226 | 27.387 | 602.178 | 25.591 | 26.361 | 1312.194 | 27.097 | 27.313 | 38.384 | 27.001 | 1 | 0.6 | 0.7 | 0.5 | 0.3
1213 | 30/07/2025 09:51:23.821 | 99.792 | 74 | 100 | 70 | 52 | 29.681 | 9.583 | 6.984 | 133.2 | 28.815 | 28.226 | 27.526 | 602.215 | 25.601 | 26.354 | 1309.565 | 27.061 | 27.281 | 38.382 | 26.001 | 3.1 | 1.1 | 0.6 | 1.4 | 0.2
1214 | 30/07/2025 09:51:25.458 | 99.936 | 74 | 100 | 69 | 52 | 26.29 | 9.504 | 6.988 | 133.09 | 28.796 | 28.241 | 27.57 | 602.23 | 25.574 | 26.353 | 1302.059 | 27.05 | 27.309 | 38.504 | 23.001 | 3.1 | 2.4 | 0.6 | 1.4 | 0.2
1215 | 30/07/2025 09:51:27.092 | 99.672 | 76 | 100 | 70 | 52 | 30.363 | 9.57 | 6.987 | 133.351 | 28.805 | 28.245 | 27.409 | 602.286 | 25.594 | 26.352 | 1293.33 | 27.022 | 27.313 | 38.589 | 27.001 | 4.4 | 1 | 0.9 | 1.2 | 0.2
1216 | 30/07/2025 09:51:28.727 | 99.384 | 74 | 100 | 70 | 52 | 26.856 | 9.584 | 7 | 133.043 | 28.798 | 28.257 | 27.402 | 602.222 | 25.577 | 26.352 | 1287.562 | 27.071 | 27.328 | 38.621 | 25.001 | 4.4 | 1.8 | 0.9 | 1.2 | 0.2
1217 | 30/07/2025 09:51:30.363 | 98.88 | 74 | 100 | 71 | 52 | 27.853 | 9.717 | 7.005 | 133.212 | 28.82 | 28.212 | 27.394 | 602.143 | 25.59 | 26.354 | 1300.104 | 27.068 | 27.31 | 38.502 | 30.001 | 3.2 | 1.7 | 0 | 0.6 | 0.2
1218 | 30/07/2025 09:51:31.999 | 98.976 | 74 | 100 | 70 | 52 | 30.239 | 9.578 | 7.005 | 133.02 | 28.836 | 28.231 | 27.581 | 602.304 | 25.58 | 26.344 | 1311.366 | 27.058 | 27.288 | 38.208 | 30.001 | 3.2 | 1.7 | 0 | 0.6 | 0.2
1219 | 30/07/2025 09:51:33.636 | 99.144 | 75 | 100 | 71 | 52 | 29.01 | 9.428 | 7.007 | 133.087 | 28.828 | 28.251 | 27.562 | 602.193 | 25.585 | 26.356 | 1307.372 | 27.058 | 27.308 | 38.749 | 23.001 | 3.2 | 1.2 | 0 | 0.6 | 0.2
1220 | 30/07/2025 09:51:35.276 | 99.456 | 73 | 100 | 70 | 51 | 26.262 | 9.577 | 7.005 | 134.731 | 28.846 | 28.236 | 27.54 | 601.977 | 25.605 | 26.347 | 1297.926 | 27.059 | 27.294 | 38.82 | 27.001 | 2.8 | 1.8 | 0 | 0.6 | 0.2
1221 | 30/07/2025 09:51:36.926 | 99.048 | 73 | 100 | 70 | 53 | 30.025 | 9.516 | 7.006 | 134.54 | 28.843 | 28.242 | 27.524 | 600.725 | 25.577 | 26.354 | 1302.021 | 27.09 | 27.308 | 38.447 | 28.001 | 2.8 | 0.8 | 0 | 0.6 | 0.2
1222 | 30/07/2025 09:51:38.563 | 99.024 | 73 | 100 | 71 | 52 | 26.449 | 9.481 | 6.986 | 134.695 | 28.842 | 28.221 | 27.575 | 600.841 | 25.586 | 26.347 | 1307.497 | 27.061 | 27.3 | 38.339 | 25.001 | 2.6 | 1 | 0 | 1.2 | 0.1
1223 | 30/07/2025 09:51:40.196 | 98.616 | 74 | 100 | 70 | 51 | 28.367 | 9.583 | 6.986 | 134.404 | 28.834 | 28.243 | 27.559 | 600.776 | 25.568 | 26.339 | 1306.635 | 27.063 | 27.305 | 38.317 | 25.001 | 2.6 | 1 | 0 | 1.2 | 0.1
1224 | 30/07/2025 09:51:41.831 | 98.016 | 74 | 100 | 71 | 52 | 30.375 | 9.579 | 6.988 | 134.62 | 28.822 | 28.238 | 27.563 | 600.74 | 25.566 | 26.331 | 1312.243 | 27.031 | 27.308 | 38.617 | 24.001 | 2.6 | 1.1 | 0 | 1.2 | 0.1
1225 | 30/07/2025 09:51:43.466 | 98.112 | 74 | 100 | 70 | 53 | 28.523 | 9.577 | 6.987 | 134.883 | 28.825 | 28.239 | 27.548 | 600.818 | 25.581 | 26.316 | 1309.741 | 27.06 | 27.306 | 38.483 | 29.001 | 2 | 1.5 | 0.9 | 0.6 | 0.2
1226 | 30/07/2025 09:51:45.102 | 98.16 | 74 | 100 | 71 | 51 | 30.194 | 9.58 | 6.969 | 134.7 | 28.834 | 28.227 | 27.537 | 600.555 | 25.58 | 26.339 | 1311.925 | 27.079 | 27.307 | 38.485 | 27.001 | 2 | 0.7 | 0.9 | 0.6 | 0.2
1227 | 30/07/2025 09:51:46.739 | 98.328 | 74 | 100 | 70 | 52 | 29.693 | 9.428 | 6.934 | 134.721 | 28.828 | 28.22 | 27.575 | 600.883 | 25.582 | 26.332 | 1317.365 | 27.063 | 27.29 | 38.331 | 25.001 | 3 | 1.4 | 0.6 | 0.5 | 0.1
1228 | 30/07/2025 09:51:48.373 | 98.232 | 73 | 100 | 70 | 52 | 26.256 | 9.429 | 6.937 | 134.319 | 28.819 | 28.242 | 27.556 | 600.654 | 25.583 | 26.352 | 1324.612 | 27.076 | 27.303 | 38.391 | 22.001 | 3 | 0.4 | 0.6 | 0.5 | 0.1
1229 | 30/07/2025 09:51:50.011 | 98.376 | 74 | 100 | 71 | 52 | 29.019 | 9.286 | 6.924 | 134.845 | 28.84 | 28.242 | 27.559 | 600.87 | 25.607 | 26.341 | 1320.908 | 27.034 | 27.312 | 38.612 | 22.001 | 3 | 0.4 | 0.6 | 0.5 | 0.1
1230 | 30/07/2025 09:51:51.646 | 97.8 | 72 | 100 | 70 | 53 | 30.415 | 9.396 | 6.865 | 134.723 | 28.813 | 28.238 | 27.537 | 599.421 | 25.594 | 26.343 | 1314.99 | 27.075 | 27.315 | 38.414 | 29.001 | 2.3 | 2.8 | 0.9 | 0.5 | 0.2
1231 | 30/07/2025 09:51:53.282 | 97.752 | 72 | 100 | 71 | 52 | 28.01 | 9.504 | 6.899 | 134.654 | 28.82 | 28.218 | 27.563 | 598.323 | 25.59 | 26.35 | 1302.661 | 27.071 | 27.283 | 38.278 | 28.001 | 2.3 | 1.3 | 0.9 | 0.5 | 0.2
1232 | 30/07/2025 09:51:54.917 | 97.272 | 73 | 100 | 70 | 50 | 30.305 | 9.435 | 6.9 | 134.504 | 28.812 | 28.23 | 27.57 | 598.353 | 25.589 | 26.36 | 1299.464 | 27.074 | 27.312 | 38.182 | 28.001 | 2.3 | 1.3 | 0.2 | 1.1 | 0.2
1233 | 30/07/2025 09:51:56.554 | 97.272 | 70 | 100 | 71 | 52 | 29.191 | 9.432 | 6.937 | 134.646 | 28.81 | 28.243 | 27.563 | 598.255 | 25.595 | 26.37 | 1297.628 | 27.033 | 27.309 | 38.453 | 26.001 | 2.3 | 0.9 | 0.2 | 1.1 | 0.2
1234 | 30/07/2025 09:51:58.190 | 96.648 | 71 | 100 | 70 | 51 | 26.275 | 9.307 | 6.935 | 134.828 | 28.809 | 28.241 | 27.561 | 598.282 | 25.589 | 26.351 | 1299.016 | 27.051 | 27.307 | 38.419 | 26.001 | 2.3 | 0.9 | 0.2 | 1.1 | 0.2
1235 | 30/07/2025 09:51:59.829 | 96.024 | 71 | 100 | 69 | 52 | 29.591 | 9.284 | 6.936 | 134.549 | 28.801 | 28.226 | 27.549 | 598.712 | 25.591 | 26.368 | 1294.884 | 27.097 | 27.308 | 38.335 | 27.001 | 2.6 | 2.9 | 0.9 | 0 | 0.2
1236 | 30/07/2025 09:52:01.463 | 96.336 | 71 | 100 | 70 | 52 | 30.439 | 9.502 | 6.933 | 134.72 | 28.821 | 28.22 | 27.58 | 599.655 | 25.607 | 26.349 | 1292.67 | 27.061 | 27.284 | 38.21 | 27.001 | 2.6 | 1.4 | 0.9 | 0 | 0.2
1237 | 30/07/2025 09:52:03.097 | 96.192 | 73 | 100 | 71 | 53 | 28.498 | 9.58 | 6.936 | 134.471 | 28.814 | 28.236 | 27.557 | 600.736 | 25.585 | 26.361 | 1297.468 | 27.072 | 27.291 | 38.302 | 28.001 | 2.4 | 0.8 | 2.2 | 0.6 | 0.2
1238 | 30/07/2025 09:52:04.732 | 96.096 | 72 | 100 | 71 | 53 | 30.401 | 9.428 | 6.985 | 134.634 | 28.827 | 28.252 | 27.564 | 600.911 | 25.601 | 26.35 | 1297.233 | 27.036 | 27.317 | 38.551 | 30.001 | 2.4 | 0.9 | 2.2 | 0.6 | 0.2
1239 | 30/07/2025 09:52:06.369 | 96.888 | 72 | 100 | 71 | 52 | 28.638 | 9.578 | 6.988 | 134.624 | 28.833 | 28.254 | 27.538 | 600.795 | 25.577 | 26.351 | 1300.043 | 27.071 | 27.322 | 38.475 | 25.001 | 2.6 | 1 | 0.6 | 0.5 | 0.2
1240 | 30/07/2025 09:52:08.010 | 96.912 | 74 | 100 | 70 | 52 | 26.51 | 9.128 | 6.988 | 134.835 | 28.832 | 28.216 | 27.553 | 600.735 | 25.584 | 26.359 | 1302.954 | 27.075 | 27.3 | 38.479 | 25.001 | 2.6 | 1 | 0.6 | 0.5 | 0.2
1241 | 30/07/2025 09:52:09.646 | 96.984 | 71 | 100 | 70 | 52 | 29.829 | 9.45 | 7.029 | 134.527 | 28.83 | 28.238 | 27.579 | 600.817 | 25.585 | 26.347 | 1302.39 | 27.063 | 27.296 | 38.222 | 26.001 | 2.6 | 1.2 | 0.6 | 0.5 | 0.2
1242 | 30/07/2025 09:52:11.280 | 97.584 | 72 | 100 | 70 | 52 | 30.344 | 9.284 | 7.035 | 134.379 | 28.822 | 28.249 | 27.547 | 600.7 | 25.56 | 26.354 | 1307.582 | 27.052 | 27.306 | 38.82 | 26.001 | 3 | 0.8 | 0.6 | 0.6 | 0.2
1243 | 30/07/2025 09:52:12.917 | 97.848 | 72 | 100 | 71 | 52 | 28.858 | 9.295 | 7.036 | 134.684 | 28.826 | 28.25 | 27.55 | 600.858 | 25.56 | 26.328 | 1302.703 | 27.039 | 27.315 | 38.714 | 28.001 | 3 | 1 | 0.6 | 0.6 | 0.2
1244 | 30/07/2025 09:52:14.553 | 97.584 | 74 | 100 | 70 | 53 | 30.468 | 9.281 | 7.029 | 134.487 | 28.82 | 28.239 | 27.541 | 600.616 | 25.574 | 26.349 | 1316.929 | 27.07 | 27.31 | 38.606 | 25.001 | 3.9 | 1.1 | 0 | 0.8 | 0.2
1245 | 30/07/2025 09:52:16.190 | 98.208 | 71 | 100 | 70 | 52 | 27.943 | 9.43 | 6.985 | 133.3 | 28.849 | 28.218 | 27.578 | 600.926 | 25.58 | 26.331 | 1324.721 | 27.059 | 27.303 | 38.345 | 25.001 | 3.9 | 1.1 | 0 | 0.8 | 0.2
1246 | 30/07/2025 09:52:17.825 | 98.544 | 73 | 100 | 71 | 53 | 26.85 | 9.456 | 6.936 | 132.866 | 28.82 | 28.248 | 27.562 | 600.768 | 25.575 | 26.325 | 1314.814 | 27.076 | 27.297 | 38.256 | 23.001 | 3.9 | 1.7 | 0 | 0.8 | 0.2
1247 | 30/07/2025 09:52:19.458 | 98.664 | 72 | 100 | 71 | 53 | 30.07 | 9.424 | 6.937 | 133.35 | 28.84 | 28.238 | 27.567 | 600.757 | 25.587 | 26.329 | 1317.596 | 27.04 | 27.309 | 38.664 | 26.001 | 1.6 | 1.6 | 0.7 | 0.8 | 0.2
1248 | 30/07/2025 09:52:21.089 | 98.904 | 74 | 100 | 71 | 52 | 26.347 | 9.431 | 6.935 | 133.176 | 28.827 | 28.247 | 27.55 | 600.751 | 25.583 | 26.328 | 1310.557 | 27.062 | 27.32 | 38.556 | 23.001 | 1.6 | 2.3 | 0.7 | 0.8 | 0.2
1249 | 30/07/2025 09:52:22.725 | 98.352 | 72 | 100 | 71 | 52 | 29.541 | 9.307 | 6.935 | 133.365 | 28.82 | 28.234 | 27.524 | 600.648 | 25.592 | 26.334 | 1310.038 | 27.08 | 27.307 | 38.469 | 21.001 | 1.8 | 2.9 | 0 | 0.5 | 0.2
1250 | 30/07/2025 09:52:24.361 | 98.784 | 74 | 100 | 71 | 53 | 30.425 | 9.465 | 6.934 | 133.294 | 28.81 | 28.22 | 27.573 | 600.859 | 25.584 | 26.348 | 1309.922 | 27.067 | 27.289 | 38.253 | 21.001 | 1.8 | 1.4 | 0 | 0.5 | 0.2
1251 | 30/07/2025 09:52:25.997 | 98.976 | 74 | 100 | 70 | 52 | 27.334 | 9.533 | 6.938 | 132.939 | 28.823 | 28.239 | 27.538 | 600.875 | 25.586 | 26.369 | 1309.222 | 27.066 | 27.296 | 38.381 | 21.001 | 1.8 | 1.4 | 0 | 0.5 | 0.2
1252 | 30/07/2025 09:52:27.635 | 98.952 | 73 | 100 | 70 | 53 | 27.281 | 9.495 | 6.935 | 133.3 | 28.816 | 28.24 | 27.55 | 600.83 | 25.595 | 26.338 | 1315.56 | 27.032 | 27.31 | 38.525 | 29.001 | 3.9 | 1.1 | 0 | 0 | 0.3
1253 | 30/07/2025 09:52:29.270 | 98.64 | 74 | 100 | 70 | 51 | 28.593 | 9.576 | 6.937 | 133.203 | 28.809 | 28.243 | 27.533 | 600.665 | 25.59 | 26.371 | 1312.753 | 27.05 | 27.302 | 38.533 | 23.001 | 3.9 | 2.5 | 0 | 0 | 0.3
1254 | 30/07/2025 09:52:30.906 | 98.712 | 73 | 100 | 71 | 52 | 26.531 | 9.437 | 6.935 | 133.326 | 28.812 | 28.228 | 27.549 | 602.191 | 25.593 | 26.35 | 1309.872 | 27.068 | 27.303 | 38.444 | 26.001 | 1.8 | 2.9 | 0.6 | 0.1 | 0.2
1255 | 30/07/2025 09:52:32.541 | 98.256 | 73 | 100 | 70 | 52 | 29.899 | 9.583 | 6.933 | 133.002 | 28.795 | 28.225 | 27.579 | 600.949 | 25.583 | 26.354 | 1304.846 | 27.086 | 27.283 | 38.437 | 28.001 | 1.8 | 2.7 | 0.6 | 0.1 | 0.2
1256 | 30/07/2025 09:52:34.176 | 97.992 | 74 | 100 | 70 | 51 | 30.379 | 9.575 | 6.935 | 133.264 | 28.81 | 28.248 | 27.547 | 600.776 | 25.593 | 26.349 | 1297.398 | 27.05 | 27.305 | 38.579 | 28.001 | 1.8 | 2.7 | 0.6 | 0.1 | 0.2
1257 | 30/07/2025 09:52:35.809 | 98.04 | 73 | 100 | 71 | 52 | 26.956 | 9.543 | 6.934 | 133.357 | 28.809 | 28.25 | 27.556 | 602.267 | 25.589 | 26.352 | 1301.87 | 27.047 | 27.324 | 38.528 | 26.001 | 2 | 1.7 | 1 | 0.5 | 0.2
1258 | 30/07/2025 09:52:37.445 | 98.328 | 76 | 100 | 70 | 50 | 27.981 | 9.56 | 6.868 | 133.111 | 28.823 | 28.233 | 27.531 | 601.982 | 25.576 | 26.362 | 1302.416 | 27.083 | 27.311 | 38.438 | 23.001 | 2 | 1.8 | 1 | 0.5 | 0.2
1259 | 30/07/2025 09:52:39.083 | 99.168 | 73 | 100 | 70 | 52 | 27.984 | 9.684 | 6.865 | 133.301 | 28.811 | 28.221 | 27.559 | 602.311 | 25.589 | 26.344 | 1304.6 | 27.073 | 27.308 | 38.317 | 29.001 | 3.2 | 0.4 | 0.9 | 0 | 0.2
1260 | 30/07/2025 09:52:40.727 | 99.12 | 74 | 100 | 70 | 53 | 26.907 | 9.578 | 6.866 | 133.085 | 28.827 | 28.232 | 27.565 | 602.278 | 25.58 | 26.358 | 1307.189 | 27.057 | 27.303 | 38.282 | 30.001 | 3.2 | 1.2 | 0.9 | 0 | 0.2
1261 | 30/07/2025 09:52:42.362 | 98.88 | 74 | 100 | 70 | 52 | 30.106 | 9.449 | 6.883 | 133.295 | 28.836 | 28.244 | 27.579 | 602.322 | 25.587 | 26.346 | 1311.336 | 27.033 | 27.319 | 38.452 | 25.001 | 3 | 0.3 | 0.9 | 0.3 | 0.3
1262 | 30/07/2025 09:52:43.996 | 99.48 | 75 | 100 | 70 | 52 | 30.078 | 9.524 | 6.901 | 133.107 | 28.829 | 28.25 | 27.542 | 600.754 | 25.579 | 26.349 | 1307.201 | 27.08 | 27.321 | 38.619 | 25.001 | 3 | 0.3 | 0.9 | 0.3 | 0.3
1263 | 30/07/2025 09:52:45.634 | 99.072 | 75 | 100 | 71 | 54 | 26.561 | 9.495 | 6.9 | 133.343 | 28.826 | 28.228 | 27.538 | 600.847 | 25.587 | 26.353 | 1314.786 | 27.066 | 27.305 | 38.542 | 27.001 | 3 | 3.1 | 0.9 | 0.3 | 0.3
1264 | 30/07/2025 09:52:47.273 | 98.784 | 73 | 100 | 70 | 52 | 28.343 | 9.284 | 6.9 | 133.105 | 28.826 | 28.227 | 27.574 | 600.711 | 25.565 | 26.33 | 1305.9 | 27.068 | 27.289 | 38.272 | 31.001 | 2.3 | 1.4 | 0.9 | 0.5 | 0.4
1265 | 30/07/2025 09:52:48.908 | 98.784 | 74 | 100 | 70 | 52 | 27.438 | 9.282 | 6.898 | 133.302 | 28.84 | 28.243 | 27.558 | 601.995 | 25.596 | 26.341 | 1298.687 | 27.057 | 27.278 | 38.581 | 28.001 | 2.3 | 1.9 | 0.9 | 0.5 | 0.4
1266 | 30/07/2025 09:52:50.543 | 98.808 | 74 | 100 | 70 | 52 | 27.262 | 9.429 | 6.869 | 133.134 | 28.818 | 28.257 | 27.567 | 602.253 | 25.57 | 26.328 | 1297.408 | 27.038 | 27.334 | 38.536 | 25.001 | 1.9 | 2.1 | 0 | 0.5 | 0.4
1267 | 30/07/2025 09:52:52.177 | 99.072 | 73 | 100 | 71 | 52 | 30.216 | 9.499 | 6.866 | 133.365 | 28.82 | 28.24 | 27.539 | 602.085 | 25.577 | 26.32 | 1291.039 | 27.072 | 27.308 | 38.578 | 25.001 | 1.9 | 2.1 | 0 | 0.5 | 0.4
1268 | 30/07/2025 09:52:53.810 | 98.256 | 73 | 100 | 70 | 52 | 29.687 | 9.482 | 6.865 | 133.229 | 28.823 | 28.223 | 27.573 | 602.275 | 25.583 | 26.331 | 1287.959 | 27.068 | 27.303 | 38.477 | 24.001 | 1.9 | 2 | 0 | 0.5 | 0.4
1269 | 30/07/2025 09:52:55.445 | 98.232 | 74 | 100 | 71 | 53 | 26.289 | 9.716 | 6.908 | 133.034 | 28.818 | 28.242 | 27.555 | 602.243 | 25.586 | 26.336 | 1290.122 | 27.079 | 27.295 | 38.378 | 25.001 | 2.4 | 2.9 | 1.2 | 0.2 | 0.3
1270 | 30/07/2025 09:52:57.080 | 98.352 | 73 | 100 | 71 | 53 | 30.338 | 9.58 | 6.935 | 133.193 | 28.812 | 28.247 | 27.565 | 602.255 | 25.584 | 26.326 | 1289.972 | 27.045 | 27.298 | 38.482 | 26.001 | 2.4 | 1.1 | 1.2 | 0.2 | 0.3
1271 | 30/07/2025 09:52:58.714 | 99.264 | 74 | 100 | 70 | 52 | 26.812 | 9.58 | 6.895 | 133.388 | 28.823 | 28.243 | 27.547 | 602.161 | 25.594 | 26.34 | 1285.803 | 27.064 | 27.319 | 38.508 | 25.001 | 2.8 | 2.5 | 0.6 | 1.1 | 0.3
1272 | 30/07/2025 09:53:00.352 | 99.576 | 74 | 100 | 71 | 52 | 27.782 | 9.577 | 6.865 | 133.373 | 28.829 | 28.238 | 27.529 | 602.137 | 25.591 | 26.359 | 1297.43 | 27.073 | 27.303 | 38.488 | 23.001 | 2.8 | 2.2 | 0.6 | 1.1 | 0.3
1273 | 30/07/2025 09:53:01.989 | 99.816 | 74 | 100 | 71 | 53 | 30.27 | 9.581 | 6.899 | 133.324 | 28.811 | 28.221 | 27.576 | 602.279 | 25.578 | 26.354 | 1296.494 | 27.072 | 27.303 | 38.274 | 23.001 | 2.8 | 2.2 | 0.6 | 1.1 | 0.3
1274 | 30/07/2025 09:53:03.623 | 100.08 | 74 | 100 | 71 | 52 | 29.134 | 9.509 | 6.928 | 133.016 | 28.806 | 28.242 | 27.561 | 602.16 | 25.585 | 26.367 | 1309.563 | 27.069 | 27.291 | 38.426 | 24.001 | 1.8 | 0.9 | 0.3 | 0.8 | 0.3
1275 | 30/07/2025 09:53:05.257 | 100.008 | 76 | 100 | 71 | 52 | 26.245 | 9.499 | 6.936 | 133.303 | 28.81 | 28.244 | 27.565 | 602.432 | 25.592 | 26.349 | 1318.357 | 27.032 | 27.312 | 38.417 | 24.001 | 1.8 | 1.7 | 0.3 | 0.8 | 0.3
1276 | 30/07/2025 09:53:06.897 | 100.008 | 74 | 100 | 70 | 53 | 30.136 | 9.429 | 6.937 | 133.434 | 28.812 | 28.239 | 27.549 | 602.123 | 25.596 | 26.366 | 1325.95 | 27.056 | 27.307 | 38.657 | 23.001 | 2.5 | 1.4 | 1.5 | 0.6 | 0.3
1277 | 30/07/2025 09:53:08.530 | 99.312 | 77 | 100 | 71 | 52 | 26.551 | 9.285 | 6.935 | 133.369 | 28.802 | 28.232 | 27.551 | 602.157 | 25.581 | 26.33 | 1334.203 | 27.071 | 27.307 | 38.42 | 24.001 | 2.5 | 0.8 | 1.5 | 0.6 | 0.3
1278 | 30/07/2025 09:53:10.167 | 99.648 | 75 | 100 | 70 | 50 | 28.539 | 9.286 | 6.933 | 133.1 | 28.811 | 28.222 | 27.584 | 602.29 | 25.59 | 26.356 | 1335.432 | 27.081 | 27.309 | 38.218 | 24.001 | 2.5 | 0.8 | 1.5 | 0.6 | 0.3
1279 | 30/07/2025 09:53:11.803 | 100.248 | 76 | 100 | 70 | 52 | 30.371 | 9.536 | 6.962 | 133.147 | 28.823 | 28.247 | 27.55 | 602.287 | 25.596 | 26.351 | 1343.673 | 27.04 | 27.293 | 38.495 | 23.001 | 3.7 | 1.6 | 0 | 2 | 0.3
1280 | 30/07/2025 09:53:13.434 | 101.088 | 77 | 100 | 70 | 52 | 28.607 | 9.425 | 7.005 | 133.291 | 28.831 | 28.246 | 27.546 | 602.215 | 25.59 | 26.348 | 1342.125 | 27.052 | 27.322 | 38.404 | 25.001 | 3.7 | 0.6 | 0 | 2 | 0.3
1281 | 30/07/2025 09:53:15.068 | 100.608 | 74 | 99 | 71 | 51 | 30.21 | 9.425 | 7.004 | 133.298 | 28.832 | 28.244 | 27.554 | 600.751 | 25.599 | 26.356 | 1337.654 | 27.061 | 27.304 | 38.421 | 29.001 | 3 | 1.7 | 0 | 0 | 0.3
1282 | 30/07/2025 09:53:16.702 | 100.632 | 76 | 100 | 70 | 52 | 29.714 | 9.582 | 7.005 | 133.17 | 28.818 | 28.227 | 27.556 | 600.83 | 25.578 | 26.336 | 1327.436 | 27.088 | 27.314 | 38.412 | 25.001 | 3 | 2.1 | 0 | 0 | 0.3
1283 | 30/07/2025 09:53:18.336 | 100.296 | 75 | 100 | 71 | 52 | 26.317 | 9.426 | 6.986 | 133.193 | 28.822 | 28.231 | 27.561 | 600.782 | 25.583 | 26.35 | 1344.541 | 27.065 | 27.289 | 38.31 | 29.001 | 2.3 | 1.2 | 0.6 | 0.5 | 0.3
1284 | 30/07/2025 09:53:19.974 | 100.44 | 77 | 100 | 69 | 52 | 29.007 | 9.574 | 6.961 | 133.268 | 28.837 | 28.238 | 27.575 | 600.93 | 25.585 | 26.336 | 1342.105 | 27.039 | 27.322 | 38.596 | 29.001 | 2.3 | 1.2 | 0.6 | 0.5 | 0.3
1285 | 30/07/2025 09:53:21.607 | 100.44 | 77 | 100 | 70 | 52 | 30.483 | 9.585 | 6.935 | 133.203 | 28.827 | 28.235 | 27.527 | 602.118 | 25.574 | 26.338 | 1337.202 | 27.082 | 27.316 | 38.478 | 26.001 | 2.3 | 1.2 | 0.6 | 0.5 | 0.3
1286 | 30/07/2025 09:53:23.243 | 99.624 | 74 | 100 | 70 | 52 | 28.06 | 9.498 | 6.934 | 133.519 | 28.84 | 28.226 | 27.541 | 602.207 | 25.593 | 26.339 | 1331.337 | 27.068 | 27.308 | 38.443 | 28.001 | 1.7 | 2.9 | 1.2 | 0.6 | 0.3
1287 | 30/07/2025 09:53:24.890 | 99.792 | 76 | 100 | 70 | 52 | 30.322 | 9.428 | 6.935 | 133.171 | 28.827 | 28.215 | 27.543 | 602.093 | 25.566 | 26.334 | 1327.016 | 27.086 | 27.299 | 38.353 | 28.001 | 1.7 | 1.9 | 1.2 | 0.6 | 0.3
1288 | 30/07/2025 09:53:26.523 | 99.504 | 75 | 100 | 70 | 52 | 29.237 | 9.339 | 6.933 | 133.191 | 28.833 | 28.243 | 27.559 | 602.282 | 25.587 | 26.327 | 1325.105 | 27.051 | 27.288 | 38.629 | 23.001 | 4.1 | 1.8 | 0.6 | 0.1 | 0.3
1289 | 30/07/2025 09:53:28.161 | 99.84 | 76 | 100 | 71 | 52 | 26.346 | 9.431 | 6.937 | 134.678 | 28.823 | 28.25 | 27.559 | 602.257 | 25.585 | 26.334 | 1327.413 | 27.041 | 27.332 | 38.486 | 23.001 | 4.1 | 1.8 | 0.6 | 0.1 | 0.3
1290 | 30/07/2025 09:53:29.795 | 99.024 | 73 | 100 | 70 | 52 | 29.535 | 9.304 | 6.937 | 134.88 | 28.829 | 28.238 | 27.533 | 602.079 | 25.595 | 26.335 | 1330.606 | 27.074 | 27.302 | 38.591 | 26.001 | 4.1 | 2 | 0.6 | 0.1 | 0.3
1291 | 30/07/2025 09:53:31.431 | 98.976 | 74 | 100 | 70 | 52 | 30.472 | 9.509 | 6.934 | 134.664 | 28.826 | 28.23 | 27.572 | 602.287 | 25.589 | 26.339 | 1331.742 | 27.062 | 27.301 | 36.978 | 29.001 | 2 | 1.6 | 0 | 0.5 | 0.3
1292 | 30/07/2025 09:53:33.066 | 99.144 | 75 | 100 | 70 | 52 | 27.444 | 9.481 | 6.945 | 134.439 | 28.813 | 28.233 | 27.546 | 602.204 | 25.579 | 26.356 | 1319.563 | 27.091 | 27.282 | 38.238 | 27.001 | 2 | 2.1 | 0 | 0.5 | 0.3
1293 | 30/07/2025 09:53:34.700 | 99.072 | 73 | 100 | 70 | 53 | 30.39 | 9.578 | 6.985 | 134.676 | 28.806 | 28.247 | 27.561 | 602.279 | 25.584 | 26.347 | 1317.825 | 27.06 | 27.298 | 38.392 | 25.001 | 2.8 | 1.4 | 0.3 | 1 | 0.4
1294 | 30/07/2025 09:53:36.335 | 99.144 | 75 | 100 | 70 | 52 | 28.583 | 9.289 | 6.99 | 134.739 | 28.8 | 28.241 | 27.555 | 602.08 | 25.576 | 26.369 | 1317.309 | 27.051 | 27.318 | 36.747 | 29.001 | 2.8 | 2.3 | 0.3 | 1 | 0.4
1295 | 30/07/2025 09:53:37.974 | 99.048 | 75 | 100 | 71 | 52 | 26.457 | 9.284 | 7.005 | 134.98 | 28.831 | 28.235 | 27.541 | 602.042 | 25.595 | 26.499 | 1325.076 | 27.068 | 27.31 | 38.483 | 29.001 | 2.8 | 2.3 | 0.3 | 1 | 0.4
1296 | 30/07/2025 09:53:39.606 | 99.168 | 74 | 100 | 70 | 53 | 29.867 | 9.284 | 7.004 | 133.256 | 28.783 | 28.222 | 27.558 | 602.408 | 25.571 | 26.495 | 1320.344 | 27.069 | 27.317 | 38.332 | 29.001 | 2.9 | 1.8 | 0.6 | 1.6 | 0.3
1297 | 30/07/2025 09:53:41.242 | 99.168 | 73 | 100 | 71 | 52 | 30.35 | 9.469 | 7.002 | 133.095 | 28.799 | 28.237 | 27.546 | 602.24 | 25.596 | 26.508 | 1304.461 | 27.063 | 27.294 | 38.452 | 23.001 | 2.9 | 1.2 | 0.6 | 1.6 | 0.3
1298 | 30/07/2025 09:53:42.874 | 99.36 | 73 | 100 | 70 | 52 | 29.044 | 9.502 | 6.938 | 132.982 | 28.801 | 28.26 | 27.554 | 602.219 | 25.586 | 26.509 | 1297.422 | 27.065 | 27.324 | 38.415 | 27.001 | 2.2 | 3.7 | 0 | 0 | 0.3
1299 | 30/07/2025 09:53:44.510 | 99.288 | 74 | 100 | 70 | 52 | 30.446 | 9.631 | 6.937 | 133.496 | 28.812 | 28.241 | 27.537 | 602.193 | 25.593 | 26.498 | 1287.969 | 27.043 | 27.305 | 38.516 | 31.001 | 2.2 | 2.2 | 0 | 0 | 0.3
1300 | 30/07/2025 09:53:46.144 | 99.336 | 74 | 100 | 70 | 52 | 28.017 | 9.581 | 6.987 | 133.126 | 28.815 | 28.235 | 27.539 | 603.05 | 25.574 | 26.491 | 1294.602 | 27.068 | 27.304 | 38.435 | 31.001 | 2.2 | 2.2 | 0 | 0 | 0.3
1301 | 30/07/2025 09:53:47.779 | 99.432 | 76 | 100 | 70 | 52 | 26.908 | 9.437 | 6.936 | 133.221 | 28.83 | 28.205 | 27.562 | 603.415 | 25.582 | 26.498 | 1311.853 | 27.075 | 27.284 | 38.128 | 29.001 | 1.9 | 1 | 0 | 0.8 | 0.3
1302 | 30/07/2025 09:53:49.412 | 100.08 | 75 | 100 | 70 | 54 | 30.09 | 9.495 | 6.943 | 133.237 | 28.841 | 28.241 | 27.562 | 603.589 | 25.596 | 26.489 | 1319.454 | 27.042 | 27.297 | 36.758 | 27.001 | 1.9 | 2.2 | 0 | 0.8 | 0.3
1303 | 30/07/2025 09:53:51.047 | 99.816 | 75 | 100 | 71 | 53 | 26.28 | 9.535 | 7.029 | 133.105 | 28.831 | 28.238 | 27.562 | 602.144 | 25.575 | 26.5 | 1317.414 | 27.04 | 27.314 | 36.793 | 24.001 | 2.4 | 2.2 | 0.6 | 0.6 | 0.2
1304 | 30/07/2025 09:53:52.681 | 99.576 | 75 | 100 | 70 | 52 | 29.485 | 9.51 | 7.027 | 133.399 | 28.824 | 28.247 | 27.56 | 603.342 | 25.59 | 26.476 | 1317.654 | 27.057 | 27.304 | 36.712 | 25.001 | 2.4 | 1.8 | 0.6 | 0.6 | 0.2
1305 | 30/07/2025 09:53:54.317 | 99.456 | 75 | 100 | 70 | 52 | 30.493 | 9.507 | 6.987 | 133.169 | 28.834 | 28.233 | 27.547 | 603.446 | 25.555 | 26.474 | 1332.479 | 27.083 | 27.324 | 38.378 | 27.001 | 2.1 | 2 | 0.9 | 0.6 | 0.3
1306 | 30/07/2025 09:53:55.950 | 99.552 | 73 | 100 | 70 | 52 | 27.508 | 9.431 | 7.005 | 133.261 | 28.83 | 28.23 | 27.56 | 603.47 | 25.574 | 26.487 | 1332.039 | 27.072 | 27.276 | 38.285 | 27.001 | 2.1 | 2 | 0.9 | 0.6 | 0.3
1307 | 30/07/2025 09:53:57.583 | 99.312 | 76 | 100 | 70 | 51 | 27.329 | 9.282 | 7.006 | 133.178 | 28.831 | 28.249 | 27.563 | 603.524 | 25.57 | 26.469 | 1327.689 | 27.044 | 27.315 | 38.471 | 30.001 | 2.1 | 1.9 | 0.9 | 0.6 | 0.3
1308 | 30/07/2025 09:53:59.217 | 99.48 | 75 | 100 | 71 | 52 | 28.729 | 9.283 | 6.936 | 133.54 | 28.832 | 28.236 | 27.553 | 603.369 | 25.592 | 26.471 | 1325 | 27.04 | 27.321 | 38.584 | 24.001 | 3.5 | 2.4 | 0.6 | 0.1 | 0.3
1309 | 30/07/2025 09:54:00.853 | 98.136 | 73 | 99 | 70 | 52 | 26.559 | 9.436 | 6.934 | 134.804 | 28.823 | 28.237 | 27.545 | 603.461 | 25.565 | 26.461 | 1322.37 | 27.068 | 27.308 | 38.389 | 30.001 | 3.5 | 3.1 | 0.6 | 0.1 | 0.3
1310 | 30/07/2025 09:54:02.489 | 97.896 | 73 | 99 | 70 | 52 | 29.914 | 9.593 | 7.036 | 134.683 | 28.82 | 28.223 | 27.542 | 603.498 | 25.575 | 26.478 | 1315.172 | 27.078 | 27.301 | 38.548 | 27.001 | 2 | 1.9 | 0.7 | 0 | 0.2
1311 | 30/07/2025 09:54:04.126 | 98.64 | 74 | 100 | 70 | 52 | 30.375 | 9.284 | 7.032 | 134.565 | 28.826 | 28.242 | 27.562 | 603.604 | 25.602 | 26.47 | 1307.344 | 27.058 | 27.29 | 38.393 | 27.001 | 2 | 1.9 | 0.7 | 0 | 0.2
1312 | 30/07/2025 09:54:05.759 | 98.568 | 75 | 100 | 70 | 52 | 26.99 | 9.338 | 7.031 | 134.737 | 28.815 | 28.255 | 27.547 | 603.44 | 25.577 | 26.496 | 1303.102 | 27.052 | 27.335 | 38.486 | 30.001 | 2 | 1.6 | 0.7 | 0 | 0.2
1313 | 30/07/2025 09:54:07.394 | 98.952 | 74 | 100 | 70 | 53 | 27.763 | 9.456 | 6.987 | 133.249 | 28.814 | 28.235 | 27.518 | 603.185 | 25.605 | 26.501 | 1286.08 | 27.067 | 27.301 | 38.517 | 25.001 | 2.3 | 1.6 | 0 | 1.3 | 0.2
1314 | 30/07/2025 09:54:09.031 | 99.096 | 76 | 100 | 72 | 52 | 28.088 | 9.426 | 6.988 | 133.114 | 28.808 | 28.243 | 27.532 | 603.28 | 25.596 | 26.498 | 1282.904 | 27.098 | 27.315 | 38.641 | 28.001 | 2.3 | 1.3 | 0 | 1.3 | 0.2
1315 | 30/07/2025 09:54:10.668 | 99.504 | 74 | 100 | 70 | 52 | 26.776 | 9.288 | 6.985 | 133.243 | 28.818 | 28.221 | 27.556 | 603.466 | 25.592 | 26.501 | 1290.096 | 27.071 | 27.288 | 38.397 | 24.001 | 2.6 | 1.3 | 0.9 | 0 | 0.1
1316 | 30/07/2025 09:54:12.302 | 99.312 | 74 | 100 | 70 | 51 | 30.072 | 9.45 | 7.005 | 133.121 | 28.808 | 28.248 | 27.561 | 603.569 | 25.579 | 26.507 | 1297.085 | 27.065 | 27.295 | 38.341 | 24.001 | 2.6 | 1.3 | 0.9 | 0 | 0.1
1317 | 30/07/2025 09:54:13.937 | 99.024 | 76 | 100 | 70 | 51 | 30.163 | 9.496 | 7.007 | 133.317 | 28.792 | 28.241 | 27.548 | 603.188 | 25.572 | 26.51 | 1297.466 | 27.052 | 27.314 | 38.676 | 30.001 | 2.6 | 1.2 | 0.9 | 0 | 0.1
1318 | 30/07/2025 09:54:15.574 | 99.528 | 74 | 100 | 70 | 52 | 26.523 | 9.35 | 7.033 | 133.294 | 28.822 | 28.236 | 27.524 | 603.294 | 25.588 | 26.486 | 1292.332 | 27.063 | 27.307 | 36.693 | 33.001 | 2.2 | 1.5 | 0.7 | 0.1 | 0.2
1319 | 30/07/2025 09:54:17.208 | 99.576 | 75 | 100 | 70 | 52 | 28.464 | 9.506 | 6.996 | 133.15 | 28.804 | 28.224 | 27.573 | 603.49 | 25.577 | 26.489 | 1292.74 | 27.081 | 27.317 | 36.734 | 30.001 | 2.2 | 2.7 | 0.7 | 0.1 | 0.2
1320 | 30/07/2025 09:54:18.843 | 99.336 | 72 | 100 | 70 | 52 | 27.434 | 9.32 | 6.984 | 133.127 | 28.818 | 28.224 | 27.568 | 603.641 | 25.581 | 26.489 | 1297.414 | 27.057 | 27.28 | 36.518 | 25.001 | 3.4 | 1.6 | 0.7 | 0.5 | 0.2
1321 | 30/07/2025 09:54:20.479 | 99.624 | 74 | 100 | 70 | 52 | 27.328 | 9.283 | 7.006 | 132.996 | 28.818 | 28.246 | 27.542 | 603.491 | 25.578 | 26.492 | 1297.031 | 27.071 | 27.319 | 36.58 | 27.001 | 3.4 | 1.4 | 0.7 | 0.5 | 0.2
1322 | 30/07/2025 09:54:22.112 | 99.504 | 76 | 100 | 70 | 51 | 30.206 | 9.432 | 7.005 | 134.915 | 28.835 | 28.238 | 27.555 | 603.275 | 25.587 | 26.493 | 1297.191 | 27.044 | 27.315 | 38.453 | 27.001 | 3.4 | 1.4 | 0.7 | 0.5 | 0.2
1323 | 30/07/2025 09:54:23.748 | 99.432 | 74 | 100 | 70 | 52 | 29.845 | 9.488 | 7.033 | 134.711 | 28.821 | 28.236 | 27.53 | 603.308 | 25.564 | 26.492 | 1305.949 | 27.073 | 27.308 | 38.344 | 25.001 | 3 | 1.4 | 0.6 | 0.5 | 0.3
1324 | 30/07/2025 09:54:25.383 | 99.36 | 74 | 100 | 70 | 51 | 26.289 | 9.498 | 7.033 | 134.63 | 28.827 | 28.211 | 27.564 | 603.445 | 25.577 | 26.5 | 1296.886 | 27.081 | 27.299 | 38.322 | 27.001 | 3 | 0 | 0.6 | 0.5 | 0.3
1325 | 30/07/2025 09:54:27.017 | 99.24 | 74 | 100 | 70 | 51 | 30.372 | 9.511 | 7.033 | 134.479 | 28.828 | 28.228 | 27.567 | 603.506 | 25.575 | 26.482 | 1296.989 | 27.079 | 27.298 | 38.303 | 29.001 | 1.1 | 2.6 | 0 | 0.6 | 0.2
1326 | 30/07/2025 09:54:28.653 | 99.144 | 74 | 100 | 71 | 52 | 27.024 | 9.484 | 7.01 | 134.535 | 28.822 | 28.247 | 27.555 | 603.383 | 25.57 | 26.481 | 1297.802 | 27.043 | 27.302 | 38.672 | 23.001 | 1.1 | 0.8 | 0 | 0.6 | 0.2
1327 | 30/07/2025 09:54:30.288 | 98.952 | 74 | 100 | 70 | 52 | 27.907 | 9.502 | 7.004 | 134.748 | 28.827 | 28.241 | 27.55 | 603.504 | 25.565 | 26.471 | 1288.161 | 27.061 | 27.316 | 38.432 | 23.001 | 1.1 | 0.8 | 0 | 0.6 | 0.2
1328 | 30/07/2025 09:54:31.922 | 98.712 | 74 | 100 | 71 | 52 | 30.383 | 9.409 | 7.035 | 134.711 | 28.828 | 28.234 | 27.545 | 603.411 | 25.577 | 26.473 | 1279.325 | 27.085 | 27.313 | 38.465 | 25.001 | 4.4 | 1.1 | 0.9 | 0.4 | 0.2
1329 | 30/07/2025 09:54:33.558 | 98.256 | 73 | 100 | 70 | 52 | 29.301 | 9.397 | 7.004 | 134.622 | 28.824 | 28.232 | 27.567 | 603.403 | 25.583 | 26.476 | 1277.993 | 27.063 | 27.29 | 38.314 | 24.001 | 4.4 | 1.8 | 0.9 | 0.4 | 0.2
1330 | 30/07/2025 09:54:35.194 | 97.824 | 73 | 100 | 70 | 52 | 30.181 | 9.284 | 6.988 | 134.463 | 28.825 | 28.249 | 27.544 | 603.393 | 25.573 | 26.486 | 1272.876 | 27.078 | 27.3 | 38.424 | 31.001 | 2.6 | 1.8 | 0 | 0.5 | 0.2
1331 | 30/07/2025 09:54:36.829 | 97.488 | 74 | 100 | 72 | 52 | 30.195 | 9.284 | 7.013 | 134.892 | 28.826 | 28.236 | 27.559 | 603.49 | 25.603 | 26.484 | 1277.393 | 27.023 | 27.313 | 38.681 | 24.001 | 2.6 | 1.8 | 0 | 0.5 | 0.2
1332 | 30/07/2025 09:54:38.463 | 96.96 | 72 | 100 | 71 | 51 | 26.608 | 9.317 | 7.035 | 134.748 | 28.815 | 28.247 | 27.536 | 602.123 | 25.586 | 26.484 | 1289.381 | 27.074 | 27.313 | 38.634 | 23.001 | 4.4 | 0.7 | 0 | 0.3 | 0.2
1333 | 30/07/2025 09:54:40.098 | 97.32 | 73 | 100 | 71 | 51 | 28.487 | 9.292 | 7.034 | 134.724 | 28.82 | 28.221 | 27.537 | 602.152 | 25.591 | 26.499 | 1294.965 | 27.07 | 27.285 | 38.567 | 23.001 | 4.4 | 0.7 | 0 | 0.3 | 0.2
1334 | 30/07/2025 09:54:41.737 | 97.92 | 72 | 100 | 70 | 52 | 30.408 | 9.318 | 7.011 | 134.549 | 28.81 | 28.24 | 27.565 | 602.458 | 25.585 | 26.479 | 1297.292 | 27.055 | 27.279 | 38.223 | 24.001 | 4.4 | 1.9 | 0 | 0.3 | 0.2
1335 | 30/07/2025 09:54:43.370 | 97.848 | 73 | 100 | 70 | 52 | 28.795 | 9.495 | 7.006 | 134.678 | 28.807 | 28.255 | 27.549 | 602.077 | 25.587 | 26.513 | 1301.673 | 27.047 | 27.324 | 38.507 | 33.001 | 4.5 | 2.6 | 0.6 | 0.5 | 0.2
1336 | 30/07/2025 09:54:45.003 | 97.68 | 72 | 100 | 70 | 52 | 30.253 | 9.43 | 6.999 | 134.961 | 28.807 | 28.238 | 27.549 | 602.284 | 25.585 | 26.502 | 1297.433 | 27.045 | 27.315 | 38.382 | 27.001 | 4.5 | 1.9 | 0.6 | 0.5 | 0.2
1337 | 30/07/2025 09:54:46.640 | 97.296 | 73 | 100 | 70 | 52 | 29.829 | 9.285 | 6.988 | 134.627 | 28.787 | 28.231 | 27.528 | 602.091 | 25.57 | 26.494 | 1313.103 | 27.089 | 27.304 | 38.459 | 24.001 | 2.9 | 1.6 | 0.6 | 0.2 | 0.1
1338 | 30/07/2025 09:54:48.275 | 96.864 | 72 | 100 | 70 | 52 | 26.393 | 9.43 | 6.985 | 134.818 | 28.816 | 28.22 | 27.557 | 600.865 | 25.604 | 26.493 | 1312.187 | 27.059 | 27.287 | 38.439 | 24.001 | 2.9 | 1.6 | 0.6 | 0.2 | 0.1
1339 | 30/07/2025 09:54:49.910 | 96.624 | 74 | 100 | 71 | 51 | 29.001 | 9.291 | 6.988 | 134.637 | 28.807 | 28.253 | 27.551 | 600.771 | 25.576 | 26.503 | 1305.409 | 27.063 | 27.296 | 38.369 | 26.001 | 2.9 | 2.8 | 0.6 | 0.2 | 0.1
1340 | 30/07/2025 09:54:51.546 | 96.504 | 72 | 100 | 70 | 52 | 30.45 | 9.286 | 6.99 | 134.787 | 28.85 | 28.239 | 27.538 | 600.766 | 25.589 | 26.507 | 1298.388 | 27.034 | 27.317 | 38.661 | 25.001 | 2.2 | 2.4 | 0.6 | 0 | 0.2
1341 | 30/07/2025 09:54:53.178 | 96.432 | 72 | 100 | 69 | 52 | 27.821 | 9.286 | 7.002 | 134.573 | 28.811 | 28.255 | 27.542 | 600.677 | 25.574 | 26.498 | 1294.964 | 27.06 | 27.314 | 38.473 | 27.001 | 2.2 | 2.6 | 0.6 | 0 | 0.2
1342 | 30/07/2025 09:54:54.812 | 96.072 | 72 | 100 | 70 | 52 | 30.34 | 9.285 | 7.006 | 134.729 | 28.823 | 28.225 | 27.534 | 600.674 | 25.585 | 26.495 | 1295.287 | 27.067 | 27.298 | 38.495 | 26.001 | 3.8 | 1.3 | 1.2 | 0.3 | 0.1
1343 | 30/07/2025 09:54:56.447 | 95.904 | 72 | 100 | 69 | 52 | 29.192 | 9.431 | 7.003 | 134.585 | 28.828 | 28.228 | 27.559 | 600.87 | 25.584 | 26.493 | 1303.838 | 27.062 | 27.282 | 38.168 | 22.001 | 3.8 | 2.6 | 1.2 | 0.3 | 0.1
1344 | 30/07/2025 09:54:58.079 | 96.024 | 72 | 100 | 70 | 52 | 26.325 | 9.43 | 7.006 | 134.398 | 28.828 | 28.254 | 27.555 | 600.752 | 25.582 | 26.494 | 1307.984 | 27.076 | 27.304 | 38.397 | 22.001 | 3.8 | 2.6 | 1.2 | 0.3 | 0.1
1345 | 30/07/2025 09:54:59.714 | 95.856 | 72 | 100 | 71 | 52 | 29.392 | 9.281 | 7.006 | 134.983 | 28.973 | 28.236 | 27.549 | 600.818 | 25.585 | 26.493 | 1319.93 | 27.033 | 27.306 | 38.531 | 26.001 | 3.9 | 1.9 | 0.1 | 0.7 | 0.1
1346 | 30/07/2025 09:55:01.351 | 96 | 72 | 100 | 70 | 52 | 26.581 | 9.284 | 7.019 | 134.765 | 28.968 | 28.238 | 27.532 | 600.692 | 25.558 | 26.494 | 1319.771 | 27.076 | 27.303 | 38.503 | 25.001 | 3.9 | 2 | 0.1 | 0.7 | 0.1
1347 | 30/07/2025 09:55:02.986 | 95.976 | 70 | 100 | 71 | 52 | 28.396 | 9.285 | 7.034 | 134.842 | 28.983 | 28.225 | 27.556 | 600.912 | 25.59 | 26.473 | 1319.784 | 27.063 | 27.306 | 38.385 | 22.001 | 2.8 | 1.4 | 1.8 | 0.9 | 0.1
1348 | 30/07/2025 09:55:04.620 | 95.976 | 72 | 100 | 71 | 51 | 30.436 | 9.287 | 7.033 | 134.519 | 28.975 | 28.24 | 27.557 | 600.813 | 25.569 | 26.476 | 1317.193 | 27.069 | 27.303 | 38.279 | 27.001 | 2.8 | 2.2 | 1.8 | 0.9 | 0.1
1349 | 30/07/2025 09:55:06.255 | 95.4 | 70 | 100 | 70 | 52 | 28.79 | 9.129 | 7.034 | 134.558 | 28.968 | 28.25 | 27.551 | 600.749 | 25.569 | 26.496 | 1320.333 | 27.049 | 27.302 | 38.621 | 27.001 | 2.8 | 2.2 | 1.8 | 0.9 | 0.1
1350 | 30/07/2025 09:55:07.971 | 95.52 | 71 | 100 | 70 | 53 | 26.582 | 9.168 | 7.032 | 134.853 | 28.967 | 28.241 | 27.545 | 600.711 | 25.578 | 26.479 | 1307.373 | 27.056 | 27.302 | 38.518 | 23.001 | 2.6 | 1.7 | 0.3 | 1 | 0.1
1351 | 30/07/2025 09:55:09.609 | 95.112 | 72 | 100 | 70 | 52 | 29.952 | 9.442 | 7.006 | 134.651 | 28.978 | 28.232 | 27.53 | 600.655 | 25.578 | 26.466 | 1306.659 | 27.097 | 27.313 | 38.481 | 22.001 | 2.6 | 3.5 | 0.3 | 1 | 0.1
1352 | 30/07/2025 09:55:11.242 | 95.352 | 71 | 100 | 70 | 52 | 26.426 | 9.288 | 7.004 | 134.759 | 28.964 | 28.226 | 27.562 | 600.872 | 25.576 | 26.47 | 1307.12 | 27.071 | 27.298 | 38.292 | 26.001 | 3.5 | 1.6 | 0.6 | 0.5 | 0.2
1353 | 30/07/2025 09:55:12.878 | 95.112 | 71 | 100 | 71 | 52 | 29.061 | 9.436 | 7.035 | 134.196 | 28.978 | 28.242 | 27.532 | 600.666 | 25.582 | 26.496 | 1307.065 | 27.08 | 27.285 | 38.297 | 26.001 | 3.5 | 2.1 | 0.6 | 0.5 | 0.2
1354 | 30/07/2025 09:55:14.512 | 94.872 | 70 | 100 | 70 | 52 | 30.495 | 9.521 | 7.011 | 134.769 | 28.968 | 28.244 | 27.548 | 600.869 | 25.606 | 26.502 | 1311.967 | 27.025 | 27.313 | 38.57 | 23.001 | 2.8 | 0.5 | 1 | 0 | 0.2
1355 | 30/07/2025 09:55:16.155 | 94.824 | 70 | 100 | 70 | 52 | 28.243 | 9.287 | 6.936 | 134.79 | 28.945 | 28.242 | 27.542 | 600.624 | 25.579 | 26.5 | 1297.38 | 27.078 | 27.319 | 38.479 | 23.001 | 2.8 | 0.5 | 1 | 0 | 0.2
1356 | 30/07/2025 09:55:17.789 | 95.616 | 70 | 100 | 70 | 52 | 26.804 | 9.463 | 6.936 | 134.719 | 28.954 | 28.219 | 27.543 | 600.762 | 25.589 | 26.502 | 1289.935 | 27.062 | 27.298 | 38.507 | 25.001 | 2.8 | 0.9 | 1 | 0 | 0.2
1357 | 30/07/2025 09:55:19.425 | 96.12 | 71 | 100 | 70 | 52 | 30.163 | 9.439 | 6.942 | 134.602 | 28.944 | 28.237 | 27.558 | 600.782 | 25.583 | 26.507 | 1297.702 | 27.06 | 27.282 | 38.233 | 26.001 | 3.2 | 1.7 | 0.6 | 0.5 | 0.2
1358 | 30/07/2025 09:55:21.059 | 96 | 71 | 100 | 71 | 52 | 26.377 | 9.43 | 6.987 | 134.618 | 28.944 | 28.238 | 27.555 | 600.795 | 25.582 | 26.503 | 1304.671 | 27.054 | 27.293 | 38.53 | 23.001 | 3.2 | 1.3 | 0.6 | 0.5 | 0.2
1359 | 30/07/2025 09:55:22.698 | 96.024 | 72 | 100 | 70 | 52 | 29.549 | 9.287 | 6.987 | 134.791 | 28.952 | 28.245 | 27.549 | 600.789 | 25.591 | 26.5 | 1312.307 | 27.034 | 27.309 | 38.485 | 24.001 | 2.7 | 1.7 | 0.7 | 0.5 | 0.1
1360 | 30/07/2025 09:55:24.337 | 96.384 | 71 | 100 | 70 | 53 | 30.479 | 9.13 | 7.006 | 134.559 | 28.959 | 28.24 | 27.514 | 600.662 | 25.584 | 26.506 | 1307.984 | 27.096 | 27.309 | 38.435 | 24.001 | 2.7 | 1.8 | 0.7 | 0.5 | 0.1
1361 | 30/07/2025 09:55:25.973 | 97.008 | 73 | 100 | 70 | 53 | 27.503 | 9.132 | 7.004 | 134.742 | 28.967 | 28.224 | 27.559 | 600.898 | 25.596 | 26.494 | 1310.053 | 27.061 | 27.296 | 38.413 | 24.001 | 2.7 | 1.8 | 0.7 | 0.5 | 0.1
1362 | 30/07/2025 09:55:27.608 | 97.272 | 73 | 100 | 70 | 52 | 27.289 | 9.408 | 7.005 | 134.448 | 28.964 | 28.244 | 27.554 | 600.735 | 25.579 | 26.498 | 1311.404 | 27.063 | 27.304 | 38.413 | 25.001 | 1.5 | 1.8 | 0.1 | 0.6 | 0.1
1363 | 30/07/2025 09:55:29.246 | 97.464 | 73 | 100 | 70 | 51 | 28.684 | 9.422 | 7.005 | 134.618 | 28.97 | 28.244 | 27.567 | 600.813 | 25.611 | 26.492 | 1307.629 | 27.045 | 27.31 | 38.543 | 24.001 | 1.5 | 0.6 | 0.1 | 0.6 | 0.1
1364 | 30/07/2025 09:55:30.883 | 97.896 | 74 | 100 | 71 | 52 | 26.548 | 9.207 | 7.006 | 133.249 | 28.973 | 28.252 | 27.557 | 600.741 | 25.722 | 26.493 | 1313.162 | 27.053 | 27.32 | 38.631 | 24.001 | 3.5 | 1.1 | 0 | 0.8 | 0.1
1365 | 30/07/2025 09:55:32.516 | 98.088 | 74 | 100 | 71 | 52 | 29.83 | 9.283 | 7.032 | 133.307 | 28.983 | 28.228 | 27.541 | 600.667 | 25.733 | 26.501 | 1306.471 | 27.079 | 27.311 | 38.632 | 30.001 | 3.5 | 0.8 | 0 | 0.8 | 0.1
1366 | 30/07/2025 09:55:34.151 | 98.472 | 73 | 100 | 71 | 52 | 30.385 | 9.287 | 7.003 | 133.234 | 28.973 | 28.229 | 27.562 | 600.841 | 25.61 | 26.494 | 1295.041 | 27.061 | 27.298 | 38.157 | 30.001 | 3.5 | 0.8 | 0 | 0.8 | 0.1
1367 | 30/07/2025 09:55:35.789 | 98.76 | 75 | 100 | 71 | 53 | 26.994 | 9.283 | 7.006 | 132.89 | 28.977 | 28.252 | 27.547 | 600.745 | 25.71 | 26.496 | 1287.649 | 27.065 | 27.301 | 38.414 | 23.001 | 3 | 0.2 | 0.7 | 0.9 | 0.1
1368 | 30/07/2025 09:55:37.425 | 98.736 | 74 | 100 | 70 | 52 | 27.865 | 9.28 | 7.033 | 133.36 | 28.983 | 28.248 | 27.561 | 600.85 | 25.737 | 26.484 | 1287.974 | 27.052 | 27.32 | 38.548 | 27.001 | 3 | 2.5 | 0.7 | 0.9 | 0.1
1369 | 30/07/2025 09:55:39.061 | 98.544 | 74 | 100 | 70 | 52 | 28.058 | 9.284 | 7.037 | 133.188 | 28.97 | 28.24 | 27.542 | 600.697 | 25.72 | 26.5 | 1287.391 | 27.059 | 27.308 | 38.448 | 22.001 | 3.1 | 2.1 | 1.5 | 0 | 0.1
1370 | 30/07/2025 09:55:40.698 | 98.04 | 74 | 100 | 71 | 52 | 26.89 | 9.431 | 7.033 | 133.227 | 28.981 | 28.227 | 27.555 | 600.8 | 25.724 | 26.46 | 1292.992 | 27.071 | 27.304 | 38.609 | 26.001 | 3.1 | 1.4 | 1.5 | 0 | 0.1
1371 | 30/07/2025 09:55:42.335 | 98.04 | 74 | 100 | 70 | 52 | 30.164 | 9.518 | 7.034 | 133.008 | 28.972 | 28.248 | 27.568 | 600.798 | 25.71 | 26.469 | 1282.798 | 27.079 | 27.304 | 38.294 | 22.001 | 5.6 | 2.5 | 0.6 | 0.5 | 0.2
1372 | 30/07/2025 09:55:43.971 | 98.088 | 73 | 100 | 71 | 52 | 30.173 | 9.128 | 7.033 | 132.999 | 28.965 | 28.239 | 27.568 | 600.639 | 25.74 | 26.478 | 1293.169 | 27.043 | 27.309 | 38.704 | 22.001 | 5.6 | 2.5 | 0.6 | 0.5 | 0.2
1373 | 30/07/2025 09:55:45.608 | 97.896 | 73 | 100 | 70 | 52 | 26.627 | 9.285 | 7.034 | 134.837 | 28.957 | 28.246 | 27.556 | 600.734 | 25.724 | 26.477 | 1292.521 | 27.051 | 27.306 | 38.4 | 25.001 | 5.6 | 1.8 | 0.6 | 0.5 | 0.2
1374 | 30/07/2025 09:55:47.243 | 97.896 | 72 | 100 | 70 | 53 | 28.488 | 9.293 | 7.033 | 134.723 | 28.971 | 28.225 | 27.52 | 600.548 | 25.735 | 26.502 | 1297.389 | 27.081 | 27.314 | 38.635 | 29.001 | 2.3 | 1.5 | 0.7 | 0.2 | 0.1
1375 | 30/07/2025 09:55:48.880 | 97.608 | 73 | 100 | 71 | 53 | 27.641 | 9.288 | 7.033 | 134.725 | 28.972 | 28.224 | 27.561 | 602.32 | 25.74 | 26.5 | 1295.24 | 27.068 | 27.309 | 38.343 | 30.001 | 2.3 | 1.9 | 0.7 | 0.2 | 0.1
1376 | 30/07/2025 09:55:50.515 | 97.344 | 72 | 100 | 70 | 52 | 27.351 | 9.43 | 7.033 | 134.366 | 28.961 | 28.235 | 27.558 | 602.11 | 25.733 | 26.514 | 1297.212 | 27.065 | 27.286 | 38.278 | 21.001 | 3 | 1.1 | 0.6 | 0.5 | 0.1
1377 | 30/07/2025 09:55:52.152 | 97.176 | 74 | 100 | 71 | 52 | 30.316 | 9.281 | 7.034 | 134.779 | 28.95 | 28.244 | 27.564 | 600.964 | 25.733 | 26.502 | 1298.579 | 27.032 | 27.315 | 38.418 | 21.001 | 3 | 1.1 | 0.6 | 0.5 | 0.1
1378 | 30/07/2025 09:55:53.789 | 96.84 | 73 | 100 | 70 | 52 | 29.942 | 9.573 | 7.034 | 134.778 | 28.939 | 28.255 | 27.532 | 600.624 | 25.729 | 26.502 | 1297.17 | 27.082 | 27.318 | 38.35 | 25.001 | 3 | 1.8 | 0.6 | 0.5 | 0.1
1379 | 30/07/2025 09:55:55.424 | 97.224 | 73 | 100 | 70 | 52 | 26.442 | 9.45 | 7.034 | 134.803 | 28.943 | 28.221 | 27.536 | 600.729 | 25.729 | 26.498 | 1295.032 | 27.071 | 27.302 | 38.336 | 28.001 | 2.6 | 2.1 | 0 | 0.6 | 0.1
1380 | 30/07/2025 09:55:57.061 | 97.32 | 73 | 100 | 71 | 52 | 30.421 | 9.288 | 7.03 | 134.595 | 28.936 | 28.216 | 27.564 | 600.756 | 25.724 | 26.503 | 1290.811 | 27.088 | 27.305 | 38.279 | 28.001 | 2.6 | 1.4 | 0 | 0.6 | 0.1
1381 | 30/07/2025 09:55:58.695 | 97.536 | 74 | 100 | 71 | 52 | 27.07 | 9.402 | 7.034 | 134.506 | 28.947 | 28.241 | 27.567 | 600.872 | 25.739 | 26.499 | 1285.224 | 27.059 | 27.3 | 38.352 | 30.001 | 1.9 | 1.3 | 0.7 | 0.2 | 0.2
1382 | 30/07/2025 09:56:00.331 | 97.44 | 74 | 100 | 70 | 52 | 27.841 | 9.197 | 7.034 | 134.644 | 28.942 | 28.248 | 27.551 | 600.798 | 25.729 | 26.489 | 1287.216 | 27.03 | 27.312 | 38.764 | 26.001 | 1.9 | 2.2 | 0.7 | 0.2 | 0.2
1383 | 30/07/2025 09:56:01.966 | 96.936 | 73 | 100 | 70 | 52 | 30.378 | 9.364 | 7.035 | 134.5 | 28.97 | 28.238 | 27.532 | 600.652 | 25.721 | 26.521 | 1296.937 | 27.087 | 27.316 | 38.64 | 26.001 | 1.9 | 2.2 | 0.7 | 0.2 | 0.2
1384 | 30/07/2025 09:56:03.604 | 96.336 | 72 | 100 | 71 | 53 | 29.287 | 9.281 | 7.032 | 134.728 | 28.975 | 28.226 | 27.573 | 600.851 | 25.729 | 26.49 | 1314.966 | 27.056 | 27.289 | 38.249 | 26.001 | 1.8 | 2.8 | 0.6 | 0.5 | 0.2
1385 | 30/07/2025 09:56:05.240 | 96.456 | 72 | 100 | 70 | 52 | 26.362 | 9.495 | 7.034 | 134.334 | 28.973 | 28.245 | 27.724 | 600.714 | 25.717 | 26.487 | 1306.58 | 27.067 | 27.289 | 38.149 | 26.001 | 1.8 | 2.2 | 0.6 | 0.5 | 0.2
1386 | 30/07/2025 09:56:06.874 | 96.096 | 71 | 100 | 70 | 52 | 30.194 | 9.718 | 7.035 | 134.61 | 28.973 | 28.251 | 27.561 | 600.875 | 25.72 | 26.478 | 1307.338 | 27.048 | 27.29 | 38.664 | 29.001 | 1.8 | 1.6 | 0.1 | 0 | 0.2
1387 | 30/07/2025 09:56:08.513 | 95.904 | 73 | 100 | 70 | 51 | 26.675 | 9.289 | 7.035 | 134.708 | 28.978 | 28.244 | 27.542 | 600.811 | 25.715 | 26.486 | 1303.34 | 27.064 | 27.304 | 38.583 | 22.001 | 1.8 | 1.5 | 0.1 | 0 | 0.2
1388 | 30/07/2025 09:56:10.149 | 95.88 | 72 | 100 | 70 | 54 | 28.326 | 9.435 | 7.006 | 134.892 | 28.993 | 28.233 | 27.667 | 601.075 | 25.726 | 26.474 | 1287.546 | 27.071 | 27.303 | 38.552 | 22.001 | 1.8 | 1.5 | 0.1 | 0 | 0.2
1389 | 30/07/2025 09:56:11.785 | 96 | 72 | 100 | 69 | 53 | 30.437 | 9.287 | 6.989 | 134.723 | 28.973 | 28.228 | 27.683 | 600.849 | 25.697 | 26.486 | 1295.882 | 27.056 | 27.303 | 38.161 | 20.001 | 3.4 | 0.8 | 0.9 | 0.5 | 0.3
1390 | 30/07/2025 09:56:13.420 | 96.024 | 73 | 100 | 70 | 52 | 28.709 | 9.433 | 6.988 | 134.448 | 28.964 | 28.24 | 27.711 | 600.635 | 25.704 | 26.479 | 1297.273 | 27.065 | 27.292 | 38.42 | 25.001 | 3.4 | 0.6 | 0.9 | 0.5 | 0.3
1391 | 30/07/2025 09:56:15.055 | 95.784 | 71 | 100 | 70 | 52 | 30.289 | 9.284 | 6.988 | 134.605 | 28.965 | 28.258 | 27.739 | 600.712 | 25.707 | 26.471 | 1297.456 | 27.049 | 27.317 | 38.414 | 28.001 | 3.7 | 1.6 | 0.7 | 0 | 0.2
1392 | 30/07/2025 09:56:16.690 | 95.952 | 72 | 100 | 72 | 52 | 29.745 | 9.578 | 6.989 | 134.674 | 28.971 | 28.233 | 27.707 | 600.682 | 25.725 | 26.491 | 1292.545 | 27.057 | 27.31 | 38.43 | 27.001 | 3.7 | 1.3 | 0.7 | 0 | 0.2
1393 | 30/07/2025 09:56:18.326 | 95.52 | 72 | 100 | 71 | 52 | 26.334 | 9.371 | 6.934 | 134.715 | 28.975 | 28.231 | 27.709 | 600.808 | 25.738 | 26.481 | 1290.929 | 27.069 | 27.303 | 38.437 | 30.001 | 1.8 | 2 | 0 | 0 | 0.3
1394 | 30/07/2025 09:56:19.962 | 94.68 | 70 | 100 | 71 | 52 | 28.966 | 9.288 | 6.992 | 134.403 | 28.955 | 28.236 | 27.729 | 600.713 | 25.736 | 26.481 | 1287.539 | 27.087 | 27.29 | 38.098 | 30.001 | 1.8 | 2 | 0 | 0 | 0.3
1395 | 30/07/2025 09:56:21.600 | 94.848 | 72 | 100 | 70 | 52 | 30.506 | 9.432 | 7.005 | 134.457 | 28.97 | 28.246 | 27.729 | 600.714 | 25.743 | 26.484 | 1297.173 | 27.055 | 27.29 | 38.707 | 28.001 | 1.8 | 2.3 | 0 | 0 | 0.3
1396 | 30/07/2025 09:56:23.238 | 95.16 | 71 | 100 | 70 | 52 | 28.22 | 9.513 | 7.004 | 134.722 | 28.964 | 28.247 | 27.734 | 600.745 | 25.729 | 26.504 | 1307.098 | 27.047 | 27.32 | 38.565 | 28.001 | 3.2 | 1.8 | 0.6 | 0.7 | 0.3
1397 | 30/07/2025 09:56:24.870 | 94.872 | 70 | 100 | 70 | 52 | 30.396 | 9.286 | 7.005 | 134.845 | 28.966 | 28.252 | 27.697 | 600.706 | 25.76 | 26.489 | 1307.282 | 27.054 | 27.303 | 38.597 | 24.001 | 3.2 | 1.1 | 0.6 | 0.7 | 0.3
1398 | 30/07/2025 09:56:26.505 | 95.208 | 71 | 100 | 70 | 53 | 29.496 | 9.493 | 6.934 | 134.668 | 28.95 | 28.222 | 27.724 | 600.79 | 25.722 | 26.505 | 1304.59 | 27.065 | 27.32 | 38.377 | 24.001 | 2.1 | 1.7 | 1.2 | 0 | 0.2
1399 | 30/07/2025 09:56:28.142 | 95.568 | 72 | 100 | 71 | 52 | 26.401 | 9.288 | 6.935 | 134.478 | 28.94 | 28.23 | 27.724 | 600.759 | 25.734 | 26.502 | 1297.12 | 27.066 | 27.287 | 38.166 | 24.001 | 2.1 | 1.7 | 1.2 | 0 | 0.2
1400 | 30/07/2025 09:56:29.777 | 95.376 | 71 | 100 | 70 | 51 | 29.629 | 9.286 | 6.935 | 134.545 | 28.938 | 28.238 | 27.747 | 600.882 | 25.738 | 26.494 | 1297.503 | 27.041 | 27.311 | 38.406 | 23.001 | 2.1 | 2 | 1.2 | 0 | 0.2
1401 | 30/07/2025 09:56:31.411 | 95.592 | 71 | 100 | 70 | 52 | 30.513 | 9.432 | 6.901 | 134.817 | 28.954 | 28.25 | 27.699 | 599.409 | 25.729 | 26.499 | 1299.323 | 27.073 | 27.319 | 38.506 | 23.001 | 3.1 | 3.1 | 1.8 | 0.5 | 0.2
1402 | 30/07/2025 09:56:33.046 | 95.592 | 71 | 100 | 70 | 52 | 28.604 | 9.285 | 6.9 | 134.643 | 28.95 | 28.24 | 27.709 | 599.366 | 25.717 | 26.492 | 1302.435 | 27.062 | 27.305 | 38.527 | 27.001 | 3.1 | 2.8 | 1.8 | 0.5 | 0.2
1403 | 30/07/2025 09:56:34.681 | 95.88 | 72 | 100 | 70 | 52 | 30.445 | 9.345 | 6.934 | 134.734 | 28.959 | 28.217 | 27.72 | 599.54 | 25.73 | 26.508 | 1306.723 | 27.096 | 27.301 | 38.377 | 27.001 | 4.4 | 2.6 | 1 | 1.1 | 0.1
1404 | 30/07/2025 09:56:36.320 | 96.336 | 73 | 100 | 70 | 52 | 28.833 | 9.314 | 6.933 | 134.729 | 28.986 | 28.245 | 27.735 | 600.909 | 25.75 | 26.497 | 1305.05 | 27.057 | 27.286 | 38.356 | 25.001 | 4.4 | 1.4 | 1 | 1.1 | 0.1
1405 | 30/07/2025 09:56:37.963 | 96.072 | 72 | 100 | 71 | 52 | 26.566 | 9.282 | 6.935 | 134.648 | 28.967 | 28.246 | 27.73 | 600.706 | 25.73 | 26.486 | 1302.229 | 27.043 | 27.324 | 38.606 | 25.001 | 4.4 | 1.4 | 1 | 1.1 | 0.1
1406 | 30/07/2025 09:56:39.602 | 96.264 | 73 | 100 | 71 | 52 | 29.936 | 9.283 | 6.989 | 134.757 | 28.974 | 28.242 | 27.707 | 600.675 | 25.736 | 26.518 | 1305.56 | 27.084 | 27.311 | 38.481 | 25.001 | 2.4 | 2.3 | 0.6 | 0.8 | 0.2
1407 | 30/07/2025 09:56:41.237 | 96.408 | 73 | 100 | 70 | 52 | 30.459 | 9.315 | 6.986 | 134.805 | 28.97 | 28.218 | 27.74 | 600.985 | 25.717 | 26.482 | 1311.001 | 27.071 | 27.299 | 38.389 | 26.001 | 2.4 | 1.8 | 0.6 | 0.8 | 0.2
1408 | 30/07/2025 09:56:42.872 | 96.816 | 73 | 100 | 71 | 52 | 29.004 | 9.529 | 6.985 | 134.641 | 28.96 | 28.217 | 27.737 | 600.882 | 25.736 | 26.489 | 1307.133 | 27.063 | 27.289 | 38.135 | 23.001 | 3 | 1.6 | 1 | 0 | 0.2
1409 | 30/07/2025 09:56:44.507 | 96.36 | 73 | 100 | 70 | 52 | 30.522 | 9.29 | 6.987 | 134.65 | 28.97 | 28.249 | 27.746 | 600.857 | 25.706 | 26.473 | 1305.419 | 27.052 | 27.304 | 38.456 | 28.001 | 3 | 2 | 1 | 0 | 0.2
1410 | 30/07/2025 09:56:46.144 | 95.808 | 72 | 100 | 71 | 52 | 28.285 | 9.427 | 6.988 | 134.659 | 28.965 | 28.243 | 27.714 | 602.118 | 25.703 | 26.479 | 1307.586 | 27.065 | 27.303 | 38.64 | 28.001 | 3 | 2 | 1 | 0 | 0.2
1411 | 30/07/2025 09:56:47.777 | 96.648 | 71 | 100 | 71 | 52 | 26.85 | 9.292 | 7.005 | 134.811 | 28.985 | 28.238 | 27.698 | 602.088 | 25.732 | 26.482 | 1304.275 | 27.077 | 27.305 | 38.423 | 30.001 | 3.4 | 1.7 | 0.3 | 0.5 | 0.3
1412 | 30/07/2025 09:56:49.412 | 96.288 | 72 | 100 | 71 | 52 | 30.158 | 9.585 | 6.977 | 134.751 | 28.965 | 28.229 | 27.728 | 602.398 | 25.725 | 26.466 | 1299.123 | 27.072 | 27.299 | 38.231 | 24.001 | 3.4 | 2.1 | 0.3 | 0.5 | 0.3
1413 | 30/07/2025 09:56:51.046 | 96.096 | 72 | 100 | 70 | 51 | 26.373 | 9.46 | 6.933 | 134.58 | 28.982 | 28.238 | 27.745 | 602.205 | 25.729 | 26.475 | 1299.914 | 27.057 | 27.282 | 38.35 | 26.001 | 4.7 | 3.2 | 1.2 | 0.9 | 0.3
1414 | 30/07/2025 09:56:52.684 | 96.696 | 73 | 100 | 71 | 51 | 29.443 | 9.568 | 6.926 | 134.605 | 28.96 | 28.248 | 27.725 | 602.361 | 25.722 | 26.466 | 1293.455 | 27.053 | 27.322 | 38.591 | 25.001 | 4.7 | 1.4 | 1.2 | 0.9 | 0.3
1415 | 30/07/2025 09:56:54.320 | 96.648 | 72 | 100 | 71 | 51 | 30.494 | 9.428 | 6.902 | 134.783 | 28.971 | 28.235 | 27.699 | 602.123 | 25.728 | 26.488 | 1292.619 | 27.048 | 27.307 | 38.529 | 32.001 | 2.1 | 1.5 | 0.6 | 0.5 | 0.3
1416 | 30/07/2025 09:56:55.965 | 96.672 | 73 | 100 | 71 | 52 | 27.509 | 9.428 | 6.899 | 134.806 | 28.959 | 28.235 | 27.733 | 602.085 | 25.73 | 26.502 | 1290.146 | 27.076 | 27.306 | 38.367 | 32.001 | 2.1 | 1.5 | 0.6 | 0.5 | 0.3
1417 | 30/07/2025 09:56:57.601 | 97.008 | 73 | 100 | 70 | 52 | 27.298 | 9.583 | 6.907 | 134.488 | 28.939 | 28.235 | 27.717 | 602.046 | 25.737 | 26.505 | 1280.227 | 27.084 | 27.303 | 38.267 | 26.001 | 2.1 | 1.2 | 0.6 | 0.5 | 0.3
1418 | 30/07/2025 09:56:59.238 | 96.48 | 72 | 100 | 71 | 52 | 30.29 | 9.288 | 6.936 | 134.586 | 28.963 | 28.245 | 27.725 | 602.293 | 25.742 | 26.503 | 1273.921 | 27.044 | 27.287 | 38.62 | 24.001 | 3.8 | 0.9 | 0.6 | 0 | 0.2
1419 | 30/07/2025 09:57:00.877 | 96.96 | 74 | 100 | 70 | 52 | 26.576 | 9.321 | 6.933 | 134.714 | 28.946 | 28.244 | 27.707 | 602.051 | 25.726 | 26.519 | 1271.823 | 27.045 | 27.326 | 38.57 | 25.001 | 3.8 | 1.9 | 0.6 | 0 | 0.2
1420 | 30/07/2025 09:57:02.513 | 96.288 | 73 | 100 | 70 | 52 | 29.939 | 9.401 | 6.899 | 134.711 | 28.951 | 28.241 | 27.71 | 602.709 | 25.744 | 26.503 | 1259.522 | 27.064 | 27.31 | 38.428 | 27.001 | 3 | 1.6 | 1.2 | 0.5 | 0.2
1421 | 30/07/2025 09:57:04.147 | 96.36 | 72 | 100 | 70 | 52 | 30.444 | 9.288 | 6.934 | 134.69 | 28.941 | 28.244 | 27.732 | 602.296 | 25.727 | 26.499 | 1274.217 | 27.084 | 27.318 | 38.508 | 27.001 | 3 | 1.6 | 1.2 | 0.5 | 0.2
1422 | 30/07/2025 09:57:05.783 | 96.456 | 71 | 100 | 70 | 53 | 27.062 | 9.286 | 6.924 | 132.901 | 28.963 | 28.235 | 27.73 | 602.32 | 25.734 | 26.5 | 1279.896 | 27.065 | 27.283 | 38.297 | 25.001 | 3 | 0.8 | 1.2 | 0.5 | 0.2
1423 | 30/07/2025 09:57:07.421 | 96.072 | 71 | 100 | 71 | 53 | 27.982 | 9.501 | 6.866 | 133.165 | 28.955 | 28.243 | 27.738 | 603.627 | 25.722 | 26.477 | 1290.267 | 27.051 | 27.303 | 38.617 | 26.001 | 3.1 | 1.6 | 0.6 | 0.2 | 0.2
1424 | 30/07/2025 09:57:09.057 | 95.904 | 72 | 100 | 70 | 52 | 28.229 | 9.284 | 6.866 | 133.427 | 28.954 | 28.241 | 27.731 | 603.398 | 25.731 | 26.499 | 1287.679 | 27.034 | 27.315 | 38.434 | 27.001 | 3.1 | 1.6 | 0.6 | 0.2 | 0.2
1425 | 30/07/2025 09:57:10.690 | 96.384 | 73 | 100 | 70 | 52 | 26.902 | 9.295 | 6.864 | 133.267 | 28.955 | 28.24 | 27.706 | 602.185 | 25.719 | 26.502 | 1277.505 | 27.071 | 27.312 | 38.36 | 27.001 | 3.5 | 1.1 | 0.6 | 0.5 | 0.2
1426 | 30/07/2025 09:57:12.328 | 96.96 | 74 | 100 | 70 | 52 | 30.198 | 9.497 | 6.865 | 133.091 | 28.974 | 28.219 | 27.717 | 602.203 | 25.726 | 26.503 | 1276.565 | 27.078 | 27.303 | 38.371 | 31.001 | 3.5 | 2.4 | 0.6 | 0.5 | 0.2
1427 | 30/07/2025 09:57:13.969 | 97.368 | 73 | 100 | 71 | 53 | 30.283 | 9.223 | 6.864 | 133.255 | 28.967 | 28.247 | 27.737 | 602.21 | 25.745 | 26.479 | 1282.683 | 27.06 | 27.286 | 37.971 | 31.001 | 3.5 | 2.4 | 0.6 | 0.5 | 0.2
1428 | 30/07/2025 09:57:15.609 | 97.488 | 74 | 100 | 70 | 52 | 26.715 | 9.728 | 6.902 | 133.087 | 28.967 | 28.256 | 27.707 | 602.22 | 25.72 | 26.483 | 1279.245 | 27.038 | 27.324 | 36.857 | 24.001 | 3.3 | 0.7 | 1.2 | 0.2 | 0.2
1429 | 30/07/2025 09:57:17.246 | 97.872 | 74 | 100 | 71 | 52 | 28.445 | 9.442 | 6.937 | 133.283 | 28.972 | 28.237 | 27.698 | 601.965 | 25.713 | 26.491 | 1266.888 | 27.065 | 27.304 | 36.824 | 28.001 | 3.3 | 1.3 | 1.2 | 0.2 | 0.2
1430 | 30/07/2025 09:57:18.883 | 98.448 | 74 | 100 | 71 | 52 | 27.773 | 9.431 | 6.935 | 133.189 | 28.971 | 28.248 | 27.7 | 602.129 | 25.711 | 26.487 | 1263.967 | 27.092 | 27.317 | 36.627 | 24.001 | 1.9 | 0.9 | 0.6 | 0 | 0.2
1431 | 30/07/2025 09:57:20.517 | 99.12 | 75 | 99 | 71 | 52 | 27.342 | 9.287 | 6.933 | 133.221 | 28.976 | 28.213 | 27.74 | 602.223 | 25.72 | 26.479 | 1267.292 | 27.059 | 27.295 | 36.618 | 26.001 | 1.9 | 2.1 | 0.6 | 0 | 0.2
1432 | 30/07/2025 09:57:22.154 | 99 | 74 | 100 | 70 | 52 | 30.362 | 9.398 | 6.935 | 133.177 | 28.975 | 28.255 | 27.733 | 602.335 | 25.711 | 26.465 | 1267.542 | 27.057 | 27.309 | 36.478 | 26.001 | 1.9 | 2.1 | 0.6 | 0 | 0.2
1433 | 30/07/2025 09:57:23.791 | 99.312 | 76 | 100 | 70 | 52 | 29.95 | 9.376 | 6.935 | 133.354 | 28.962 | 28.244 | 27.715 | 602.178 | 25.724 | 26.478 | 1280.173 | 27.058 | 27.3 | 36.702 | 27.001 | 1.8 | 2.1 | 0.6 | 0 | 0.1
1434 | 30/07/2025 09:57:25.426 | 98.976 | 75 | 100 | 70 | 53 | 26.462 | 9.282 | 6.983 | 133.288 | 28.989 | 28.242 | 27.706 | 602.297 | 25.736 | 26.474 | 1279.893 | 27.067 | 27.306 | 36.764 | 29.001 | 1.8 | 2.3 | 0.6 | 0 | 0.1
1435 | 30/07/2025 09:57:27.063 | 98.448 | 75 | 100 | 70 | 52 | 30.459 | 9.284 | 6.989 | 133.235 | 28.971 | 28.223 | 27.675 | 602.071 | 25.722 | 26.489 | 1285.654 | 27.071 | 27.304 | 36.728 | 26.001 | 1.8 | 0.8 | 0.6 | 0.6 | 0.1
1436 | 30/07/2025 09:57:28.702 | 98.208 | 74 | 100 | 70 | 53 | 27.041 | 9.422 | 6.935 | 133.202 | 28.973 | 28.234 | 27.746 | 602.43 | 25.727 | 26.483 | 1285.883 | 27.071 | 27.292 | 36.438 | 27.001 | 1.8 | 1.9 | 0.6 | 0.6 | 0.1
1437 | 30/07/2025 09:57:30.341 | 98.328 | 74 | 100 | 71 | 51 | 27.861 | 9.459 | 6.936 | 133.021 | 28.962 | 28.263 | 27.707 | 602.224 | 25.731 | 26.502 | 1272.221 | 27.068 | 27.315 | 36.642 | 22.001 | 3 | 3.4 | 0.6 | 0.6 | 0.1
1438 | 30/07/2025 09:57:31.973 | 98.832 | 76 | 100 | 70 | 52 | 30.43 | 9.212 | 6.935 | 133.416 | 28.948 | 28.243 | 27.71 | 602.115 | 25.743 | 26.512 | 1267.58 | 27.048 | 27.309 | 36.613 | 22.001 | 3 | 3.4 | 0.6 | 0.6 | 0.1
1439 | 30/07/2025 09:57:33.607 | 98.664 | 75 | 100 | 71 | 52 | 29.426 | 9.289 | 6.934 | 133.27 | 28.941 | 28.242 | 27.711 | 602.224 | 25.731 | 26.491 | 1267.624 | 27.067 | 27.306 | 36.582 | 23.001 | 3 | 2.1 | 0.6 | 0.6 | 0.1
1440 | 30/07/2025 09:57:35.243 | 98.448 | 75 | 100 | 70 | 52 | 26.421 | 9.329 | 6.935 | 133.196 | 28.934 | 28.221 | 27.728 | 602.197 | 25.725 | 26.506 | 1274.082 | 27.079 | 27.292 | 36.568 | 26.001 | 1.5 | 0.7 | 0.5 | 1.1 | 0.1
1441 | 30/07/2025 09:57:36.880 | 99.432 | 76 | 100 | 70 | 52 | 30.256 | 9.133 | 7.002 | 133.088 | 28.936 | 28.246 | 27.746 | 602.276 | 25.721 | 26.508 | 1284.483 | 27.067 | 27.291 | 38.231 | 26.001 | 1.5 | 0.6 | 0.5 | 1.1 | 0.1
1442 | 30/07/2025 09:57:38.515 | 99.168 | 76 | 100 | 72 | 52 | 26.723 | 9.365 | 7.007 | 133.176 | 28.941 | 28.243 | 27.726 | 602.132 | 25.728 | 26.508 | 1288.086 | 27.051 | 27.308 | 36.727 | 27.001 | 2.6 | 1 | 0 | 0 | 0.2
1443 | 30/07/2025 09:57:40.151 | 98.88 | 76 | 100 | 71 | 53 | 28.499 | 9.346 | 6.986 | 133.01 | 28.948 | 28.243 | 27.704 | 602.293 | 25.735 | 26.495 | 1291.691 | 27.061 | 27.311 | 36.562 | 27.001 | 2.6 | 1 | 0 | 0 | 0.2
1444 | 30/07/2025 09:57:41.786 | 99 | 76 | 100 | 70 | 52 | 30.479 | 9.269 | 6.986 | 133.167 | 28.953 | 28.244 | 27.715 | 602.193 | 25.727 | 26.492 | 1287.599 | 27.085 | 27.32 | 36.537 | 26.001 | 2.6 | 1.8 | 0 | 0 | 0.2
1445 | 30/07/2025 09:57:43.420 | 98.664 | 74 | 100 | 70 | 52 | 28.95 | 9.292 | 6.986 | 133.187 | 28.97 | 28.233 | 27.728 | 602.247 | 25.726 | 26.496 | 1297.162 | 27.064 | 27.288 | 36.35 | 24.001 | 4.3 | 0.7 | 0.6 | 0 | 0.2
1446 | 30/07/2025 09:57:45.056 | 97.896 | 75 | 100 | 70 | 52 | 30.361 | 9.285 | 7.005 | 133.086 | 28.982 | 28.261 | 27.718 | 602.129 | 25.716 | 26.506 | 1297.304 | 27.082 | 27.301 | 36.63 | 30.001 | 4.3 | 1 | 0.6 | 0 | 0.2
1447 | 30/07/2025 09:57:46.691 | 98.256 | 75 | 100 | 70 | 51 | 29.931 | 9.28 | 7.005 | 133.328 | 28.991 | 28.242 | 27.725 | 602.256 | 25.741 | 26.504 | 1290.105 | 27.023 | 27.314 | 36.639 | 26.001 | 3.1 | 1.8 | 1.2 | 0 | 0.1
1448 | 30/07/2025 09:57:48.325 | 98.664 | 76 | 100 | 70 | 52 | 26.534 | 9.499 | 7.005 | 133.253 | 28.971 | 28.244 | 27.68 | 602.087 | 25.73 | 26.488 | 1277.869 | 27.072 | 27.303 | 36.549 | 37.001 | 3.1 | 1.7 | 1.2 | 0 | 0.1
1449 | 30/07/2025 09:57:49.968 | 99.408 | 77 | 100 | 71 | 51 | 29.116 | 9.429 | 7.006 | 133.186 | 28.973 | 28.213 | 27.721 | 602.152 | 25.721 | 26.502 | 1269.608 | 27.078 | 27.296 | 36.489 | 37.001 | 3.1 | 1.7 | 1.2 | 0 | 0.1
1450 | 30/07/2025 09:57:51.603 | 100.2 | 78 | 100 | 70 | 53 | 30.56 | 9.509 | 7.003 | 132.982 | 28.981 | 28.243 | 27.745 | 602.357 | 25.717 | 26.477 | 1269.97 | 27.059 | 27.283 | 36.534 | 30.001 | 2.2 | 1.8 | 0.6 | 0 | 0.1
1451 | 30/07/2025 09:57:53.238 | 100.104 | 76 | 100 | 70 | 52 | 28.03 | 9.426 | 7.027 | 132.922 | 28.964 | 28.246 | 27.708 | 602.154 | 25.718 | 26.474 | 1277.718 | 27.05 | 27.296 | 36.863 | 31.001 | 2.2 | 1.8 | 0.6 | 0 | 0.1
1452 | 30/07/2025 09:57:54.873 | 100.104 | 76 | 100 | 70 | 52 | 30.518 | 9.473 | 7.035 | 133.413 | 28.965 | 28.241 | 27.741 | 602.343 | 25.727 | 26.475 | 1286.479 | 27.04 | 27.319 | 36.828 | 25.001 | 2.6 | 1.9 | 0 | 0 | 0.2
1453 | 30/07/2025 09:57:56.510 | 100.32 | 76 | 100 | 71 | 52 | 29.503 | 9.401 | 7.034 | 133.13 | 28.972 | 28.245 | 27.701 | 602.098 | 25.699 | 26.468 | 1288.171 | 27.093 | 27.306 | 36.755 | 25.001 | 2.6 | 1.6 | 0 | 0 | 0.2
1454 | 30/07/2025 09:57:58.150 | 100.2 | 79 | 100 | 71 | 52 | 26.503 | 9.431 | 7.067 | 133.262 | 28.966 | 28.21 | 27.732 | 602.209 | 25.737 | 26.476 | 1297.306 | 27.062 | 27.303 | 36.562 | 25.001 | 2.6 | 1.6 | 0 | 0 | 0.2
1455 | 30/07/2025 09:57:59.785 | 99.96 | 77 | 100 | 70 | 52 | 29.5 | 9.288 | 7.071 | 133.212 | 28.959 | 28.25 | 27.735 | 602.212 | 25.725 | 26.472 | 1299.909 | 27.06 | 27.296 | 36.605 | 28.001 | 2 | 1.3 | 0.3 | 0.1 | 0.3
1456 | 30/07/2025 09:58:01.421 | 99.768 | 76 | 100 | 70 | 53 | 30.579 | 9.131 | 7.075 | 133.125 | 28.966 | 28.237 | 27.716 | 602.19 | 25.734 | 26.494 | 1293.954 | 27.051 | 27.301 | 36.878 | 28.001 | 2 | 1.6 | 0.3 | 0.1 | 0.3
1457 | 30/07/2025 09:58:03.057 | 99.528 | 77 | 100 | 70 | 52 | 28.406 | 9.28 | 7.071 | 133.359 | 28.961 | 28.257 | 27.708 | 602.26 | 25.738 | 26.489 | 1297.765 | 27.063 | 27.315 | 36.813 | 30.001 | 3.1 | 1 | 0.6 | 0.5 | 0.2
1458 | 30/07/2025 09:58:04.693 | 98.976 | 75 | 100 | 70 | 53 | 30.523 | 9.429 | 7.075 | 133.303 | 28.969 | 28.237 | 27.709 | 602.073 | 25.73 | 26.497 | 1294.504 | 27.08 | 27.306 | 36.825 | 26.001 | 3.1 | 0.9 | 0.6 | 0.5 | 0.2
1459 | 30/07/2025 09:58:06.330 | 98.952 | 76 | 100 | 71 | 51 | 28.875 | 9.464 | 7.069 | 134.658 | 28.959 | 28.224 | 27.724 | 602.462 | 25.737 | 26.496 | 1283.075 | 27.067 | 27.279 | 38.216 | 30.001 | 3.9 | 1.7 | 0 | 0 | 0.2
1460 | 30/07/2025 09:58:07.966 | 98.952 | 76 | 100 | 71 | 52 | 26.634 | 9.429 | 7.071 | 134.48 | 28.936 | 28.25 | 27.72 | 602.262 | 25.729 | 26.501 | 1284.551 | 27.073 | 27.316 | 36.764 | 30.001 | 3.9 | 1.7 | 0 | 0 | 0.2
1461 | 30/07/2025 09:58:09.602 | 99 | 77 | 100 | 71 | 52 | 29.91 | 9.284 | 7.072 | 134.913 | 28.955 | 28.241 | 27.719 | 602.098 | 25.738 | 26.505 | 1294.361 | 27.037 | 27.32 | 36.549 | 26.001 | 3.9 | 2.4 | 0 | 0 | 0.2
1462 | 30/07/2025 09:58:11.237 | 98.856 | 75 | 100 | 70 | 51 | 26.524 | 9.427 | 7.072 | 134.59 | 28.938 | 28.254 | 27.693 | 602.008 | 25.718 | 26.514 | 1301.465 | 27.082 | 27.314 | 36.994 | 25.001 | 1.5 | 1.8 | 0.1 | 0.5 | 0.2
1463 | 30/07/2025 09:58:12.871 | 99.216 | 77 | 100 | 71 | 51 | 29.021 | 9.395 | 7.071 | 134.967 | 28.947 | 28.226 | 27.712 | 600.634 | 25.734 | 26.504 | 1297.219 | 27.06 | 27.304 | 38.456 | 28.001 | 1.5 | 2.9 | 0.1 | 0.5 | 0.2
1464 | 30/07/2025 09:58:14.526 | 98.736 | 76 | 100 | 70 | 52 | 30.535 | 9.283 | 7.069 | 134.563 | 28.935 | 28.241 | 27.736 | 601.382 | 25.715 | 26.49 | 1290.341 | 27.073 | 27.293 | 36.467 | 28.001 | 4.1 | 2.6 | 0.1 | 0 | 0.2
1465 | 30/07/2025 09:58:16.162 | 97.992 | 75 | 100 | 70 | 51 | 28.201 | 9.283 | 7.074 | 134.541 | 28.953 | 28.242 | 27.719 | 600.698 | 25.73 | 26.5 | 1283.824 | 27.047 | 27.303 | 37.34 | 28.001 | 4.1 | 2.6 | 0.1 | 0 | 0.2
1466 | 30/07/2025 09:58:17.798 | 98.976 | 77 | 100 | 71 | 52 | 26.855 | 9.411 | 7.031 | 134.676 | 28.977 | 28.244 | 27.715 | 600.773 | 25.734 | 26.488 | 1270.426 | 27.059 | 27.306 | 36.634 | 24.001 | 4.1 | 2.5 | 0.1 | 0 | 0.2
1467 | 30/07/2025 09:58:19.436 | 98.928 | 75 | 100 | 71 | 52 | 30.236 | 9.525 | 7.006 | 134.496 | 28.965 | 28.247 | 27.725 | 602.092 | 25.732 | 26.502 | 1271.442 | 27.088 | 27.316 | 38.416 | 29.001 | 2.5 | 2 | 1 | 0 | 0.2
1468 | 30/07/2025 09:58:21.072 | 98.712 | 76 | 100 | 70 | 52 | 26.471 | 9.435 | 7.003 | 134.621 | 28.977 | 28.221 | 27.717 | 602.337 | 25.718 | 26.494 | 1279.31 | 27.066 | 27.303 | 38.235 | 26.001 | 2.5 | 2.7 | 1 | 0 | 0.2
1469 | 30/07/2025 09:58:22.708 | 98.904 | 75 | 100 | 71 | 52 | 29.582 | 9.486 | 7.006 | 134.416 | 28.972 | 28.24 | 27.733 | 602.138 | 25.716 | 26.504 | 1280.974 | 27.082 | 27.293 | 38.448 | 30.001 | 2.9 | 2.2 | 0 | 0.5 | 0.2
1470 | 30/07/2025 09:58:24.345 | 99.048 | 76 | 100 | 70 | 51 | 30.58 | 9.286 | 7.005 | 134.718 | 28.973 | 28.249 | 27.7 | 602.266 | 25.738 | 26.487 | 1288.082 | 27.027 | 27.316 | 38.743 | 28.001 | 2.9 | 1.3 | 0 | 0.5 | 0.2
1471 | 30/07/2025 09:58:25.979 | 98.736 | 75 | 100 | 70 | 53 | 27.791 | 9.287 | 7.034 | 134.814 | 28.963 | 28.245 | 27.711 | 602.068 | 25.716 | 26.486 | 1287.769 | 27.076 | 27.317 | 36.765 | 28.001 | 2.9 | 1.3 | 0 | 0.5 | 0.2
1472 | 30/07/2025 09:58:27.614 | 99.168 | 75 | 100 | 70 | 52 | 27.48 | 9.284 | 7.009 | 134.609 | 28.98 | 28.229 | 27.715 | 602.215 | 25.703 | 26.482 | 1287.884 | 27.075 | 27.296 | 38.45 | 29.001 | 4.1 | 1.4 | 0.6 | 0.8 | 0.1
1473 | 30/07/2025 09:58:29.247 | 99.12 | 76 | 100 | 71 | 51 | 30.374 | 9.288 | 6.985 | 134.616 | 28.971 | 28.244 | 27.752 | 602.264 | 25.722 | 26.462 | 1285.303 | 27.06 | 27.284 | 38.247 | 26.001 | 4.1 | 1.6 | 0.6 | 0.8 | 0.1
1474 | 30/07/2025 09:58:30.882 | 98.592 | 75 | 100 | 70 | 52 | 26.656 | 9.283 | 6.968 | 134.541 | 28.97 | 28.254 | 27.722 | 602.076 | 25.723 | 26.482 | 1283.343 | 27.053 | 27.298 | 36.677 | 19 | 3.2 | 2.2 | 0.7 | 0.5 | 0.2
1475 | 30/07/2025 09:58:32.518 | 98.4 | 76 | 100 | 71 | 53 | 29.987 | 9.431 | 6.935 | 134.835 | 28.977 | 28.25 | 27.724 | 602.351 | 25.723 | 26.466 | 1289.589 | 27.045 | 27.304 | 36.604 | 28.001 | 3.2 | 1.7 | 0.7 | 0.5 | 0.2
1476 | 30/07/2025 09:58:34.154 | 97.464 | 74 | 100 | 71 | 52 | 30.548 | 9.366 | 6.935 | 134.507 | 28.963 | 28.235 | 27.666 | 601.994 | 25.713 | 26.487 | 1290.844 | 27.097 | 27.322 | 38.542 | 28.001 | 3.2 | 1.7 | 0.7 | 0.5 | 0.2
1477 | 30/07/2025 09:58:35.791 | 96.936 | 74 | 100 | 71 | 52 | 27.155 | 9.505 | 6.922 | 134.825 | 28.964 | 28.222 | 27.722 | 602.252 | 25.753 | 26.486 | 1292.719 | 27.059 | 27.295 | 38.462 | 30.001 | 1.8 | 0.5 | 0 | 0.8 | 0.2
1478 | 30/07/2025 09:58:37.424 | 97.44 | 75 | 100 | 71 | 52 | 27.903 | 9.311 | 6.9 | 134.443 | 28.955 | 28.254 | 27.728 | 603.429 | 25.738 | 26.497 | 1292.686 | 27.064 | 27.299 | 36.578 | 25.001 | 1.8 | 0.7 | 0 | 0.8 | 0.2
1479 | 30/07/2025 09:58:39.059 | 96.864 | 74 | 100 | 70 | 52 | 28.34 | 9.214 | 6.909 | 134.652 | 28.968 | 28.253 | 27.702 | 603.488 | 25.733 | 26.49 | 1297.254 | 27.046 | 27.301 | 38.371 | 28.001 | 1.3 | 1.1 | 0 | 0.1 | 0.2
1480 | 30/07/2025 09:58:40.695 | 97.224 | 74 | 100 | 70 | 52 | 26.918 | 9.433 | 6.935 | 134.827 | 28.952 | 28.246 | 27.718 | 603.345 | 25.725 | 26.509 | 1306.878 | 27.056 | 27.325 | 38.531 | 24.001 | 1.3 | 1.4 | 0 | 0.1 | 0.2
1481 | 30/07/2025 09:58:42.332 | 97.68 | 76 | 100 | 70 | 52 | 30.257 | 9.284 | 6.938 | 134.572 | 28.942 | 28.232 | 27.693 | 603.202 | 25.737 | 26.491 | 1309.83 | 27.074 | 27.298 | 38.495 | 29.001 | 1.8 | 1.1 | 0.6 | 1 | 0.2
1482 | 30/07/2025 09:58:43.970 | 97.344 | 76 | 100 | 71 | 54 | 30.351 | 9.285 | 6.955 | 134.506 | 28.946 | 28.228 | 27.726 | 603.456 | 25.726 | 26.499 | 1309.911 | 27.063 | 27.282 | 38.15 | 29.001 | 1.8 | 1.1 | 0.6 | 1 | 0.2
1483 | 30/07/2025 09:58:45.607 | 98.04 | 74 | 100 | 70 | 53 | 26.777 | 9.427 | 7.006 | 134.385 | 28.942 | 28.247 | 27.724 | 603.447 | 25.726 | 26.506 | 1297.619 | 27.075 | 27.304 | 38.475 | 27.001 | 1.8 | 0.5 | 0.6 | 1 | 0.2
1484 | 30/07/2025 09:58:47.241 | 97.68 | 74 | 100 | 71 | 52 | 28.484 | 9.421 | 6.987 | 134.833 | 28.952 | 28.244 | 27.702 | 603.349 | 25.731 | 26.491 | 1293.55 | 27.032 | 27.302 | 38.658 | 28.001 | 2.9 | 1.9 | 1.2 | 0.5 | 0.2
1485 | 30/07/2025 09:58:48.880 | 97.944 | 75 | 99 | 70 | 52 | 27.655 | 9.505 | 6.99 | 134.751 | 28.959 | 28.244 | 27.697 | 603.29 | 25.726 | 26.513 | 1299.933 | 27.082 | 27.319 | 38.607 | 27.001 | 2.9 | 1.5 | 1.2 | 0.5 | 0.2
1486 | 30/07/2025 09:58:50.514 | 97.896 | 75 | 100 | 70 | 52 | 27.285 | 9.281 | 7.031 | 134.845 | 28.966 | 28.227 | 27.725 | 603.438 | 25.732 | 26.493 | 1290.942 | 27.066 | 27.303 | 38.607 | 31.001 | 3.1 | 0.9 | 1 | 0.2 | 0.2
1487 | 30/07/2025 09:58:52.148 | 98.112 | 74 | 100 | 72 | 52 | 30.381 | 9.227 | 7.023 | 134.485 | 28.964 | 28.233 | 27.738 | 603.531 | 25.726 | 26.493 | 1284.645 | 27.07 | 27.295 | 38.147 | 31.001 | 3.1 | 0.9 | 1 | 0.2 | 0.2
1488 | 30/07/2025 09:58:53.783 | 98.136 | 74 | 100 | 70 | 53 | 29.939 | 9.281 | 7.007 | 134.634 | 28.973 | 28.243 | 27.716 | 603.358 | 25.717 | 26.5 | 1287.683 | 27.036 | 27.308 | 38.626 | 31.001 | 3.1 | 0.4 | 1 | 0.2 | 0.2
1489 | 30/07/2025 09:58:55.418 | 98.208 | 75 | 100 | 70 | 52 | 26.475 | 9.344 | 7.004 | 134.739 | 28.974 | 28.247 | 27.714 | 602.22 | 25.719 | 26.483 | 1277.372 | 27.047 | 27.307 | 38.377 | 28.001 | 3.3 | 1.5 | 0.7 | 0.8 | 0.2
1490 | 30/07/2025 09:58:57.051 | 98.016 | 75 | 100 | 69 | 52 | 30.5 | 9.404 | 7.006 | 134.756 | 28.975 | 28.244 | 27.689 | 601.951 | 25.724 | 26.492 | 1280.935 | 27.068 | 27.298 | 38.669 | 25.001 | 3.3 | 1.6 | 0.7 | 0.8 | 0.2
1491 | 30/07/2025 09:58:58.685 | 98.016 | 73 | 100 | 71 | 52 | 27.092 | 9.499 | 7.003 | 134.732 | 28.97 | 28.231 | 27.728 | 602.192 | 25.703 | 26.476 | 1287.726 | 27.066 | 27.296 | 36.559 | 26.001 | 4.3 | 1.1 | 1.2 | 0.5 | 0.1
1492 | 30/07/2025 09:59:00.318 | 97.992 | 74 | 100 | 71 | 52 | 27.961 | 9.557 | 7.005 | 134.243 | 28.967 | 28.243 | 27.716 | 603.251 | 25.712 | 26.503 | 1283.201 | 27.073 | 27.294 | 36.525 | 27.001 | 4.3 | 1 | 1.2 | 0.5 | 0.1
1493 | 30/07/2025 09:59:01.962 | 98.256 | 74 | 100 | 70 | 52 | 30.492 | 9.284 | 7.032 | 134.722 | 28.975 | 28.243 | 27.73 | 602.215 | 25.717 | 26.464 | 1290.037 | 27.02 | 27.312 | 36.627 | 27.001 | 4.3 | 1 | 1.2 | 0.5 | 0.1
1494 | 30/07/2025 09:59:03.599 | 98.16 | 75 | 100 | 70 | 53 | 29.518 | 9.437 | 7.035 | 134.766 | 28.97 | 28.249 | 27.702 | 602.153 | 25.715 | 26.454 | 1284.511 | 27.08 | 27.314 | 36.472 | 28.001 | 3.2 | 0.8 | 0.2 | 0.1 | 0.2
1495 | 30/07/2025 09:59:05.233 | 97.608 | 75 | 100 | 71 | 52 | 30.211 | 9.282 | 7.032 | 134.691 | 28.984 | 28.243 | 27.726 | 602.219 | 25.72 | 26.462 | 1280.498 | 27.071 | 27.306 | 36.603 | 31.001 | 3.2 | 1.1 | 0.2 | 0.1 | 0.2
1496 | 30/07/2025 09:59:06.871 | 97.44 | 74 | 100 | 71 | 52 | 30.367 | 9.139 | 7.005 | 134.679 | 28.967 | 28.235 | 27.733 | 602.209 | 25.73 | 26.464 | 1277.297 | 27.078 | 27.297 | 36.565 | 31.001 | 2.4 | 2 | 0.6 | 0.8 | 0.1
1497 | 30/07/2025 09:59:08.506 | 96.888 | 74 | 100 | 70 | 52 | 26.754 | 9.428 | 7.005 | 134.474 | 28.969 | 28.253 | 27.729 | 602.063 | 25.739 | 26.486 | 1282.919 | 27.05 | 27.297 | 36.743 | 25.001 | 2.4 | 1 | 0.6 | 0.8 | 0.1
1498 | 30/07/2025 09:59:10.140 | 97.008 | 74 | 100 | 71 | 52 | 28.488 | 9.122 | 7.005 | 134.866 | 28.969 | 28.249 | 27.723 | 602.233 | 25.739 | 26.488 | 1289.891 | 27.04 | 27.315 | 36.694 | 25.001 | 2.4 | 1 | 0.6 | 0.8 | 0.1
1499 | 30/07/2025 09:59:11.775 | 97.128 | 76 | 100 | 70 | 52 | 30.545 | 9.29 | 7.032 | 134.461 | 29.103 | 28.236 | 27.692 | 600.547 | 25.726 | 26.506 | 1292.869 | 27.078 | 27.308 | 36.828 | 27.001 | 3.5 | 1.8 | 0.3 | 0.5 | 0.1
1500 | 30/07/2025 09:59:13.412 | 97.2 | 76 | 100 | 69 | 52 | 29.012 | 9.431 | 7.032 | 134.714 | 29 | 28.225 | 27.731 | 600.803 | 25.75 | 26.489 | 1295.676 | 27.065 | 27.293 | 36.717 | 30.001 | 3.5 | 2 | 0.3 | 0.5 | 0.1
1501 | 30/07/2025 09:59:15.048 | 97.512 | 76 | 100 | 70 | 52 | 30.466 | 9.156 | 7.034 | 134.527 | 29.036 | 28.232 | 27.715 | 600.677 | 25.728 | 26.49 | 1297.256 | 27.067 | 27.283 | 36.453 | 31.001 | 4.3 | 1.6 | 1.6 | 0.6 | 0.1
1502 | 30/07/2025 09:59:16.688 | 97.248 | 76 | 100 | 70 | 52 | 30.082 | 9.45 | 7.033 | 134.491 | 29.114 | 28.251 | 27.737 | 600.796 | 25.738 | 26.495 | 1295.255 | 27.046 | 27.3 | 36.657 | 27.001 | 4.3 | 1.1 | 1.6 | 0.6 | 0.1
1503 | 30/07/2025 09:59:18.327 | 97.008 | 75 | 100 | 71 | 52 | 26.578 | 9.348 | 7.035 | 134.612 | 29.096 | 28.257 | 27.718 | 600.619 | 25.714 | 26.504 | 1299.352 | 27.062 | 27.316 | 36.794 | 27.001 | 4.6 | 2.7 | 1 | 1.1 | 0.1
1504 | 30/07/2025 09:59:19.962 | 96.84 | 75 | 100 | 70 | 52 | 29.058 | 9.484 | 7.033 | 134.846 | 29.094 | 28.233 | 27.688 | 600.571 | 25.735 | 26.501 | 1294.529 | 27.076 | 27.302 | 36.68 | 27.001 | 4.6 | 2.7 | 1 | 1.1 | 0.1
1505 | 30/07/2025 09:59:21.598 | 96.72 | 74 | 100 | 70 | 51 | 30.582 | 9.303 | 7.029 | 134.68 | 29.106 | 28.224 | 27.737 | 600.734 | 25.72 | 26.498 | 1292.116 | 27.064 | 27.293 | 36.274 | 26.001 | 4.6 | 2 | 1 | 1.1 | 0.1
1506 | 30/07/2025 09:59:23.234 | 96.816 | 73 | 100 | 70 | 51 | 28.336 | 9.295 | 7.007 | 134.502 | 29.095 | 28.246 | 27.697 | 600.698 | 25.724 | 26.501 | 1293.239 | 27.075 | 27.301 | 36.542 | 29.001 | 3.5 | 0.5 | 0.6 | 0.7 | 0.2
1507 | 30/07/2025 09:59:24.870 | 97.128 | 76 | 100 | 71 | 52 | 30.473 | 9.42 | 7.007 | 134.605 | 29.114 | 28.248 | 27.704 | 600.614 | 25.725 | 26.482 | 1290.747 | 27.041 | 27.312 | 36.78 | 30.001 | 3.5 | 1.1 | 0.6 | 0.7 | 0.2
1508 | 30/07/2025 09:59:26.504 | 97.368 | 76 | 100 | 71 | 52 | 29.468 | 9.394 | 6.936 | 134.798 | 29.125 | 28.245 | 27.699 | 602.015 | 25.723 | 26.504 | 1292.465 | 27.062 | 27.313 | 36.778 | 32.001 | 4.9 | 1.2 | 0 | 0.5 | 0.2
1509 | 30/07/2025 09:59:28.139 | 97.176 | 76 | 100 | 70 | 52 | 26.442 | 9.286 | 6.98 | 134.7 | 29.129 | 28.238 | 27.727 | 602.257 | 25.732 | 26.491 | 1285.726 | 27.067 | 27.304 | 36.704 | 32.001 | 4.9 | 1.2 | 0 | 0.5 | 0.2
1510 | 30/07/2025 09:59:29.776 | 97.2 | 75 | 100 | 71 | 52 | 29.555 | 9.436 | 6.991 | 134.474 | 29.128 | 28.233 | 27.726 | 601.875 | 25.715 | 26.494 | 1287.999 | 27.07 | 27.283 | 36.534 | 29.001 | 4.9 | 1.7 | 0 | 0.5 | 0.2
1511 | 30/07/2025 09:59:31.414 | 96.504 | 76 | 100 | 70 | 50 | 30.575 | 9.286 | 6.934 | 134.678 | 29.131 | 28.242 | 27.704 | 600.86 | 25.729 | 26.487 | 1301.711 | 27.052 | 27.292 | 36.766 | 26.001 | 1.6 | 2.3 | 0 | 0 | 0.1
1512 | 30/07/2025 09:59:33.048 | 96.768 | 74 | 100 | 71 | 51 | 28.538 | 9.471 | 6.936 | 134.606 | 29.139 | 28.255 | 27.708 | 602.141 | 25.722 | 26.636 | 1299.819 | 27.062 | 27.316 | 36.772 | 25.001 | 1.6 | 2.3 | 0 | 0 | 0.1
1513 | 30/07/2025 09:59:34.684 | 97.488 | 76 | 100 | 71 | 53 | 30.566 | 9.285 | 6.935 | 133.346 | 29.122 | 28.239 | 27.708 | 602.025 | 25.722 | 26.627 | 1299.87 | 27.071 | 27.309 | 36.763 | 30.001 | 2.8 | 1.7 | 0.6 | 0 | 0.1
1514 | 30/07/2025 09:59:36.320 | 98.28 | 76 | 100 | 70 | 51 | 28.966 | 9.285 | 6.934 | 133.206 | 29.127 | 28.233 | 27.73 | 602.121 | 25.694 | 26.624 | 1299.802 | 27.063 | 27.308 | 38.411 | 27.001 | 2.8 | 1.1 | 0.6 | 0 | 0.1
1515 | 30/07/2025 09:59:37.962 | 98.976 | 77 | 100 | 71 | 52 | 26.611 | 9.434 | 6.935 | 132.981 | 29.115 | 28.24 | 27.698 | 602.113 | 25.721 | 26.616 | 1291.118 | 27.067 | 27.284 | 36.398 | 27.001 | 2.8 | 1.1 | 0.6 | 0 | 0.1
1516 | 30/07/2025 09:59:39.598 | 98.784 | 75 | 100 | 70 | 52 | 29.952 | 9.293 | 6.987 | 133.2 | 29.125 | 28.243 | 27.733 | 601.997 | 25.718 | 26.62 | 1290.766 | 27.042 | 27.315 | 36.709 | 28.001 | 2.1 | 1 | 1.5 | 0.5 | 0.1
1517 | 30/07/2025 09:59:41.233 | 98.928 | 76 | 100 | 69 | 52 | 30.532 | 9.283 | 6.938 | 133.132 | 29.11 | 28.267 | 27.713 | 602.078 | 25.718 | 26.637 | 1294.628 | 27.078 | 27.324 | 36.595 | 31.001 | 2.1 | 0.4 | 1.5 | 0.5 | 0.1
1518 | 30/07/2025 09:59:42.867 | 99.144 | 77 | 100 | 71 | 52 | 29.052 | 9.494 | 6.934 | 133.344 | 29.117 | 28.241 | 27.709 | 602.117 | 25.739 | 26.621 | 1297.622 | 27.076 | 27.304 | 36.77 | 29.001 | 3.4 | 1.2 | 0.9 | 0.8 | 0.1
1519 | 30/07/2025 09:59:44.502 | 100.032 | 76 | 100 | 71 | 52 | 30.59 | 9.417 | 6.933 | 133.037 | 29.115 | 28.232 | 27.717 | 602.131 | 25.715 | 26.641 | 1306.76 | 27.085 | 27.306 | 36.519 | 25.001 | 3.4 | 1.6 | 0.9 | 0.8 | 0.1
1520 | 30/07/2025 09:59:46.137 | 99.672 | 75 | 100 | 70 | 54 | 28.487 | 9.289 | 6.934 | 132.999 | 29.114 | 28.246 | 27.716 | 602.094 | 25.746 | 26.654 | 1294.413 | 27.058 | 27.285 | 36.629 | 25.001 | 3.4 | 1.6 | 0.9 | 0.8 | 0.1
1521 | 30/07/2025 09:59:47.774 | 99.528 | 76 | 100 | 72 | 52 | 27.035 | 9.43 | 6.994 | 133.287 | 29.099 | 28.245 | 27.73 | 602.276 | 25.735 | 26.65 | 1281.225 | 27.036 | 27.316 | 36.573 | 28.001 | 3 | 1.4 | 1.2 | 0.1 | 0.1
1522 | 30/07/2025 09:59:49.418 | 99.816 | 77 | 100 | 71 | 52 | 30.344 | 9.285 | 6.989 | 133.206 | 29.109 | 28.242 | 27.681 | 602.001 | 25.725 | 26.658 | 1277.926 | 27.076 | 27.306 | 36.679 | 26.001 | 3 | 0.8 | 1.2 | 0.1 | 0.1
1523 | 30/07/2025 09:59:51.059 | 99.48 | 76 | 100 | 71 | 52 | 26.545 | 9.482 | 7.005 | 133.206 | 29.1 | 28.24 | 27.714 | 602.131 | 25.726 | 26.64 | 1284.435 | 27.071 | 27.305 | 36.71 | 27.001 | 2.3 | 1.7 | 0.7 | 0.5 | 0.1
1524 | 30/07/2025 09:59:52.697 | 99.576 | 78 | 100 | 70 | 53 | 29.684 | 9.323 | 6.953 | 133.053 | 29.083 | 28.227 | 27.7 | 602.789 | 25.733 | 26.657 | 1292.704 | 27.065 | 27.28 | 36.491 | 29.001 | 2.3 | 1.4 | 0.7 | 0.5 | 0.1
1525 | 30/07/2025 09:59:54.342 | 99.648 | 77 | 100 | 70 | 52 | 30.644 | 9.479 | 6.935 | 133.002 | 29.092 | 28.247 | 27.733 | 603.532 | 25.726 | 26.646 | 1307.328 | 27.043 | 27.29 | 36.656 | 22.001 | 1.9 | 1.9 | 0.1 | 0 | 0.1
1526 | 30/07/2025 09:59:55.976 | 98.448 | 76 | 100 | 70 | 52 | 27.832 | 9.195 | 7.005 | 134.636 | 29.087 | 28.257 | 27.711 | 602.155 | 25.724 | 26.64 | 1307.403 | 27.047 | 27.305 | 36.689 | 22.001 | 1.9 | 1.9 | 0.1 | 0 | 0.1
1527 | 30/07/2025 09:59:57.613 | 98.16 | 75 | 100 | 70 | 52 | 27.332 | 9.393 | 7.02 | 134.819 | 29.114 | 28.24 | 27.69 | 602.001 | 25.737 | 26.639 | 1314.24 | 27.086 | 27.302 | 36.593 | 28.001 | 1.9 | 1.7 | 0.1 | 0 | 0.1
1528 | 30/07/2025 09:59:59.271 | 98.616 | 77 | 100 | 70 | 53 | 30.384 | 9.541 | 7.03 | 134.622 | 29.124 | 28.229 | 27.739 | 602.233 | 25.726 | 26.641 | 1314.735 | 27.071 | 27.287 | 36.377 | 28.001 | 3.9 | 1 | 0.6 | 0 | 0.1
1529 | 30/07/2025 10:00:00.909 | 98.688 | 78 | 100 | 70 | 52 | 26.58 | 9.446 | 7.031 | 134.677 | 29.144 | 28.234 | 27.719 | 602.176 | 25.738 | 26.638 | 1317.307 | 27.059 | 27.286 | 36.52 | 28.001 | 3.9 | 1.9 | 0.6 | 0 | 0.1
1530 | 30/07/2025 10:00:02.546 | 98.88 | 77 | 100 | 70 | 53 | 29.943 | 9.283 | 7.034 | 134.494 | 29.113 | 28.241 | 27.722 | 602.178 | 25.721 | 26.638 | 1300.153 | 27.045 | 27.319 | 36.668 | 26.001 | 2.8 | 2.8 | 0 | 0.5 | 0.1
1531 | 30/07/2025 10:00:04.185 | 98.424 | 77 | 100 | 69 | 53 | 30.623 | 9.576 | 7.006 | 134.805 | 29.118 | 28.238 | 27.699 | 601.913 | 25.726 | 26.643 | 1292.998 | 27.048 | 27.307 | 36.696 | 26.001 | 2.8 | 2.8 | 0 | 0.5 | 0.1
1532 | 30/07/2025 10:00:05.822 | 98.208 | 76 | 100 | 71 | 52 | 27.255 | 9.429 | 6.96 | 134.833 | 29.128 | 28.237 | 27.72 | 603.333 | 25.714 | 26.626 | 1287.575 | 27.067 | 27.306 | 36.454 | 26.001 | 2.8 | 0.8 | 0 | 0.5 | 0.1
1533 | 30/07/2025 10:00:07.455 | 97.752 | 75 | 100 | 70 | 53 | 27.906 | 9.289 | 6.933 | 134.572 | 29.119 | 28.226 | 27.721 | 602.469 | 25.71 | 26.638 | 1288.194 | 27.084 | 27.282 | 36.294 | 28.001 | 2.9 | 0.9 | 0.6 | 1 | 0.1
1534 | 30/07/2025 10:00:09.090 | 98.208 | 75 | 100 | 70 | 52 | 28.348 | 9.505 | 6.96 | 134.588 | 29.121 | 28.249 | 27.749 | 602.215 | 25.705 | 26.613 | 1281.054 | 27.053 | 27.283 | 36.42 | 26.001 | 2.9 | 1.2 | 0.6 | 1 | 0.1
1535 | 30/07/2025 10:00:10.728 | 98.16 | 76 | 100 | 70 | 53 | 26.987 | 9.284 | 6.989 | 134.438 | 29.109 | 28.249 | 27.699 | 602.022 | 25.72 | 26.626 | 1280.046 | 27.05 | 27.313 | 36.616 | 26.001 | 4.6 | 2.5 | 0.1 | 0 | 0.1
1536 | 30/07/2025 10:00:12.365 | 97.872 | 74 | 100 | 71 | 53 | 30.291 | 9.283 | 6.997 | 134.919 | 29.143 | 28.246 | 27.728 | 602.065 | 25.72 | 26.63 | 1285.462 | 27.07 | 27.313 | 38.649 | 24.001 | 4.6 | 1.1 | 0.1 | 0 | 0.1
1537 | 30/07/2025 10:00:14.002 | 97.008 | 74 | 100 | 71 | 52 | 30.37 | 9.317 | 7.003 | 134.818 | 29.113 | 28.225 | 27.716 | 602.241 | 25.723 | 26.617 | 1289.237 | 27.073 | 27.31 | 36.941 | 24.001 | 4.6 | 1.1 | 0.1 | 0 | 0.1
1538 | 30/07/2025 10:00:15.638 | 96.264 | 73 | 100 | 70 | 53 | 26.761 | 9.288 | 7.005 | 134.546 | 29.115 | 28.233 | 27.733 | 602.087 | 25.73 | 26.633 | 1287.454 | 27.067 | 27.29 | 38.304 | 27.001 | 2.2 | 1.4 | 0.6 | 0.6 | 0.1
1539 | 30/07/2025 10:00:17.274 | 96.456 | 74 | 100 | 70 | 52 | 30.609 | 9.505 | 6.982 | 134.257 | 29.113 | 28.256 | 27.725 | 602.229 | 25.727 | 26.626 | 1285.772 | 27.066 | 27.31 | 38.733 | 25.001 | 2.2 | 1.7 | 0.6 | 0.6 | 0.1
1540 | 30/07/2025 10:00:18.909 | 96.528 | 73 | 100 | 71 | 52 | 27.758 | 9.526 | 6.936 | 134.794 | 29.108 | 28.242 | 27.72 | 602.08 | 25.753 | 26.657 | 1272.16 | 27.032 | 27.313 | 38.488 | 26.001 | 2.6 | 2.1 | 0 | 0.6 | 0.1
1541 | 30/07/2025 10:00:20.544 | 96.384 | 73 | 100 | 71 | 52 | 27.484 | 9.433 | 7.005 | 134.773 | 29.101 | 28.248 | 27.708 | 602.023 | 25.725 | 26.643 | 1270.749 | 27.065 | 27.302 | 38.45 | 30.001 | 2.6 | 2.6 | 0 | 0.6 | 0.1
1542 | 30/07/2025 10:00:22.180 | 96.024 | 73 | 100 | 71 | 53 | 30.458 | 9.399 | 7.005 | 134.546 | 29.101 | 28.23 | 27.706 | 602.101 | 25.73 | 26.653 | 1285.82 | 27.082 | 27.299 | 38.391 | 30.001 | 2.6 | 2.6 | 0 | 0.6 | 0.1
1543 | 30/07/2025 10:00:23.817 | 95.928 | 74 | 100 | 70 | 52 | 30.085 | 9.501 | 7.004 | 134.481 | 29.115 | 28.249 | 27.731 | 602.154 | 25.755 | 26.652 | 1294.921 | 27.059 | 27.275 | 38.285 | 25.001 | 2.8 | 1.3 | 0.6 | 0.5 | 0.1
1544 | 30/07/2025 10:00:25.450 | 96 | 73 | 100 | 71 | 52 | 26.608 | 9.309 | 7.005 | 134.773 | 29.083 | 28.253 | 27.724 | 602.198 | 25.735 | 26.647 | 1289.971 | 27.043 | 27.31 | 38.594 | 22.001 | 2.8 | 1.4 | 0.6 | 0.5 | 0.1
1545 | 30/07/2025 10:00:27.084 | 95.784 | 72 | 100 | 71 | 52 | 29.227 | 9.568 | 7.014 | 134.773 | 29.096 | 28.245 | 27.699 | 600.635 | 25.727 | 26.651 | 1284.877 | 27.069 | 27.3 | 38.581 | 26.001 | 3.7 | 1.6 | 0.4 | 0.3 | 0.1
1546 | 30/07/2025 10:00:28.720 | 95.448 | 72 | 100 | 70 | 52 | 27.324 | 9.44 | 7.033 | 134.5 | 29.092 | 28.254 | 27.699 | 600.651 | 25.723 | 26.643 | 1283.007 | 27.078 | 27.316 | 38.556 | 25.001 | 3.7 | 2 | 0.4 | 0.3 | 0.1
1547 | 30/07/2025 10:00:30.357 | 95.064 | 73 | 100 | 70 | 53 | 27.9 | 9.505 | 7.03 | 134.637 | 29.104 | 28.219 | 27.726 | 601.92 | 25.731 | 26.641 | 1287.18 | 27.066 | 27.288 | 38.216 | 29.001 | 4.4 | 1.6 | 0.6 | 0 | 0.1
1548 | 30/07/2025 10:00:31.993 | 94.608 | 73 | 100 | 70 | 53 | 30.501 | 9.554 | 7.033 | 134.403 | 29.112 | 28.25 | 27.731 | 600.708 | 25.734 | 26.637 | 1289.511 | 27.054 | 27.302 | 38.439 | 29.001 | 4.4 | 1.6 | 0.6 | 0 | 0.1
1549 | 30/07/2025 10:00:33.629 | 95.208 | 73 | 100 | 70 | 53 | 29.595 | 9.434 | 7.035 | 134.755 | 29.11 | 28.249 | 27.719 | 600.601 | 25.724 | 26.652 | 1287.54 | 27.061 | 27.317 | 38.605 | 34.001 | 4.4 | 1.9 | 0.6 | 0 | 0.1
1550 | 30/07/2025 10:00:35.262 | 95.496 | 74 | 100 | 70 | 52 | 26.457 | 9.426 | 7.033 | 134.784 | 29.141 | 28.241 | 27.7 | 600.624 | 25.743 | 26.645 | 1290.314 | 27.072 | 27.303 | 38.637 | 23.001 | 3.6 | 1.8 | 1.8 | 0.8 | 0.2
1551 | 30/07/2025 10:00:36.896 | 95.688 | 73 | 100 | 69 | 52 | 30.463 | 9.308 | 7.034 | 134.455 | 29.124 | 28.229 | 27.692 | 600.668 | 25.721 | 26.645 | 1289.989 | 27.077 | 27.305 | 38.47 | 26.001 | 3.6 | 1.6 | 1.8 | 0.8 | 0.2
1552 | 30/07/2025 10:00:38.537 | 96.312 | 73 | 100 | 72 | 52 | 26.912 | 9.284 | 7.018 | 134.588 | 29.135 | 28.242 | 27.745 | 600.821 | 25.734 | 26.635 | 1288.24 | 27.062 | 27.288 | 38.294 | 25.001 | 1.8 | 2.3 | 0.6 | 0.8 | 0.2
1553 | 30/07/2025 10:00:40.174 | 97.128 | 75 | 100 | 71 | 52 | 28.532 | 9.504 | 7.004 | 134.521 | 29.112 | 28.253 | 27.724 | 600.681 | 25.714 | 26.637 | 1285.161 | 27.051 | 27.324 | 38.537 | 25.001 | 1.8 | 2.3 | 0.6 | 0.8 | 0.2
1554 | 30/07/2025 10:00:41.812 | 97.104 | 74 | 100 | 70 | 52 | 30.571 | 9.379 | 7.005 | 134.755 | 29.134 | 28.238 | 27.702 | 600.729 | 25.715 | 26.637 | 1286.437 | 27.048 | 27.305 | 38.677 | 25.001 | 1.8 | 2.2 | 0.6 | 0.8 | 0.2
1555 | 30/07/2025 10:00:43.450 | 96.792 | 73 | 100 | 71 | 52 | 28.932 | 9.503 | 7.005 | 133.334 | 29.135 | 28.233 | 27.723 | 600.633 | 25.717 | 26.623 | 1289.977 | 27.069 | 27.297 | 38.489 | 24.001 | 5.3 | 0.6 | 1.4 | 0 | 0.2
1556 | 30/07/2025 10:00:45.087 | 96.96 | 73 | 100 | 71 | 52 | 26.614 | 9.293 | 7.005 | 133.1 | 29.117 | 28.226 | 27.717 | 600.698 | 25.692 | 26.631 | 1289.034 | 27.089 | 27.295 | 38.062 | 24.001 | 5.3 | 1.3 | 1.4 | 0 | 0.2
1557 | 30/07/2025 10:00:46.724 | 97.368 | 74 | 100 | 70 | 52 | 29.997 | 9.135 | 7 | 132.988 | 29.104 | 28.241 | 27.736 | 600.694 | 25.713 | 26.621 | 1287.675 | 27.059 | 27.295 | 38.24 | 25.001 | 1.8 | 1.1 | 0.1 | 0 | 0.2
1558 | 30/07/2025 10:00:48.359 | 97.68 | 75 | 100 | 70 | 53 | 26.511 | 9.282 | 6.937 | 133 | 29.114 | 28.249 | 27.717 | 599.416 | 25.72 | 26.63 | 1272.878 | 27.043 | 27.306 | 36.671 | 23.001 | 1.8 | 1.3 | 0.1 | 0 | 0.2
1559 | 30/07/2025 10:00:49.995 | 97.272 | 75 | 100 | 71 | 53 | 28.973 | 9.295 | 6.935 | 133.241 | 29.134 | 28.249 | 27.72 | 599.394 | 25.741 | 26.634 | 1273.683 | 27.059 | 27.305 | 36.761 | 23.001 | 1.8 | 1.3 | 0.1 | 0 | 0.2
1560 | 30/07/2025 10:00:51.633 | 97.008 | 74 | 100 | 70 | 51 | 30.614 | 9.416 | 6.935 | 133.173 | 29.109 | 28.237 | 27.719 | 598.144 | 25.733 | 26.636 | 1267.296 | 27.084 | 27.317 | 36.52 | 26.001 | 2.6 | 3.1 | 0.6 | 1.1 | 0.2
1561 | 30/07/2025 10:00:53.269 | 97.464 | 75 | 100 | 71 | 52 | 28.379 | 9.434 | 6.934 | 133.047 | 29.104 | 28.235 | 27.714 | 598.108 | 25.742 | 26.652 | 1283.111 | 27.059 | 27.273 | 36.495 | 29.001 | 2.6 | 2 | 0.6 | 1.1 | 0.2
1562 | 30/07/2025 10:00:54.905 | 98.232 | 75 | 100 | 70 | 51 | 30.534 | 9.504 | 6.941 | 132.94 | 29.103 | 28.266 | 27.714 | 598.2 | 25.727 | 26.651 | 1290.554 | 27.064 | 27.294 | 36.444 | 30.001 | 3.2 | 1.6 | 0.7 | 1.1 | 0.2
1563 | 30/07/2025 10:00:56.539 | 97.848 | 75 | 100 | 70 | 52 | 29.633 | 9.288 | 6.987 | 133.395 | 29.09 | 28.241 | 27.714 | 599.457 | 25.742 | 26.652 | 1288.47 | 27.03 | 27.303 | 36.666 | 25.001 | 3.2 | 1.6 | 0.7 | 1.1 | 0.2
1564 | 30/07/2025 10:00:58.173 | 98.088 | 77 | 100 | 70 | 52 | 26.497 | 9.395 | 6.995 | 133.116 | 29.099 | 28.245 | 27.706 | 598.091 | 25.727 | 26.644 | 1298.26 | 27.066 | 27.303 | 36.603 | 25.001 | 3.2 | 1.6 | 0.7 | 1.1 | 0.2
1565 | 30/07/2025 10:00:59.808 | 98.088 | 75 | 100 | 71 | 52 | 29.621 | 9.365 | 6.997 | 133.123 | 29.092 | 28.216 | 27.699 | 599.406 | 25.723 | 26.669 | 1306.707 | 27.083 | 27.305 | 36.51 | 28.001 | 3.5 | 1.6 | 0.6 | 0.6 | 0.2
1566 | 30/07/2025 10:01:01.442 | 97.944 | 74 | 100 | 70 | 52 | 30.612 | 9.313 | 7.003 | 133.043 | 29.1 | 28.242 | 27.729 | 599.424 | 25.735 | 26.638 | 1297.449 | 27.056 | 27.278 | 36.382 | 29.001 | 3.5 | 2.2 | 0.6 | 0.6 | 0.2
1567 | 30/07/2025 10:01:03.080 | 98.448 | 74 | 100 | 70 | 52 | 28.525 | 9.213 | 6.997 | 133.055 | 29.096 | 28.247 | 27.714 | 600.652 | 25.733 | 26.646 | 1292.598 | 27.053 | 27.305 | 36.736 | 24.001 | 3.6 | 1.8 | 0 | 0.5 | 0.2
1568 | 30/07/2025 10:01:04.715 | 97.992 | 76 | 100 | 70 | 54 | 30.55 | 9.489 | 6.988 | 133.117 | 29.1 | 28.243 | 27.733 | 600.892 | 25.736 | 26.63 | 1288.202 | 27.038 | 27.31 | 38.617 | 30.001 | 3.6 | 1.9 | 0 | 0.5 | 0.2
1569 | 30/07/2025 10:01:06.350 | 98.184 | 75 | 100 | 71 | 52 | 29.025 | 9.288 | 7.027 | 133.133 | 29.115 | 28.254 | 27.723 | 600.656 | 25.721 | 26.637 | 1283.335 | 27.09 | 27.301 | 38.685 | 26.001 | 1.9 | 2.6 | 0.6 | 0.8 | 0.2
1570 | 30/07/2025 10:01:07.985 | 97.896 | 74 | 100 | 71 | 52 | 26.629 | 9.579 | 7.032 | 133.158 | 29.135 | 28.22 | 27.781 | 599.319 | 25.734 | 26.657 | 1287.289 | 27.062 | 27.294 | 38.131 | 26.001 | 1.9 | 2.6 | 0.6 | 0.8 | 0.2
1571 | 30/07/2025 10:01:09.620 | 97.92 | 74 | 100 | 70 | 52 | 30.033 | 9.508 | 7.033 | 132.859 | 29.13 | 28.246 | 27.733 | 598.238 | 25.719 | 26.643 | 1288.354 | 27.058 | 27.297 | 36.588 | 29.001 | 1.9 | 2.8 | 0.6 | 0.8 | 0.2
1572 | 30/07/2025 10:01:11.255 | 98.448 | 76 | 100 | 70 | 52 | 30.609 | 9.566 | 7.035 | 133.171 | 29.114 | 28.244 | 27.704 | 598.138 | 25.713 | 26.647 | 1298.09 | 27.044 | 27.314 | 38.501 | 31.001 | 3.3 | 2.7 | 1.2 | 0 | 0.3
1573 | 30/07/2025 10:01:12.889 | 98.712 | 76 | 100 | 70 | 52 | 29.09 | 9.507 | 7.034 | 133.055 | 29.128 | 28.244 | 27.858 | 598.075 | 25.712 | 26.638 | 1306.66 | 27.055 | 27.31 | 38.371 | 25.001 | 3.3 | 1.6 | 1.2 | 0 | 0.3
1574 | 30/07/2025 10:01:14.524 | 98.208 | 74 | 100 | 69 | 52 | 30.655 | 9.434 | 7.007 | 133.156 | 29.115 | 28.223 | 27.857 | 598.062 | 25.714 | 26.641 | 1311.893 | 27.068 | 27.304 | 38.457 | 25.001 | 3.6 | 2.7 | 1.1 | 1 | 0.3
1575 | 30/07/2025 10:01:16.159 | 98.472 | 76 | 100 | 70 | 52 | 28.537 | 9.41 | 7.003 | 133.205 | 29.124 | 28.235 | 27.744 | 598.282 | 25.722 | 26.631 | 1317.308 | 27.059 | 27.29 | 38.302 | 25.001 | 3.6 | 2.7 | 1.1 | 1 | 0.3
1576 | 30/07/2025 10:01:17.794 | 97.8 | 74 | 100 | 70 | 52 | 26.968 | 9.474 | 7.007 | 132.704 | 29.116 | 28.249 | 27.873 | 598.09 | 25.704 | 26.622 | 1318.201 | 27.055 | 27.316 | 38.682 | 23.001 | 3.6 | 1.3 | 1.1 | 1 | 0.3
1577 | 30/07/2025 10:01:19.428 | 98.304 | 75 | 100 | 70 | 52 | 30.297 | 9.293 | 7.005 | 133.296 | 29.113 | 28.242 | 27.708 | 599.388 | 25.718 | 26.615 | 1315.021 | 27.049 | 27.295 | 38.529 | 31.001 | 3.2 | 2.5 | 0.7 | 0.5 | 0.3
1578 | 30/07/2025 10:01:21.065 | 98.04 | 77 | 100 | 70 | 51 | 26.493 | 9.283 | 7.006 | 133.081 | 29.109 | 28.254 | 27.83 | 599.216 | 25.723 | 26.612 | 1317.196 | 27.091 | 27.31 | 38.608 | 23.001 | 3.2 | 0.7 | 0.7 | 0.5 | 0.3
1579 | 30/07/2025 10:01:22.698 | 98.544 | 77 | 100 | 70 | 52 | 29.52 | 9.415 | 7.004 | 133.281 | 29.134 | 28.234 | 27.865 | 600.639 | 25.739 | 26.616 | 1321.495 | 27.064 | 27.291 | 36.738 | 23.001 | 3 | 0.9 | 0.1 | 1 | 0.3
1580 | 30/07/2025 10:01:24.334 | 98.592 | 77 | 100 | 70 | 52 | 30.711 | 9.436 | 7.004 | 133.085 | 29.118 | 28.254 | 27.872 | 600.665 | 25.732 | 26.632 | 1316.876 | 27.057 | 27.302 | 38.223 | 27.001 | 3 | 2.1 | 0.1 | 1 | 0.3
1581 | 30/07/2025 10:01:25.973 | 98.4 | 75 | 100 | 71 | 52 | 27.819 | 9.433 | 7.008 | 133.046 | 29.106 | 28.245 | 27.863 | 600.697 | 25.865 | 26.648 | 1302.771 | 27.038 | 27.313 | 38.501 | 27.001 | 3 | 2.1 | 0.1 | 1 | 0.3
1582 | 30/07/2025 10:01:27.609 | 98.736 | 77 | 100 | 70 | 52 | 27.391 | 9.482 | 7.02 | 133.258 | 29.125 | 28.243 | 27.875 | 599.26 | 25.73 | 26.634 | 1304.644 | 27.054 | 27.296 | 38.611 | 30.001 | 2.8 | 0.9 | 0.7 | 0.5 | 0.3
1583 | 30/07/2025 10:01:29.245 | 98.88 | 76 | 99 | 70 | 52 | 29.024 | 9.567 | 7.035 | 133.273 | 29.101 | 28.235 | 27.821 | 599.277 | 25.879 | 26.66 | 1302.178 | 27.075 | 27.294 | 38.482 | 23.001 | 2.8 | 1.6 | 0.7 | 0.5 | 0.3
1584 | 30/07/2025 10:01:30.881 | 98.52 | 76 | 100 | 71 | 53 | 26.665 | 9.436 | 6.961 | 134.617 | 29.097 | 28.217 | 27.9 | 599.686 | 25.878 | 26.66 | 1290.059 | 27.062 | 27.299 | 38.286 | 28.001 | 5 | 2 | 0.9 | 0.6 | 0.2
1585 | 30/07/2025 10:01:32.523 | 98.616 | 75 | 100 | 70 | 52 | 30.972 | 9.505 | 6.935 | 134.261 | 29.087 | 28.249 | 27.872 | 600.701 | 25.719 | 26.651 | 1297.471 | 27.081 | 27.292 | 38.546 | 25.001 | 5 | 2.1 | 0.9 | 0.6 | 0.2
1586 | 30/07/2025 10:01:34.158 | 98.472 | 75 | 100 | 70 | 51 | 30.612 | 9.284 | 6.935 | 134.912 | 29.089 | 28.25 | 27.859 | 600.725 | 25.877 | 26.644 | 1307.469 | 27.029 | 27.297 | 37.014 | 25.001 | 5 | 2.1 | 0.9 | 0.6 | 0.2
1587 | 30/07/2025 10:01:35.795 | 98.928 | 76 | 100 | 70 | 52 | 27.277 | 9.338 | 6.969 | 134.595 | 29.084 | 28.251 | 27.858 | 600.673 | 25.728 | 26.647 | 1319.482 | 27.071 | 27.314 | 36.874 | 28.001 | 3.3 | 2.7 | 1.2 | 0 | 0.3
1588 | 30/07/2025 10:01:37.429 | 98.472 | 75 | 100 | 70 | 53 | 27.921 | 9.47 | 7.006 | 134.709 | 29.103 | 28.229 | 27.866 | 600.691 | 25.72 | 26.661 | 1312.608 | 27.073 | 27.302 | 36.522 | 26.001 | 3.3 | 0.6 | 1.2 | 0 | 0.3
1589 | 30/07/2025 10:01:39.065 | 97.56 | 74 | 100 | 71 | 51 | 28.503 | 9.294 | 6.999 | 134.527 | 29.112 | 28.223 | 27.885 | 600.72 | 25.728 | 26.644 | 1312.151 | 27.074 | 27.306 | 36.435 | 25.001 | 3 | 0.9 | 0 | 0 | 0.3
1590 | 30/07/2025 10:01:40.700 | 97.56 | 76 | 100 | 71 | 52 | 26.926 | 9.442 | 7.006 | 134.326 | 29.122 | 28.243 | 27.867 | 602.088 | 25.871 | 26.653 | 1305.848 | 27.059 | 27.3 | 36.754 | 29.001 | 3 | 5.2 | 0 | 0 | 0.3
1591 | 30/07/2025 10:01:42.337 | 97.296 | 75 | 100 | 70 | 52 | 30.3 | 9.419 | 7.005 | 134.604 | 29.125 | 28.249 | 27.873 | 602.258 | 25.866 | 26.626 | 1288.075 | 27.039 | 27.307 | 36.763 | 23.001 | 3.5 | 1.9 | 0.6 | 0.1 | 0.3
1592 | 30/07/2025 10:01:43.974 | 97.632 | 75 | 100 | 71 | 52 | 30.482 | 9.286 | 7.006 | 134.578 | 29.114 | 28.236 | 27.833 | 601.984 | 25.866 | 26.647 | 1300.968 | 27.085 | 27.31 | 36.542 | 23.001 | 3.5 | 1.9 | 0.6 | 0.1 | 0.3
1593 | 30/07/2025 10:01:45.610 | 98.208 | 76 | 100 | 70 | 52 | 26.941 | 9.502 | 7.003 | 134.585 | 29.137 | 28.224 | 27.872 | 602.103 | 25.87 | 26.645 | 1307.624 | 27.066 | 27.297 | 36.399 | 33.001 | 3.5 | 4.1 | 0.6 | 0.1 | 0.3
1594 | 30/07/2025 10:01:47.245 | 97.752 | 74 | 100 | 71 | 52 | 30.726 | 9.466 | 7.005 | 134.513 | 29.114 | 28.237 | 27.858 | 602.135 | 25.861 | 26.645 | 1304.687 | 27.079 | 27.292 | 36.428 | 26.001 | 2.8 | 2.8 | 2.4 | 0 | 0.3
1595 | 30/07/2025 10:01:48.880 | 97.536 | 76 | 100 | 70 | 51 | 28.027 | 9.498 | 7.005 | 134.589 | 29.125 | 28.246 | 27.849 | 602.128 | 25.88 | 26.628 | 1300.975 | 27.039 | 27.304 | 36.826 | 25.001 | 2.8 | 0.8 | 2.4 | 0 | 0.3
1596 | 30/07/2025 10:01:50.515 | 97.152 | 74 | 100 | 71 | 52 | 27.471 | 9.286 | 7.032 | 134.793 | 29.114 | 28.248 | 27.851 | 602.196 | 25.836 | 26.623 | 1295.753 | 27.061 | 27.318 | 36.725 | 22.001 | 2.7 | 2.9 | 0.9 | 0.5 | 0.2
1597 | 30/07/2025 10:01:52.151 | 97.296 | 75 | 100 | 71 | 52 | 30.511 | 9.245 | 7.015 | 134.632 | 29.118 | 28.241 | 27.848 | 602.014 | 25.86 | 26.611 | 1287.782 | 27.078 | 27.311 | 36.644 | 22.001 | 2.7 | 2.9 | 0.9 | 0.5 | 0.2
1598 | 30/07/2025 10:01:53.787 | 97.176 | 74 | 100 | 70 | 51 | 30.17 | 9.42 | 7.003 | 134.696 | 29.103 | 28.231 | 27.893 | 602.377 | 25.856 | 26.614 | 1292.287 | 27.057 | 27.281 | 36.271 | 23.001 | 2.7 | 2.1 | 0.9 | 0.5 | 0.2
1599 | 30/07/2025 10:01:55.421 | 97.584 | 74 | 100 | 71 | 52 | 26.616 | 9.311 | 6.937 | 134.203 | 29.129 | 28.26 | 27.871 | 602.123 | 25.868 | 26.631 | 1295.279 | 27.074 | 27.317 | 36.595 | 27.001 | 3 | 2.4 | 0.8 | 0.5 | 0.3
1600 | 30/07/2025 10:01:57.057 | 97.752 | 76 | 100 | 70 | 52 | 30.663 | 9.489 | 6.935 | 134.681 | 29.117 | 28.249 | 27.875 | 602.156 | 25.865 | 26.612 | 1295.081 | 27.019 | 27.314 | 36.618 | 25.001 | 3 | 1.2 | 0.8 | 0.5 | 0.3
1601 | 30/07/2025 10:01:58.692 | 97.752 | 76 | 100 | 70 | 52 | 27.378 | 9.286 | 6.935 | 134.627 | 29.109 | 28.25 | 27.837 | 601.928 | 25.878 | 26.644 | 1297.302 | 27.08 | 27.314 | 36.582 | 22.001 | 2.6 | 0.7 | 0.7 | 0.8 | 0.3
1602 | 30/07/2025 10:02:00.325 | 97.56 | 74 | 100 | 71 | 52 | 27.954 | 9.5 | 6.934 | 134.677 | 29.116 | 28.23 | 27.861 | 602.231 | 25.892 | 26.648 | 1297.459 | 27.064 | 27.306 | 36.647 | 26.001 | 2.6 | 1.5 | 0.7 | 0.8 | 0.3
1603 | 30/07/2025 10:02:01.964 | 97.512 | 75 | 100 | 70 | 53 | 30.555 | 9.288 | 6.934 | 134.631 | 29.107 | 28.25 | 27.878 | 602.175 | 25.878 | 26.644 | 1294.412 | 27.072 | 27.301 | 36.417 | 26.001 | 2.6 | 1.5 | 0.7 | 0.8 | 0.3
1604 | 30/07/2025 10:02:03.603 | 98.136 | 76 | 100 | 70 | 53 | 29.6 | 9.284 | 6.938 | 134.535 | 29.1 | 28.25 | 27.86 | 600.671 | 25.883 | 26.655 | 1287.768 | 27.04 | 27.311 | 36.765 | 23.001 | 2.5 | 0.8 | 2.4 | 0.5 | 0.3
1605 | 30/07/2025 10:02:05.239 | 98.064 | 76 | 100 | 70 | 52 | 30.307 | 9.289 | 6.936 | 134.599 | 29.107 | 28.261 | 27.867 | 601.985 | 25.875 | 26.657 | 1292.306 | 27.044 | 27.329 | 36.725 | 35.001 | 2.5 | 0.8 | 2.4 | 0.5 | 0.3
1606 | 30/07/2025 10:02:06.876 | 98.016 | 76 | 100 | 71 | 52 | 30.435 | 9.221 | 6.9 | 134.691 | 29.097 | 28.242 | 27.828 | 601.891 | 25.882 | 26.645 | 1297.344 | 27.074 | 27.306 | 36.727 | 30.001 | 3 | 1 | 0.9 | 0 | 0.4
1607 | 30/07/2025 10:02:08.512 | 98.208 | 76 | 100 | 70 | 52 | 26.8 | 9.404 | 6.898 | 134.707 | 29.1 | 28.224 | 27.874 | 602.318 | 25.873 | 26.641 | 1295.104 | 27.064 | 27.301 | 36.564 | 25.001 | 3 | 2.4 | 0.9 | 0 | 0.4
1608 | 30/07/2025 10:02:10.145 | 97.368 | 76 | 100 | 70 | 52 | 28.462 | 9.436 | 6.901 | 134.38 | 29.086 | 28.251 | 27.869 | 602.115 | 25.872 | 26.661 | 1277.602 | 27.078 | 27.294 | 36.445 | 25.001 | 3 | 2.4 | 0.9 | 0 | 0.4
1609 | 30/07/2025 10:02:11.782 | 97.68 | 76 | 100 | 70 | 53 | 30.545 | 9.28 | 6.986 | 134.785 | 29.105 | 28.242 | 27.859 | 602.193 | 25.887 | 26.634 | 1283.188 | 27.033 | 27.299 | 36.796 | 27.001 | 2.7 | 1.8 | 1.3 | 0.5 | 0.3
1610 | 30/07/2025 10:02:13.415 | 97.368 | 76 | 100 | 70 | 52 | 29.017 | 9.278 | 6.969 | 134.667 | 29.108 | 28.254 | 27.854 | 600.575 | 25.877 | 26.645 | 1287.578 | 27.062 | 27.319 | 36.678 | 26.001 | 2.7 | 2.2 | 1.3 | 0.5 | 0.3
1611 | 30/07/2025 10:02:15.050 | 97.608 | 77 | 100 | 70 | 53 | 30.434 | 9.13 | 6.935 | 134.797 | 29.131 | 28.235 | 27.849 | 600.56 | 25.883 | 26.644 | 1291.98 | 27.066 | 27.302 | 36.688 | 28.001 | 2.2 | 1.4 | 0.6 | 0.5 | 0.3
1612 | 30/07/2025 10:02:16.687 | 97.752 | 77 | 100 | 70 | 52 | 30.152 | 9.438 | 6.934 | 134.425 | 29.13 | 28.213 | 27.878 | 600.877 | 25.869 | 26.648 | 1294.168 | 27.074 | 27.308 | 36.339 | 22.001 | 2.2 | 0.7 | 0.6 | 0.5 | 0.3
1613 | 30/07/2025 10:02:18.322 | 97.56 | 76 | 100 | 71 | 52 | 26.55 | 9.284 | 6.936 | 134.556 | 29.124 | 28.245 | 27.862 | 600.703 | 25.87 | 26.656 | 1292.454 | 27.049 | 27.292 | 36.675 | 28.001 | 3.9 | 1.7 | 0.6 | 0.2 | 0.2
1614 | 30/07/2025 10:02:19.964 | 98.136 | 77 | 100 | 70 | 52 | 29.154 | 9.468 | 6.935 | 134.743 | 29.114 | 28.257 | 27.88 | 600.907 | 25.863 | 26.637 | 1298.286 | 27.042 | 27.316 | 36.587 | 28.001 | 3.9 | 1.7 | 0.6 | 0.2 | 0.2
1615 | 30/07/2025 10:02:21.600 | 97.776 | 75 | 100 | 70 | 52 | 30.667 | 9.508 | 6.936 | 133.047 | 29.129 | 28.24 | 27.839 | 600.605 | 25.862 | 26.642 | 1299.935 | 27.082 | 27.315 | 36.734 | 27.001 | 3.9 | 1.5 | 0.6 | 0.2 | 0.2
1616 | 30/07/2025 10:02:23.234 | 98.376 | 76 | 100 | 70 | 52 | 27.988 | 9.283 | 6.935 | 133.314 | 29.121 | 28.236 | 27.854 | 600.636 | 25.842 | 26.621 | 1299.764 | 27.067 | 27.301 | 36.795 | 33.001 | 3 | 1.5 | 0.1 | 0.8 | 0.2
1617 | 30/07/2025 10:02:24.870 | 98.16 | 78 | 100 | 70 | 52 | 30.577 | 9.295 | 6.936 | 133.23 | 29.118 | 28.231 | 27.856 | 600.865 | 25.851 | 26.63 | 1297.332 | 27.081 | 27.281 | 36.513 | 28.001 | 3 | 1.3 | 0.1 | 0.8 | 0.2
1618 | 30/07/2025 10:02:26.504 | 98.352 | 77 | 100 | 70 | 52 | 29.764 | 9.414 | 6.936 | 134.66 | 29.127 | 28.254 | 27.872 | 600.768 | 25.877 | 26.613 | 1307.33 | 27.053 | 27.315 | 36.693 | 28.001 | 1.8 | 3 | 0.4 | 0.6 | 0.3
1619 | 30/07/2025 10:02:28.137 | 98.184 | 78 | 100 | 70 | 52 | 26.542 | 9.287 | 6.988 | 134.675 | 29.1 | 28.265 | 27.854 | 600.607 | 25.845 | 26.614 | 1302.319 | 27.048 | 27.32 | 38.459 | 28.001 | 1.8 | 3 | 0.4 | 0.6 | 0.3
1620 | 30/07/2025 10:02:29.772 | 98.232 | 76 | 100 | 70 | 52 | 29.633 | 9.287 | 7.007 | 134.694 | 29.109 | 28.234 | 27.832 | 600.526 | 25.868 | 26.632 | 1292.862 | 27.069 | 27.308 | 37.275 | 28.001 | 1.8 | 1.6 | 0.4 | 0.6 | 0.3
1621 | 30/07/2025 10:02:31.407 | 97.968 | 77 | 100 | 70 | 50 | 30.728 | 9.398 | 7.032 | 134.639 | 29.112 | 28.231 | 27.886 | 600.837 | 25.872 | 26.613 | 1287.779 | 27.064 | 27.284 | 38.451 | 21.001 | 2.6 | 2.7 | 0 | 0.5 | 0.3
1622 | 30/07/2025 10:02:33.042 | 97.584 | 78 | 100 | 69 | 52 | 28.496 | 9.433 | 7.032 | 134.411 | 29.12 | 28.243 | 27.867 | 600.762 | 25.893 | 26.624 | 1289.41 | 27.057 | 27.282 | 38.493 | 26.001 | 2.6 | 1.1 | 0 | 0.5 | 0.3
1623 | 30/07/2025 10:02:34.691 | 97.728 | 76 | 100 | 71 | 52 | 30.611 | 9.33 | 7.033 | 134.685 | 29.107 | 28.255 | 27.866 | 600.838 | 25.868 | 26.646 | 1302.236 | 27.04 | 27.316 | 38.567 | 25.001 | 3.2 | 2.5 | 0.6 | 0 | 0.3
1624 | 30/07/2025 10:02:36.323 | 97.392 | 76 | 100 | 70 | 52 | 29.215 | 9.392 | 7.034 | 134.612 | 29.104 | 28.24 | 27.821 | 600.584 | 25.874 | 26.652 | 1314.847 | 27.076 | 27.303 | 38.561 | 27.001 | 3.2 | 1.2 | 0.6 | 0 | 0.3
1625 | 30/07/2025 10:02:37.963 | 98.088 | 77 | 100 | 72 | 52 | 26.663 | 9.561 | 7.032 | 134.648 | 29.119 | 28.229 | 27.873 | 602.06 | 25.887 | 26.642 | 1306.977 | 27.065 | 27.302 | 36.682 | 27.001 | 3.2 | 1.2 | 0.6 | 0 | 0.3
1626 | 30/07/2025 10:02:39.597 | 98.088 | 76 | 100 | 71 | 52 | 30.084 | 9.292 | 7.031 | 134.352 | 29.087 | 28.237 | 27.87 | 600.833 | 25.87 | 26.655 | 1306.987 | 27.073 | 27.302 | 38.332 | 28.001 | 2.8 | 1.7 | 1.2 | 0 | 0.3
1627 | 30/07/2025 10:02:41.233 | 97.728 | 76 | 100 | 70 | 53 | 30.653 | 9.574 | 7.033 | 134.546 | 29.083 | 28.25 | 27.869 | 600.674 | 25.867 | 26.642 | 1297.613 | 27.038 | 27.301 | 38.715 | 27.001 | 2.8 | 3.2 | 1.2 | 0 | 0.3
1628 | 30/07/2025 10:02:42.866 | 97.608 | 77 | 100 | 70 | 53 | 29.024 | 9.582 | 7.033 | 134.571 | 29.087 | 28.261 | 27.859 | 600.58 | 25.873 | 26.65 | 1297.127 | 27.059 | 27.325 | 38.558 | 26.001 | 3.5 | 0.4 | 1.2 | 0.6 | 0.3
1629 | 30/07/2025 10:02:44.501 | 97.632 | 75 | 100 | 70 | 52 | 30.652 | 9.43 | 7.006 | 134.626 | 29.094 | 28.24 | 27.816 | 600.506 | 25.876 | 26.655 | 1292.508 | 27.072 | 27.304 | 36.755 | 28.001 | 3.5 | 0.6 | 1.2 | 0.6 | 0.3
1630 | 30/07/2025 10:02:46.135 | 98.112 | 75 | 100 | 71 | 52 | 28.405 | 9.433 | 7.004 | 134.705 | 29.107 | 28.232 | 27.869 | 602.15 | 25.866 | 26.641 | 1289.893 | 27.064 | 27.299 | 36.526 | 28.001 | 3.5 | 0.6 | 1.2 | 0.6 | 0.3
1631 | 30/07/2025 10:02:47.771 | 98.664 | 76 | 100 | 72 | 51 | 26.929 | 9.435 | 7.034 | 134.485 | 29.112 | 28.244 | 27.852 | 602.17 | 25.874 | 26.651 | 1297.236 | 27.074 | 27.289 | 36.441 | 28.001 | 3.7 | 3.2 | 0.1 | 0 | 0.2
1632 | 30/07/2025 10:02:49.411 | 98.736 | 77 | 100 | 69 | 52 | 30.294 | 9.319 | 7.032 | 134.678 | 29.139 | 28.246 | 27.87 | 602.087 | 25.866 | 26.639 | 1297.609 | 27.023 | 27.307 | 36.808 | 24.001 | 3.7 | 2.4 | 0.1 | 0 | 0.2
1633 | 30/07/2025 10:02:51.047 | 99.432 | 77 | 100 | 70 | 52 | 26.515 | 9.288 | 7.033 | 134.657 | 29.132 | 28.245 | 27.853 | 602.034 | 25.873 | 26.653 | 1296.942 | 27.042 | 27.306 | 38.204 | 25.001 | 2.5 | 1.7 | 0.6 | 0.1 | 0.2
1634 | 30/07/2025 10:02:52.683 | 99.624 | 75 | 100 | 71 | 51 | 29.56 | 9.577 | 7.033 | 134.777 | 29.135 | 28.239 | 27.859 | 601.937 | 25.861 | 26.632 | 1290.075 | 27.065 | 27.308 | 38.447 | 28.001 | 2.5 | 1.5 | 0.6 | 0.1 | 0.2
1635 | 30/07/2025 10:02:54.319 | 99.36 | 77 | 100 | 70 | 52 | 30.722 | 9.434 | 7.031 | 134.575 | 29.109 | 28.235 | 27.873 | 602.235 | 25.855 | 26.634 | 1292.506 | 27.082 | 27.309 | 38.367 | 28.001 | 2.5 | 1.5 | 0.6 | 0.1 | 0.2
1636 | 30/07/2025 10:02:55.953 | 99.096 | 77 | 100 | 70 | 52 | 27.943 | 9.29 | 7.034 | 134.644 | 29.131 | 28.247 | 27.865 | 602.104 | 25.855 | 26.644 | 1297.348 | 27.058 | 27.293 | 38.554 | 26.001 | 2.9 | 1.6 | 0.9 | 0 | 0.1
1637 | 30/07/2025 10:02:57.588 | 98.472 | 75 | 100 | 70 | 52 | 27.486 | 9.321 | 7.005 | 134.666 | 29.118 | 28.251 | 27.86 | 602.262 | 25.863 | 26.626 | 1306.16 | 27.033 | 27.323 | 38.502 | 32.001 | 2.9 | 1.6 | 0.9 | 0 | 0.1
1638 | 30/07/2025 10:02:59.222 | 98.52 | 78 | 100 | 70 | 52 | 29.196 | 9.281 | 7.005 | 134.918 | 29.13 | 28.249 | 27.848 | 600.68 | 25.865 | 26.625 | 1304.631 | 27.045 | 27.298 | 38.447 | 28.001 | 3.4 | 2.3 | 1.5 | 0.2 | 0.1
1639 | 30/07/2025 10:03:00.863 | 98.256 | 75 | 100 | 72 | 52 | 26.666 | 9.285 | 7.006 | 134.597 | 29.121 | 28.236 | 27.861 | 601.843 | 25.863 | 26.614 | 1298.379 | 27.076 | 27.317 | 38.529 | 27.001 | 3.4 | 1.4 | 1.5 | 0.2 | 0.1
1640 | 30/07/2025 10:03:02.501 | 98.4 | 77 | 100 | 70 | 53 | 30.047 | 9.197 | 7.005 | 134.451 | 29.126 | 28.237 | 27.863 | 602.121 | 25.865 | 26.622 | 1304.54 | 27.071 | 27.284 | 36.494 | 26.001 | 3 | 2.2 | 0.6 | 0.8 | 0.2
1641 | 30/07/2025 10:03:04.133 | 98.304 | 74 | 100 | 70 | 52 | 30.696 | 9.282 | 7.033 | 134.57 | 29.122 | 28.253 | 27.86 | 602.19 | 25.878 | 26.616 | 1298.467 | 27.046 | 27.301 | 36.751 | 26.001 | 3 | 2.2 | 0.6 | 0.8 | 0.2
1642 | 30/07/2025 10:03:06.001 | 98.136 | 76 | 99 | 71 | 52 | 27.555 | 9.357 | 7.035 | 134.684 | 29.113 | 28.264 | 27.844 | 602.129 | 25.877 | 26.627 | 1293.987 | 27.056 | 27.318 | 36.795 | 31.001 | 3 | 1.9 | 0.6 | 0.8 | 0.2
1643 | 30/07/2025 10:03:07.637 | 97.92 | 76 | 100 | 69 | 53 | 28.073 | 9.284 | 7.032 | 134.696 | 29.113 | 28.232 | 27.832 | 601.893 | 25.875 | 26.644 | 1292.177 | 27.079 | 27.31 | 36.585 | 27.001 | 2.7 | 2.1 | 1.2 | 0.7 | 0.1
1644 | 30/07/2025 10:03:09.275 | 98.304 | 76 | 100 | 71 | 52 | 30.548 | 9.44 | 7.069 | 134.671 | 29.111 | 28.233 | 27.893 | 602.207 | 25.879 | 26.638 | 1285.275 | 27.056 | 27.292 | 36.311 | 29.001 | 2.7 | 3.6 | 1.2 | 0.7 | 0.1
1645 | 30/07/2025 10:03:10.911 | 98.16 | 74 | 100 | 71 | 53 | 29.749 | 9.43 | 7.035 | 134.294 | 29.106 | 28.24 | 27.856 | 600.626 | 25.873 | 26.664 | 1292.409 | 27.075 | 27.299 | 36.612 | 29.001 | 3.1 | 1.5 | 1 | 0.1 | 0.2
1646 | 30/07/2025 10:03:12.547 | 97.896 | 77 | 100 | 70 | 52 | 30.358 | 9.284 | 7.033 | 134.66 | 29.098 | 28.261 | 27.869 | 600.796 | 25.873 | 26.643 | 1290.449 | 27.044 | 27.322 | 36.775 | 24.001 | 3.1 | 2.2 | 1 | 0.1 | 0.2
1647 | 30/07/2025 10:03:14.183 | 97.56 | 74 | 100 | 70 | 52 | 30.501 | 9.429 | 7.063 | 134.776 | 29.081 | 28.247 | 27.839 | 600.62 | 25.865 | 26.643 | 1297.334 | 27.059 | 27.298 | 36.762 | 24.001 | 3.1 | 2.2 | 1 | 0.1 | 0.2
1648 | 30/07/2025 10:03:15.822 | 97.536 | 75 | 100 | 71 | 51 | 26.92 | 9.499 | 7.07 | 134.67 | 29.095 | 28.231 | 27.873 | 600.643 | 25.874 | 26.641 | 1307.576 | 27.067 | 27.306 | 36.738 | 26.001 | 2.9 | 1.1 | 0.6 | 0.5 | 0.2
1649 | 30/07/2025 10:03:17.459 | 97.416 | 74 | 100 | 70 | 53 | 28.452 | 9.518 | 7.07 | 134.6 | 29.222 | 28.244 | 27.868 | 599.359 | 25.868 | 26.659 | 1306.72 | 27.072 | 27.319 | 36.348 | 30.001 | 2.9 | 2.3 | 0.6 | 0.5 | 0.2
1650 | 30/07/2025 10:03:19.096 | 97.368 | 75 | 99 | 71 | 52 | 30.644 | 9.283 | 7.037 | 134.505 | 29.095 | 28.24 | 27.87 | 599.558 | 25.872 | 26.647 | 1296.935 | 27.046 | 27.297 | 38.706 | 31.001 | 1.1 | 1.2 | 1.4 | 0.2 | 0.2
1651 | 30/07/2025 10:03:20.730 | 97.632 | 75 | 100 | 71 | 52 | 27.332 | 9.42 | 7.033 | 134.581 | 29.251 | 28.257 | 27.866 | 599.501 | 25.868 | 26.643 | 1294.369 | 27.053 | 27.309 | 38.617 | 27.001 | 1.1 | 1.9 | 1.4 | 0.2 | 0.2
1652 | 30/07/2025 10:03:22.369 | 97.248 | 76 | 100 | 71 | 53 | 30.464 | 9.538 | 7.034 | 134.932 | 29.286 | 28.241 | 27.844 | 600.505 | 25.884 | 26.648 | 1287.635 | 27.069 | 27.315 | 38.586 | 28.001 | 2.6 | 2.7 | 1.2 | 0.5 | 0.2
1653 | 30/07/2025 10:03:24.009 | 97.104 | 73 | 100 | 69 | 52 | 30.144 | 9.581 | 7.033 | 134.764 | 29.262 | 28.221 | 27.872 | 600.744 | 25.856 | 26.639 | 1303.891 | 27.069 | 27.307 | 38.452 | 28.001 | 2.6 | 2.7 | 1.2 | 0.5 | 0.2
1654 | 30/07/2025 10:03:25.644 | 97.416 | 77 | 100 | 70 | 52 | 26.624 | 9.43 | 7.007 | 134.439 | 29.256 | 28.246 | 27.858 | 600.716 | 25.871 | 26.66 | 1307.037 | 27.067 | 27.3 | 38.287 | 30.001 | 2.6 | 1.4 | 1.2 | 0.5 | 0.2
1655 | 30/07/2025 10:03:27.279 | 97.272 | 75 | 100 | 70 | 52 | 29.042 | 9.285 | 7.019 | 134.732 | 29.285 | 28.25 | 27.866 | 600.803 | 25.862 | 26.631 | 1307.525 | 27.034 | 27.309 | 38.588 | 21.001 | 1.8 | 1.6 | 0.3 | 0.5 | 0.2
1656 | 30/07/2025 10:03:28.916 | 97.344 | 75 | 100 | 70 | 52 | 27.327 | 9.284 | 7.036 | 134.817 | 29.274 | 28.251 | 27.846 | 600.662 | 25.865 | 26.641 | 1302.89 | 27.046 | 27.306 | 38.742 | 24.001 | 1.8 | 0.9 | 0.3 | 0.5 | 0.2
1657 | 30/07/2025 10:03:30.550 | 96.696 | 74 | 100 | 70 | 52 | 27.921 | 9.435 | 7.033 | 134.679 | 29.268 | 28.244 | 27.838 | 600.463 | 25.864 | 26.621 | 1299.924 | 27.077 | 27.3 | 38.531 | 25.001 | 2.5 | 1.1 | 1 | 0.8 | 0.3
1658 | 30/07/2025 10:03:32.186 | 96.96 | 74 | 100 | 70 | 52 | 30.57 | 9.509 | 7.033 | 134.473 | 29.266 | 28.21 | 27.868 | 600.802 | 25.861 | 26.624 | 1302.072 | 27.087 | 27.304 | 38.438 | 25.001 | 2.5 | 1.1 | 1 | 0.8 | 0.3
1659 | 30/07/2025 10:03:33.823 | 97.008 | 76 | 100 | 70 | 52 | 29.673 | 9.578 | 7.033 | 134.549 | 29.283 | 28.252 | 27.862 | 600.713 | 25.86 | 26.628 | 1299.595 | 27.063 | 27.284 | 38.496 | 31.001 | 2.5 | 1.8 | 1 | 0.8 | 0.3
1660 | 30/07/2025 10:03:35.458 | 96.816 | 74 | 100 | 71 | 52 | 26.547 | 9.586 | 7.033 | 134.639 | 29.266 | 28.256 | 27.862 | 600.76 | 25.853 | 26.619 | 1290.24 | 27.042 | 27.313 | 36.792 | 31.001 | 2.3 | 0.9 | 0 | 0.7 | 0.2
1661 | 30/07/2025 10:03:37.092 | 96.528 | 73 | 100 | 71 | 53 | 29.631 | 9.286 | 7.035 | 134.68 | 29.263 | 28.241 | 27.844 | 600.53 | 25.867 | 26.635 | 1297.208 | 27.07 | 27.308 | 36.729 | 29.001 | 2.3 | 0.6 | 0 | 0.7 | 0.2
1662 | 30/07/2025 10:03:38.727 | 96.384 | 73 | 99 | 71 | 53 | 27.047 | 9.504 | 7.032 | 134.762 | 29.262 | 28.236 | 27.849 | 600.446 | 25.872 | 26.63 | 1294.771 | 27.079 | 27.32 | 36.689 | 22.001 | 4.7 | 0.9 | 0 | 0 | 0.2
1663 | 30/07/2025 10:03:40.361 | 95.832 | 74 | 100 | 71 | 52 | 28.604 | 9.507 | 7.032 | 134.502 | 29.251 | 28.229 | 27.867 | 600.863 | 25.867 | 26.638 | 1304.198 | 27.059 | 27.284 | 36.52 | 25.001 | 4.7 | 1.8 | 0 | 0 | 0.2
1664 | 30/07/2025 10:03:41.996 | 95.76 | 74 | 100 | 70 | 52 | 30.57 | 9.429 | 7.032 | 134.439 | 29.259 | 28.254 | 27.876 | 600.75 | 25.877 | 26.634 | 1288.126 | 27.045 | 27.299 | 36.556 | 25.001 | 4.7 | 1.8 | 0 | 0 | 0.2
1665 | 30/07/2025 10:03:43.630 | 95.496 | 73 | 100 | 70 | 52 | 29.335 | 9.331 | 7.034 | 134.591 | 29.253 | 28.261 | 27.85 | 600.614 | 25.874 | 26.656 | 1287.623 | 27.047 | 27.313 | 36.578 | 22.001 | 3.3 | 0.9 | 0.4 | 0.1 | 0.2
1666 | 30/07/2025 10:03:45.264 | 94.584 | 73 | 100 | 71 | 52 | 26.693 | 9.434 | 7.032 | 134.686 | 29.26 | 28.241 | 27.825 | 600.52 | 25.887 | 26.645 | 1281.478 | 27.081 | 27.3 | 36.64 | 28.001 | 3.3 | 1.3 | 0.4 | 0.1 | 0.2
1667 | 30/07/2025 10:03:46.900 | 94.8 | 72 | 100 | 70 | 53 | 30.198 | 9.502 | 7.033 | 134.512 | 29.239 | 28.23 | 27.84 | 600.603 | 25.873 | 26.66 | 1280.01 | 27.09 | 27.306 | 36.647 | 25.001 | 3.3 | 1 | 0.6 | 0.6 | 0.1
1668 | 30/07/2025 10:03:48.536 | 94.608 | 73 | 100 | 71 | 52 | 26.654 | 9.288 | 7.029 | 134.584 | 29.259 | 28.24 | 27.87 | 600.752 | 25.886 | 26.648 | 1274.762 | 27.055 | 27.285 | 36.571 | 28.001 | 3.3 | 1 | 0.6 | 0.6 | 0.1
1669 | 30/07/2025 10:03:50.170 | 93.936 | 74 | 100 | 71 | 52 | 29.127 | 9.499 | 7.034 | 134.578 | 29.248 | 28.25 | 27.87 | 600.714 | 25.875 | 26.651 | 1285.287 | 27.046 | 27.327 | 36.791 | 28.001 | 3.3 | 1 | 0.6 | 0.6 | 0.1
1670 | 30/07/2025 10:03:51.805 | 94.584 | 72 | 100 | 70 | 52 | 30.715 | 9.283 | 7.02 | 134.704 | 29.248 | 28.248 | 27.833 | 600.616 | 25.875 | 26.647 | 1286.687 | 27.049 | 27.307 | 36.856 | 22.001 | 1.8 | 1.4 | 0.1 | 0.2 | 0.2
1671 | 30/07/2025 10:03:53.439 | 94.416 | 73 | 100 | 70 | 52 | 28.603 | 9.287 | 7.003 | 134.824 | 29.253 | 28.236 | 27.86 | 600.668 | 25.869 | 26.631 | 1291.939 | 27.06 | 27.303 | 38.436 | 24.001 | 1.8 | 1.3 | 0.1 | 0.2 | 0.2
1672 | 30/07/2025 10:03:55.075 | 94.56 | 74 | 100 | 70 | 54 | 26.911 | 9.437 | 7.002 | 134.462 | 29.258 | 28.237 | 27.889 | 602.07 | 25.877 | 26.644 | 1276.928 | 27.086 | 27.286 | 38.178 | 27.001 | 2.3 | 1.2 | 0.9 | 0.8 | 0.2
1673 | 30/07/2025 10:03:56.711 | 95.352 | 73 | 100 | 71 | 52 | 29.775 | 9.433 | 7.005 | 134.421 | 29.258 | 28.246 | 27.864 | 602.172 | 25.86 | 26.649 | 1277.376 | 27.061 | 27.286 | 38.247 | 28.001 | 2.3 | 2.1 | 0.9 | 0.8 | 0.2
1674 | 30/07/2025 10:03:58.346 | 95.232 | 74 | 100 | 70 | 50 | 26.531 | 9.297 | 7.005 | 134.592 | 29.268 | 28.244 | 27.858 | 601.987 | 25.874 | 26.648 | 1287.573 | 27.058 | 27.308 | 38.442 | 28.001 | 1.8 | 0.8 | 0.1 | 0.2 | 0.2
1675 | 30/07/2025 10:03:59.982 | 95.472 | 74 | 100 | 71 | 52 | 29.62 | 9.428 | 7.004 | 134.728 | 29.266 | 28.252 | 27.832 | 602.048 | 25.883 | 26.631 | 1278.425 | 27.058 | 27.299 | 37.981 | 28.001 | 1.8 | 0.8 | 0.1 | 0.2 | 0.2
1676 | 30/07/2025 10:04:01.612 | 95.4 | 75 | 100 | 70 | 52 | 30.829 | 9.577 | 7.004 | 134.716 | 29.269 | 28.233 | 27.869 | 602.196 | 25.877 | 26.639 | 1277.039 | 27.077 | 27.31 | 36.518 | 29.001 | 1.8 | 0.8 | 0.1 | 0.2 | 0.2
1677 | 30/07/2025 10:04:03.246 | 95.952 | 74 | 100 | 69 | 52 | 27.877 | 9.582 | 7.005 | 134.62 | 29.254 | 28.233 | 27.858 | 602.008 | 25.855 | 26.643 | 1272.092 | 27.058 | 27.293 | 37.843 | 24.001 | 1.9 | 0.8 | 0.6 | 0.3 | 0.2
1678 | 30/07/2025 10:04:04.880 | 95.448 | 76 | 100 | 70 | 52 | 30.663 | 9.581 | 7.005 | 134.459 | 29.26 | 28.256 | 27.869 | 602.157 | 25.851 | 26.63 | 1270.656 | 27.067 | 27.306 | 38.336 | 28.001 | 1.9 | 2.6 | 0.6 | 0.3 | 0.2
1679 | 30/07/2025 10:04:06.515 | 95.976 | 75 | 100 | 71 | 52 | 29.08 | 9.426 | 7.034 | 134.793 | 29.268 | 28.239 | 27.862 | 602.046 | 25.866 | 26.643 | 1286.811 | 27.031 | 27.316 | 38.702 | 24.001 | 2.4 | 1 | 0.6 | 0.3 | 0.3
1680 | 30/07/2025 10:04:08.150 | 96.312 | 76 | 100 | 71 | 52 | 26.677 | 9.638 | 7.023 | 134.632 | 29.261 | 28.241 | 27.849 | 602.05 | 25.849 | 26.614 | 1286.869 | 27.07 | 27.302 | 36.673 | 24.001 | 2.4 | 1 | 0.6 | 0.3 | 0.3
1681 | 30/07/2025 10:04:09.786 | 96.48 | 76 | 100 | 70 | 54 | 30.043 | 9.476 | 7.006 | 134.536 | 29.261 | 28.214 | 27.856 | 602.142 | 25.864 | 26.608 | 1277.132 | 27.08 | 27.302 | 36.591 | 26.001 | 2.4 | 1.7 | 0.6 | 0.3 | 0.3
1682 | 30/07/2025 10:04:11.423 | 96.216 | 76 | 100 | 71 | 52 | 30.735 | 9.447 | 7.004 | 134.84 | 29.27 | 28.257 | 27.876 | 602.17 | 25.875 | 26.612 | 1279.641 | 27.058 | 27.279 | 36.626 | 27.001 | 2.4 | 1.2 | 0.4 | 0.5 | 0.3
1683 | 30/07/2025 10:04:13.057 | 96.504 | 76 | 100 | 70 | 54 | 27.43 | 9.284 | 7.011 | 134.607 | 29.249 | 28.256 | 27.877 | 602.165 | 25.867 | 26.759 | 1282.617 | 27.045 | 27.325 | 36.563 | 26.001 | 2.4 | 1 | 0.4 | 0.5 | 0.3
1684 | 30/07/2025 10:04:14.692 | 96.696 | 75 | 100 | 71 | 52 | 30.722 | 9.42 | 7.032 | 134.821 | 29.271 | 28.244 | 27.856 | 602.168 | 25.873 | 26.617 | 1277.271 | 27.04 | 27.306 | 36.616 | 28.001 | 4.1 | 0.6 | 1.2 | 1.1 | 0.2
1685 | 30/07/2025 10:04:16.327 | 96.504 | 76 | 100 | 71 | 52 | 28.73 | 9.43 | 7.033 | 134.62 | 29.26 | 28.241 | 27.853 | 601.946 | 25.876 | 26.676 | 1267.492 | 27.094 | 27.322 | 36.612 | 29.001 | 4.1 | 0.9 | 1.2 | 1.1 | 0.2
1686 | 30/07/2025 10:04:17.968 | 96.936 | 76 | 100 | 70 | 52 | 27.091 | 9.374 | 7.032 | 134.55 | 29.26 | 28.229 | 27.876 | 602.124 | 25.892 | 26.741 | 1280.391 | 27.065 | 27.288 | 36.484 | 29.001 | 4.1 | 0.9 | 1.2 | 1.1 | 0.2
1687 | 30/07/2025 10:04:19.604 | 97.08 | 76 | 99 | 70 | 53 | 30.4 | 9.312 | 7.032 | 134.504 | 29.253 | 28.253 | 27.88 | 602.204 | 25.875 | 26.651 | 1287.174 | 27.05 | 27.308 | 36.509 | 24.001 | 3.1 | 1 | 0.1 | 0.8 | 0.2
1688 | 30/07/2025 10:04:21.238 | 97.44 | 76 | 100 | 71 | 51 | 30.594 | 9.285 | 7.033 | 134.707 | 29.243 | 28.249 | 27.858 | 602.11 | 25.883 | 26.809 | 1282.629 | 27.049 | 27.322 | 36.774 | 25.001 | 3.1 | 1.8 | 0.1 | 0.8 | 0.2
1689 | 30/07/2025 10:04:22.874 | 97.464 | 76 | 100 | 70 | 52 | 29.711 | 9.425 | 7.033 | 134.711 | 29.238 | 28.247 | 27.861 | 602.067 | 25.862 | 26.802 | 1294.115 | 27.059 | 27.316 | 36.699 | 28.001 | 2.9 | 2 | 0.6 | 0.8 | 0.1
1690 | 30/07/2025 10:04:24.509 | 97.296 | 76 | 100 | 70 | 52 | 30.803 | 9.43 | 7.025 | 134.69 | 29.239 | 28.228 | 27.835 | 602.014 | 25.871 | 26.674 | 1292.429 | 27.078 | 27.304 | 36.63 | 28.001 | 2.9 | 3.1 | 0.6 | 0.8 | 0.1
1691 | 30/07/2025 10:04:26.144 | 97.176 | 77 | 100 | 70 | 52 | 28.07 | 9.361 | 7.003 | 134.501 | 29.247 | 28.236 | 27.879 | 602.189 | 25.878 | 26.795 | 1279.182 | 27.058 | 27.278 | 36.472 | 28.001 | 2.9 | 3.1 | 0.6 | 0.8 | 0.1
1692 | 30/07/2025 10:04:27.778 | 97.392 | 77 | 100 | 70 | 53 | 27.336 | 9.515 | 7.005 | 134.513 | 29.243 | 28.269 | 27.864 | 602.079 | 25.868 | 26.786 | 1287.177 | 27.062 | 27.313 | 36.629 | 25.001 | 2 | 1.6 | 0.6 | 1.2 | 0.1
1693 | 30/07/2025 10:04:29.415 | 97.44 | 76 | 100 | 71 | 52 | 30.497 | 9.574 | 7.005 | 134.753 | 29.267 | 28.245 | 27.852 | 602.027 | 25.863 | 26.774 | 1278.262 | 27.049 | 27.308 | 36.713 | 29.001 | 2 | 2.7 | 0.6 | 1.2 | 0.1
1694 | 30/07/2025 10:04:31.050 | 97.128 | 74 | 100 | 72 | 51 | 30.248 | 9.507 | 7.004 | 134.675 | 29.27 | 28.235 | 27.864 | 602.102 | 25.866 | 26.65 | 1273.768 | 27.061 | 27.308 | 36.474 | 23.001 | 2 | 1.1 | 0.9 | 0.3 | 0.2
1695 | 30/07/2025 10:04:32.685 | 97.8 | 76 | 100 | 70 | 52 | 30.035 | 9.289 | 7.004 | 134.678 | 29.277 | 28.218 | 27.861 | 602.142 | 25.876 | 26.79 | 1266.032 | 27.069 | 27.304 | 36.496 | 25.001 | 2 | 0.9 | 0.9 | 0.3 | 0.2
1696 | 30/07/2025 10:04:34.321 | 97.656 | 77 | 100 | 70 | 52 | 30.757 | 9.342 | 7.004 | 134.372 | 29.272 | 28.252 | 27.873 | 600.674 | 25.858 | 26.786 | 1252.956 | 27.059 | 27.299 | 36.362 | 25.001 | 2 | 0.9 | 0.9 | 0.3 | 0.2
1697 | 30/07/2025 10:04:35.959 | 98.256 | 78 | 100 | 69 | 54 | 27.437 | 9.421 | 7.032 | 134.663 | 29.259 | 28.235 | 27.857 | 601.981 | 25.851 | 26.792 | 1257.425 | 27.041 | 27.314 | 36.762 | 24.001 | 4 | 2.4 | 0.2 | 0 | 0.2
1698 | 30/07/2025 10:04:37.594 | 99.144 | 77 | 99 | 70 | 52 | 27.867 | 9.425 | 7.033 | 134.732 | 29.27 | 28.242 | 27.842 | 600.519 | 25.869 | 26.773 | 1267.404 | 27.054 | 27.305 | 36.588 | 26.001 | 4 | 2.9 | 0.2 | 0 | 0.2
1699 | 30/07/2025 10:04:39.229 | 99.504 | 77 | 100 | 70 | 52 | 30.619 | 9.505 | 7.032 | 134.48 | 29.256 | 28.237 | 27.853 | 600.596 | 25.852 | 26.774 | 1274.56 | 27.081 | 27.325 | 36.819 | 24.001 | 2.5 | 2.3 | 1 | 0.5 | 0.2
1700 | 30/07/2025 10:04:40.861 | 98.616 | 76 | 100 | 71 | 52 | 26.941 | 9.286 | 7.033 | 134.711 | 29.265 | 28.236 | 27.888 | 600.879 | 25.859 | 26.774 | 1280.978 | 27.058 | 27.302 | 36.423 | 26.001 | 2.5 | 3 | 1 | 0.5 | 0.2
1701 | 30/07/2025 10:04:42.499 | 99.168 | 77 | 100 | 71 | 51 | 30.317 | 9.223 | 7.033 | 134.208 | 29.254 | 28.259 | 27.858 | 600.737 | 25.858 | 26.763 | 1291.672 | 27.078 | 27.313 | 36.516 | 27.001 | 2.5 | 2.1 | 1.2 | 0.5 | 0.1
1702 | 30/07/2025 10:04:44.132 | 98.808 | 76 | 100 | 70 | 52 | 30.566 | 9.5 | 7.033 | 134.923 | 29.259 | 28.245 | 27.857 | 600.698 | 25.881 | 26.773 | 1297.384 | 27.036 | 27.317 | 36.823 | 27.001 | 2.5 | 2.1 | 1.2 | 0.5 | 0.1
1703 | 30/07/2025 10:04:45.769 | 98.808 | 77 | 100 | 71 | 52 | 26.936 | 9.287 | 7.033 | 134.752 | 29.261 | 28.243 | 27.852 | 600.538 | 25.862 | 26.767 | 1299.87 | 27.07 | 27.308 | 36.542 | 26.001 | 2.5 | 1.6 | 1.2 | 0.5 | 0.1
1704 | 30/07/2025 10:04:47.405 | 98.616 | 77 | 100 | 70 | 52 | 28.56 | 9.287 | 7.035 | 134.658 | 29.256 | 28.219 | 27.866 | 600.697 | 25.878 | 26.782 | 1287.271 | 27.079 | 27.294 | 36.585 | 25.001 | 4.8 | 1.8 | 0.6 | 1.1 | 0.1
1705 | 30/07/2025 10:04:49.041 | 98.856 | 76 | 100 | 71 | 52 | 30.636 | 9.475 | 7.032 | 134.592 | 29.27 | 28.243 | 27.865 | 600.665 | 25.888 | 26.779 | 1286.582 | 27.052 | 27.293 | 36.349 | 26.001 | 4.8 | 2.1 | 0.6 | 1.1 | 0.1
1706 | 30/07/2025 10:04:50.675 | 98.952 | 76 | 99 | 70 | 52 | 27.494 | 9.434 | 7.036 | 134.48 | 29.259 | 28.249 | 27.853 | 600.65 | 25.875 | 26.801 | 1287.235 | 27.045 | 27.296 | 36.758 | 28.001 | 3 | 2 | 0.7 | 0.2 | 0.1
1707 | 30/07/2025 10:04:52.310 | 98.376 | 77 | 100 | 70 | 53 | 30.531 | 9.288 | 7.031 | 134.812 | 29.25 | 28.246 | 27.873 | 600.645 | 25.873 | 26.801 | 1292.511 | 27.041 | 27.312 | 36.685 | 28.001 | 3 | 2 | 0.7 | 0.2 | 0.1
1708 | 30/07/2025 10:04:53.947 | 98.472 | 76 | 100 | 70 | 54 | 30.296 | 9.493 | 7.033 | 134.564 | 29.238 | 28.249 | 27.835 | 600.597 | 25.881 | 26.791 | 1291.816 | 27.093 | 27.313 | 36.541 | 25.001 | 3 | 2.7 | 0.7 | 0.2 | 0.1
1709 | 30/07/2025 10:04:55.581 | 98.52 | 77 | 100 | 69 | 52 | 26.672 | 9.581 | 7.033 | 134.719 | 29.247 | 28.229 | 27.86 | 600.793 | 25.887 | 26.803 | 1296.224 | 27.069 | 27.283 | 36.481 | 22.001 | 1.7 | 2.6 | 0.6 | 0.5 | 0.2
1710 | 30/07/2025 10:04:57.216 | 98.184 | 76 | 100 | 70 | 52 | 29.187 | 9.311 | 7.032 | 134.506 | 29.233 | 28.248 | 27.874 | 600.746 | 25.855 | 26.793 | 1297.499 | 27.055 | 27.293 | 36.558 | 24.001 | 1.7 | 1.2 | 0.6 | 0.5 | 0.2
1711 | 30/07/2025 10:04:58.852 | 98.184 | 77 | 100 | 71 | 52 | 27.484 | 9.395 | 7.031 | 134.666 | 29.25 | 28.249 | 27.872 | 600.626 | 25.883 | 26.799 | 1297.896 | 27.039 | 27.308 | 36.964 | 23.001 | 3.1 | 1.8 | 0.6 | 0.8 | 0.2
1712 | 30/07/2025 10:05:00.488 | 98.232 | 75 | 100 | 70 | 51 | 28.024 | 9.29 | 7.034 | 134.83 | 29.251 | 28.248 | 27.856 | 600.799 | 25.867 | 26.79 | 1310.557 | 27.056 | 27.316 | 36.526 | 26.001 | 3.1 | 1.1 | 0.6 | 0.8 | 0.2
1713 | 30/07/2025 10:05:02.124 | 97.8 | 77 | 100 | 71 | 52 | 30.564 | 9.434 | 7.035 | 134.705 | 29.243 | 28.231 | 27.839 | 600.648 | 25.876 | 26.807 | 1319.901 | 27.077 | 27.301 | 36.581 | 26.001 | 3.1 | 1.1 | 0.6 | 0.8 | 0.2
1714 | 30/07/2025 10:05:03.758 | 97.896 | 76 | 100 | 72 | 52 | 29.875 | 9.431 | 7.03 | 134.679 | 29.263 | 28.227 | 27.887 | 600.821 | 25.879 | 26.79 | 1315.238 | 27.067 | 27.288 | 36.317 | 23.001 | 1.1 | 2.3 | 0.6 | 0.8 | 0.2
1715 | 30/07/2025 10:05:05.402 | 97.824 | 76 | 100 | 70 | 52 | 26.584 | 9.284 | 7.034 | 134.42 | 29.266 | 28.26 | 27.86 | 600.763 | 25.863 | 26.789 | 1307.083 | 27.067 | 27.311 | 36.609 | 26.001 | 1.1 | 1.3 | 0.6 | 0.8 | 0.2
1716 | 30/07/2025 10:05:07.041 | 97.2 | 76 | 100 | 70 | 53 | 30.597 | 9.499 | 7.034 | 134.875 | 29.272 | 28.246 | 27.883 | 600.742 | 25.861 | 26.783 | 1307.124 | 27.032 | 27.303 | 36.699 | 25.001 | 2 | 1.1 | 1 | 0.2 | 0.2
1717 | 30/07/2025 10:05:08.674 | 96.672 | 75 | 100 | 71 | 52 | 26.981 | 9.385 | 7.033 | 134.737 | 29.27 | 28.247 | 27.839 | 600.575 | 25.866 | 26.796 | 1305.873 | 27.086 | 27.316 | 36.771 | 25.001 | 2 | 1.1 | 1 | 0.2 | 0.2
1718 | 30/07/2025 10:05:10.398 | 95.04 | 74 | 100 | 70 | 51 | 28.581 | 9.266 | 7.033 | 134.874 | 29.27 | 28.223 | 27.858 | 600.714 | 25.875 | 26.786 | 1319.825 | 27.065 | 27.294 | 36.59 | 25.001 | 2.9 | 2.4 | 0.6 | 0.1 | 0.2
1719 | 30/07/2025 10:05:12.040 | 95.376 | 74 | 100 | 70 | 52 | 30.678 | 9.5 | 7.033 | 134.41 | 29.262 | 28.251 | 27.87 | 600.694 | 25.851 | 26.785 | 1321.687 | 27.061 | 27.289 | 36.412 | 25.001 | 2.9 | 2.4 | 0.6 | 0.1 | 0.2
1720 | 30/07/2025 10:05:13.676 | 95.76 | 74 | 100 | 71 | 51 | 29.259 | 9.433 | 7.035 | 134.64 | 29.262 | 28.246 | 27.853 | 600.64 | 25.844 | 26.771 | 1325.972 | 27.047 | 27.303 | 36.719 | 26.001 | 2.9 | 2.5 | 0.6 | 0.1 | 0.2
1721 | 30/07/2025 10:05:15.310 | 95.544 | 74 | 100 | 70 | 53 | 26.677 | 9.426 | 7.032 | 134.786 | 29.272 | 28.252 | 27.861 | 600.66 | 25.865 | 26.761 | 1310.212 | 27.057 | 27.305 | 36.556 | 24.001 | 3.3 | 1.9 | 0.9 | 0.6 | 0.2
1722 | 30/07/2025 10:05:16.949 | 95.856 | 75 | 100 | 71 | 52 | 30.29 | 9.356 | 7.035 | 134.767 | 29.265 | 28.237 | 27.824 | 600.683 | 25.871 | 26.781 | 1312.095 | 27.069 | 27.299 | 36.714 | 27.001 | 3.3 | 2.5 | 0.9 | 0.6 | 0.2
1723 | 30/07/2025 10:05:18.584 | 96.48 | 77 | 100 | 70 | 52 | 26.75 | 9.285 | 7.032 | 134.816 | 29.264 | 28.223 | 27.877 | 600.824 | 25.856 | 26.776 | 1297.247 | 27.065 | 27.292 | 36.465 | 25.001 | 2.1 | 1.4 | 0.7 | 0.1 | 0.2
1724 | 30/07/2025 10:05:20.221 | 96.048 | 74 | 100 | 71 | 52 | 29.067 | 9.494 | 7.033 | 134.516 | 29.263 | 28.26 | 27.868 | 600.782 | 25.873 | 26.778 | 1306.112 | 27.079 | 27.304 | 36.525 | 25.001 | 2.1 | 1.4 | 0.7 | 0.1 | 0.2
1725 | 30/07/2025 10:05:21.855 | 95.616 | 75 | 100 | 71 | 52 | 30.726 | 9.294 | 7.008 | 134.871 | 29.266 | 28.239 | 27.853 | 600.63 | 25.884 | 26.788 | 1302.408 | 27.016 | 27.314 | 36.812 | 23.001 | 2.1 | 0.6 | 0.7 | 0.1 | 0.2
1726 | 30/07/2025 10:05:23.492 | 95.76 | 76 | 100 | 69 | 52 | 28.623 | 9.575 | 7.005 | 134.906 | 29.244 | 28.247 | 27.844 | 600.674 | 25.878 | 26.786 | 1306.881 | 27.071 | 27.299 | 36.702 | 25.001 | 2 | 1.3 | 0.6 | 0 | 0.1
1727 | 30/07/2025 10:05:25.134 | 95.808 | 75 | 100 | 70 | 52 | 27.036 | 9.579 | 7.033 | 134.648 | 29.243 | 28.226 | 27.848 | 600.604 | 25.871 | 26.801 | 1306.896 | 27.077 | 27.297 | 36.635 | 25.001 | 2 | 1 | 0.6 | 0 | 0.1
1728 | 30/07/2025 10:05:26.771 | 96.288 | 76 | 100 | 71 | 52 | 29.819 | 9.301 | 7.03 | 134.572 | 29.242 | 28.237 | 27.872 | 600.778 | 25.879 | 26.79 | 1316.091 | 27.071 | 27.301 | 36.432 | 24.001 | 1.8 | 1.5 | 0.7 | 0.5 | 0.2
1729 | 30/07/2025 10:05:28.406 | 96.456 | 74 | 100 | 71 | 52 | 26.552 | 9.431 | 6.902 | 134.277 | 29.249 | 28.252 | 27.856 | 600.721 | 25.87 | 26.793 | 1322.264 | 27.051 | 27.301 | 36.711 | 24.001 | 1.8 | 2.3 | 0.7 | 0.5 | 0.2
1730 | 30/07/2025 10:05:30.040 | 96.384 | 77 | 100 | 70 | 52 | 29.664 | 9.504 | 6.9 | 134.846 | 29.239 | 28.242 | 27.881 | 600.675 | 25.883 | 26.801 | 1319.923 | 27.032 | 27.314 | 36.655 | 24.001 | 1.8 | 2.3 | 0.7 | 0.5 | 0.2
1731 | 30/07/2025 10:05:31.677 | 96.744 | 77 | 100 | 70 | 52 | 30.803 | 9.432 | 6.901 | 134.635 | 29.238 | 28.237 | 27.827 | 600.591 | 25.871 | 26.8 | 1315.529 | 27.091 | 27.298 | 36.98 | 23.001 | 2.3 | 2.2 | 0.6 | 0.6 | 0.2
1732 | 30/07/2025 10:05:33.314 | 96.768 | 78 | 100 | 69 | 54 | 28.058 | 9.398 | 6.934 | 134.83 | 29.248 | 28.225 | 27.862 | 600.772 | 25.876 | 26.796 | 1317.31 | 27.063 | 27.293 | 36.734 | 24.001 | 2.3 | 2 | 0.6 | 0.6 | 0.2
1733 | 30/07/2025 10:05:34.949 | 97.104 | 76 | 100 | 71 | 52 | 30.673 | 9.564 | 6.935 | 134.57 | 29.243 | 28.234 | 27.875 | 600.64 | 25.863 | 26.796 | 1314.744 | 27.072 | 27.288 | 36.512 | 31.001 | 2.3 | 2.3 | 1 | 0.5 | 0.2
1734 | 30/07/2025 10:05:36.585 | 97.776 | 77 | 100 | 70 | 52 | 29.338 | 9.633 | 7.003 | 134.591 | 29.267 | 28.252 | 27.861 | 600.683 | 25.879 | 26.79 | 1308.141 | 27.043 | 27.302 | 36.903 | 31.001 | 2.3 | 2.1 | 1 | 0.5 | 0.2
1735 | 30/07/2025 10:05:38.220 | 97.848 | 77 | 100 | 70 | 52 | 26.759 | 9.441 | 6.904 | 134.736 | 29.25 | 28.246 | 27.858 | 600.7 | 25.869 | 26.797 | 1308.353 | 27.058 | 27.318 | 36.602 | 31.001 | 2.3 | 2.1 | 1 | 0.5 | 0.2
1736 | 30/07/2025 10:05:39.855 | 97.68 | 77 | 100 | 70 | 52 | 30.087 | 9.573 | 6.85 | 134.648 | 29.261 | 28.237 | 27.84 | 600.663 | 25.86 | 26.785 | 1314.979 | 27.068 | 27.304 | 36.654 | 29.001 | 1.3 | 1.1 | 0.6 | 1.2 | 0.2
1737 | 30/07/2025 10:05:41.489 | 98.304 | 79 | 100 | 70 | 52 | 30.826 | 9.287 | 6.932 | 133.148 | 29.276 | 28.23 | 28.029 | 600.928 | 25.869 | 26.772 | 1317.383 | 27.066 | 27.272 | 36.581 | 24.001 | 1.3 | 1.7 | 0.6 | 1.2 | 0.2
1738 | 30/07/2025 10:05:43.125 | 98.352 | 78 | 100 | 70 | 51 | 27.53 | 9.281 | 6.936 | 133.048 | 29.278 | 28.256 | 27.879 | 600.712 | 25.855 | 26.781 | 1317.511 | 27.071 | 27.316 | 36.722 | 24.001 | 2.9 | 1 | 0.9 | 0.3 | 0.2
1739 | 30/07/2025 10:05:44.762 | 98.376 | 77 | 100 | 71 | 52 | 30.786 | 9.286 | 6.936 | 133.115 | 29.278 | 28.251 | 27.885 | 600.819 | 25.847 | 26.783 | 1317.747 | 27.032 | 27.308 | 36.704 | 21.001 | 2.9 | 1.7 | 0.9 | 0.3 | 0.2
1740 | 30/07/2025 10:05:46.399 | 98.256 | 78 | 100 | 70 | 52 | 28.736 | 9.43 | 6.959 | 133.176 | 29.259 | 28.242 | 27.988 | 600.598 | 25.856 | 26.797 | 1311.621 | 27.083 | 27.31 | 36.581 | 23.001 | 3.5 | 2 | 1.6 | 0 | 0.2
1741 | 30/07/2025 10:05:48.033 | 98.376 | 78 | 99 | 70 | 52 | 26.973 | 9.499 | 7.003 | 133.253 | 29.281 | 28.231 | 28.009 | 600.779 | 25.872 | 26.775 | 1300.349 | 27.061 | 27.298 | 36.656 | 23.001 | 3.5 | 2 | 1.6 | 0 | 0.2
1742 | 30/07/2025 10:05:49.669 | 98.544 | 77 | 100 | 70 | 52 | 30.42 | 9.438 | 7.004 | 134.45 | 29.259 | 28.223 | 28.008 | 600.703 | 25.849 | 26.767 | 1299.543 | 27.057 | 27.286 | 36.463 | 28.001 | 3.5 | 1.4 | 1.6 | 0 | 0.2
1743 | 30/07/2025 10:05:51.313 | 97.728 | 77 | 99 | 70 | 52 | 30.661 | 9.428 | 7.007 | 134.497 | 29.254 | 28.249 | 27.867 | 600.648 | 25.869 | 26.776 | 1294.933 | 27.044 | 27.294 | 36.807 | 31.001 | 2.5 | 3 | 0.7 | 0.5 | 0.2
1744 | 30/07/2025 10:05:52.950 | 97.824 | 77 | 100 | 71 | 52 | 27.1 | 9.431 | 7.034 | 134.784 | 29.257 | 28.246 | 28.001 | 601.639 | 25.872 | 26.763 | 1291.912 | 27.052 | 27.303 | 36.613 | 28.001 | 2.5 | 2.7 | 0.7 | 0.5 | 0.2
1745 | 30/07/2025 10:05:54.586 | 98.064 | 77 | 100 | 70 | 52 | 30.878 | 9.433 | 7.048 | 134.711 | 29.258 | 28.244 | 27.968 | 602.067 | 25.874 | 26.765 | 1297.087 | 27.066 | 27.302 | 36.579 | 28.001 | 2.1 | 2.1 | 0.1 | 0 | 0.1
1746 | 30/07/2025 10:05:56.221 | 97.704 | 77 | 100 | 70 | 51 | 28.113 | 9.44 | 7.07 | 134.73 | 29.267 | 28.225 | 28.022 | 602.313 | 25.857 | 26.786 | 1305.661 | 27.06 | 27.304 | 36.414 | 28.001 | 2.1 | 2.1 | 0.1 | 0 | 0.1
1747 | 30/07/2025 10:05:57.857 | 97.104 | 76 | 100 | 70 | 52 | 27.46 | 9.444 | 7.005 | 134.321 | 29.265 | 28.25 | 27.851 | 602.011 | 25.872 | 26.795 | 1316.948 | 27.076 | 27.289 | 36.41 | 28.001 | 2.1 | 1.3 | 0.1 | 0 | 0.1
1748 | 30/07/2025 10:05:59.494 | 97.632 | 76 | 100 | 71 | 52 | 30.513 | 9.498 | 7.003 | 134.883 | 29.267 | 28.251 | 28.014 | 602.094 | 25.879 | 26.805 | 1317.445 | 27.026 | 27.316 | 36.791 | 25.001 | 2.1 | 0.8 | 0.6 | 0.5 | 0.1
1749 | 30/07/2025 10:06:01.129 | 97.416 | 78 | 100 | 71 | 52 | 30.275 | 9.495 | 7.005 | 134.648 | 29.23 | 28.249 | 27.994 | 602.034 | 25.863 | 26.797 | 1313.764 | 27.079 | 27.319 | 36.652 | 27.001 | 2.1 | 0.4 | 0.6 | 0.5 | 0.1
1750 | 30/07/2025 10:06:02.778 | 97.152 | 77 | 100 | 70 | 52 | 30.016 | 9.492 | 7.004 | 134.799 | 29.251 | 28.241 | 27.999 | 602.178 | 25.882 | 26.79 | 1308.575 | 27.068 | 27.302 | 36.791 | 25.001 | 1.6 | 1.7 | 1.5 | 0.5 | 0.2
1751 | 30/07/2025 10:06:04.414 | 97.224 | 76 | 100 | 70 | 53 | 30.806 | 9.455 | 7.003 | 134.549 | 29.245 | 28.228 | 28.027 | 602.19 | 25.872 | 26.796 | 1316.6 | 27.072 | 27.31 | 36.456 | 28.001 | 1.6 | 0.8 | 1.5 | 0.5 | 0.2
1752 | 30/07/2025 10:06:06.050 | 97.008 | 76 | 100 | 71 | 51 | 27.405 | 9.578 | 7.006 | 134.447 | 29.244 | 28.249 | 28.015 | 602.119 | 25.874 | 26.795 | 1318.471 | 27.05 | 27.289 | 36.791 | 28.001 | 1.6 | 0.8 | 1.5 | 0.5 | 0.2
1753 | 30/07/2025 10:06:07.685 | 97.008 | 77 | 100 | 70 | 52 | 27.929 | 9.498 | 7.005 | 134.814 | 29.244 | 28.251 | 28.013 | 602.118 | 25.872 | 26.789 | 1310.477 | 27.032 | 27.313 | 36.643 | 26.001 | 3.7 | 1.1 | 0 | 0 | 0.2
1754 | 30/07/2025 10:06:09.319 | 97.176 | 76 | 100 | 70 | 52 | 30.593 | 9.296 | 7.005 | 134.506 | 29.249 | 28.251 | 27.978 | 601.97 | 25.873 | 26.796 | 1305.854 | 27.093 | 27.302 | 36.754 | 28.001 | 3.7 | 1.4 | 0 | 0 | 0.2
1755 | 30/07/2025 10:06:10.955 | 96.816 | 76 | 100 | 70 | 53 | 29.918 | 9.268 | 7.004 | 134.845 | 29.267 | 28.229 | 28.01 | 602.172 | 25.887 | 26.791 | 1297.06 | 27.066 | 27.29 | 36.552 | 33.001 | 1.8 | 0.8 | 0.6 | 0.1 | 0.2
1756 | 30/07/2025 10:06:12.589 | 96.768 | 76 | 100 | 70 | 53 | 30.381 | 9.293 | 7.003 | 134.505 | 29.266 | 28.233 | 28.01 | 602.193 | 25.875 | 26.808 | 1292.781 | 27.072 | 27.286 | 36.472 | 29.001 | 1.8 | 1 | 0.6 | 0.1 | 0.2
1757 | 30/07/2025 10:06:14.225 | 96.984 | 76 | 100 | 70 | 52 | 30.677 | 9.524 | 7.005 | 134.462 | 29.28 | 28.249 | 28.001 | 602.259 | 25.879 | 26.796 | 1292.241 | 27.043 | 27.304 | 38.528 | 29.001 | 1.8 | 1 | 0.6 | 0.1 | 0.2
1758 | 30/07/2025 10:06:15.861 | 96.72 | 75 | 100 | 71 | 52 | 27.043 | 9.577 | 6.982 | 134.812 | 29.265 | 28.25 | 27.993 | 602.172 | 25.857 | 26.783 | 1283.481 | 27.043 | 27.315 | 36.718 | 28.001 | 2.3 | 1.5 | 0.8 | 0.5 | 0.2
1759 | 30/07/2025 10:06:17.496 | 96.6 | 75 | 100 | 70 | 53 | 28.613 | 9.29 | 6.936 | 134.657 | 29.263 | 28.237 | 27.988 | 601.943 | 25.85 | 26.787 | 1280.383 | 27.064 | 27.3 | 36.812 | 25.001 | 2.3 | 4.2 | 0.8 | 0.5 | 0.2
1760 | 30/07/2025 10:06:19.130 | 96.408 | 76 | 100 | 71 | 52 | 30.723 | 9.412 | 6.985 | 134.575 | 29.271 | 28.235 | 28.024 | 602.306 | 25.854 | 26.784 | 1283.106 | 27.06 | 27.285 | 36.548 | 23.001 | 1.2 | 1.3 | 0.1 | 1.1 | 0.2
1761 | 30/07/2025 10:06:20.767 | 96.264 | 76 | 100 | 70 | 51 | 27.515 | 9.433 | 7.004 | 134.689 | 29.27 | 28.24 | 28.009 | 602.076 | 25.864 | 26.782 | 1292.063 | 27.06 | 27.283 | 36.561 | 23.001 | 1.2 | 2 | 0.1 | 1.1 | 0.2
1762 | 30/07/2025 10:06:22.403 | 95.712 | 76 | 100 | 70 | 51 | 30.61 | 9.416 | 7.031 | 134.664 | 29.267 | 28.262 | 28.007 | 602.221 | 25.855 | 26.779 | 1295.012 | 27.041 | 27.322 | 38.549 | 23.001 | 3.4 | 2.1 | 0 | 0.1 | 0.2
1763 | 30/07/2025 10:06:24.041 | 96.096 | 75 | 100 | 71 | 52 | 30.439 | 9.429 | 7.035 | 134.624 | 29.27 | 28.244 | 27.977 | 601.982 | 25.847 | 26.774 | 1302.803 | 27.07 | 27.302 | 38.534 | 23.001 | 3.4 | 2.1 | 0 | 0.1 | 0.2
1764 | 30/07/2025 10:06:25.678 | 96.672 | 77 | 100 | 70 | 52 | 26.812 | 9.397 | 7.032 | 134.71 | 29.272 | 28.232 | 28.005 | 602.248 | 25.883 | 26.76 | 1314.692 | 27.065 | 27.308 | 37.062 | 28.001 | 3.4 | 1.7 | 0 | 0.1 | 0.2
1765 | 30/07/2025 10:06:27.312 | 96.84 | 76 | 100 | 69 | 52 | 29.176 | 9.432 | 7.032 | 134.495 | 29.263 | 28.237 | 28.016 | 602.184 | 25.864 | 26.759 | 1319.679 | 27.068 | 27.303 | 36.53 | 32.001 | 2.3 | 0.8 | 0.3 | 0.8 | 0.2
1766 | 30/07/2025 10:06:28.947 | 97.416 | 76 | 100 | 70 | 52 | 30.813 | 9.43 | 7.034 | 134.538 | 29.257 | 28.246 | 27.996 | 602.029 | 25.874 | 26.779 | 1312.378 | 27.051 | 27.297 | 36.925 | 28.001 | 2.3 | 1.4 | 0.3 | 0.8 | 0.2
1767 | 30/07/2025 10:06:30.581 | 96.384 | 76 | 100 | 70 | 52 | 28.024 | 9.449 | 7.034 | 134.647 | 29.253 | 28.268 | 28 | 602.147 | 25.873 | 26.786 | 1313.205 | 27.053 | 27.303 | 36.758 | 25.001 | 1.1 | 1.9 | 0.1 | 0.6 | 0.2
1768 | 30/07/2025 10:06:32.217 | 97.416 | 76 | 100 | 70 | 52 | 30.648 | 9.284 | 7.034 | 134.72 | 29.257 | 28.247 | 27.974 | 602.026 | 25.889 | 26.804 | 1313.212 | 27.059 | 27.31 | 36.644 | 25.001 | 1.1 | 1.9 | 0.1 | 0.6 | 0.2
1769 | 30/07/2025 10:06:33.854 | 97.728 | 79 | 100 | 70 | 52 | 29.892 | 9.297 | 7.032 | 134.778 | 29.245 | 28.231 | 28.016 | 602.213 | 25.875 | 26.801 | 1317.234 | 27.066 | 27.305 | 36.908 | 25.001 | 1.1 | 1.6 | 0.1 | 0.6 | 0.2
1770 | 30/07/2025 10:06:35.489 | 97.824 | 76 | 100 | 69 | 52 | 26.66 | 9.451 | 7.033 | 134.235 | 29.245 | 28.244 | 27.999 | 600.604 | 25.874 | 26.799 | 1322.304 | 27.075 | 27.283 | 38.307 | 29.001 | 2.7 | 2.3 | 0.9 | 0.5 | 0.2
1771 | 30/07/2025 10:06:37.126 | 98.16 | 76 | 100 | 70 | 53 | 29.635 | 9.291 | 7.032 | 134.678 | 29.252 | 28.253 | 28.007 | 600.726 | 25.896 | 26.791 | 1309.762 | 27.034 | 27.3 | 38.568 | 34.001 | 2.7 | 1.1 | 0.9 | 0.5 | 0.2
1772 | 30/07/2025 10:06:38.762 | 97.944 | 78 | 100 | 70 | 52 | 27.071 | 9.428 | 7.036 | 134.568 | 29.237 | 28.247 | 27.99 | 600.612 | 25.873 | 26.813 | 1314.676 | 27.042 | 27.306 | 37.744 | 26.001 | 3.8 | 1.9 | 1.2 | 0.5 | 0.2
1773 | 30/07/2025 10:06:40.398 | 97.32 | 78 | 99 | 70 | 52 | 28.477 | 9.558 | 7.033 | 134.757 | 29.237 | 28.237 | 27.992 | 600.674 | 25.865 | 26.786 | 1302.254 | 27.071 | 27.301 | 36.537 | 27.001 | 3.8 | 1.5 | 1.2 | 0.5 | 0.2
1774 | 30/07/2025 10:06:42.032 | 97.008 | 76 | 100 | 70 | 52 | 30.749 | 9.534 | 7.032 | 134.605 | 29.233 | 28.239 | 28.019 | 600.764 | 25.861 | 26.796 | 1291.082 | 27.077 | 27.305 | 36.523 | 27.001 | 3.8 | 1.5 | 1.2 | 0.5 | 0.2
1775 | 30/07/2025 10:06:43.667 | 96.792 | 76 | 100 | 70 | 52 | 29.319 | 9.428 | 7.034 | 134.61 | 29.257 | 28.245 | 28.001 | 600.725 | 25.878 | 26.796 | 1288.77 | 27.054 | 27.289 | 36.566 | 27.001 | 1.7 | 1.7 | 0.9 | 0.9 | 0.2
1776 | 30/07/2025 10:06:45.306 | 96.672 | 77 | 100 | 70 | 52 | 26.759 | 9.411 | 7.034 | 134.627 | 29.262 | 28.252 | 28 | 600.665 | 25.877 | 26.786 | 1289.005 | 27.028 | 27.316 | 36.638 | 26.001 | 1.7 | 0.8 | 0.9 | 0.9 | 0.2
1777 | 30/07/2025 10:06:46.943 | 96.456 | 74 | 100 | 71 | 52 | 30.084 | 9.372 | 7.035 | 134.621 | 29.262 | 28.242 | 27.964 | 600.519 | 25.872 | 26.798 | 1299.107 | 27.089 | 27.296 | 36.587 | 25.001 | 4.4 | 1 | 0.7 | 0 | 0.2
1778 | 30/07/2025 10:06:48.577 | 96.504 | 76 | 100 | 70 | 52 | 26.74 | 9.289 | 7.032 | 134.619 | 29.262 | 28.238 | 27.983 | 601.909 | 25.86 | 26.79 | 1306.888 | 27.068 | 27.31 | 36.574 | 29.001 | 4.4 | 1.1 | 0.7 | 0 | 0.2
1779 | 30/07/2025 10:06:50.215 | 96.888 | 77 | 100 | 70 | 52 | 29.101 | 9.464 | 7.032 | 134.554 | 29.268 | 28.238 | 27.997 | 602.09 | 25.856 | 26.792 | 1321.87 | 27.066 | 27.289 | 36.58 | 29.001 | 4.4 | 1.1 | 0.7 | 0 | 0.2
1780 | 30/07/2025 10:06:51.853 | 96.792 | 78 | 100 | 70 | 52 | 30.786 | 9.432 | 7.033 | 134.634 | 29.267 | 28.256 | 28.018 | 602.108 | 25.865 | 26.783 | 1329.764 | 27.053 | 27.304 | 36.612 | 29.001 | 3.3 | 0.8 | 0.6 | 0.8 | 0.2
1781 | 30/07/2025 10:06:53.490 | 96.312 | 76 | 100 | 72 | 52 | 28.751 | 9.5 | 7.033 | 134.655 | 29.256 | 28.259 | 27.992 | 602.062 | 25.861 | 26.785 | 1329.476 | 27.051 | 27.316 | 36.698 | 30.001 | 3.3 | 1.4 | 0.6 | 0.8 | 0.2
1782 | 30/07/2025 10:06:55.125 | 97.176 | 76 | 100 | 70 | 52 | 27.022 | 9.434 | 7.033 | 134.636 | 29.27 | 28.238 | 27.986 | 603.149 | 25.843 | 26.768 | 1327.403 | 27.076 | 27.298 | 36.855 | 31.001 | 3.9 | 1 | 1 | 0.8 | 0.1
1783 | 30/07/2025 10:06:56.762 | 97.32 | 77 | 100 | 70 | 52 | 29.975 | 9.431 | 7.032 | 134.607 | 29.26 | 28.219 | 27.99 | 603.447 | 25.844 | 26.777 | 1320.458 | 27.087 | 27.307 | 36.538 | 25.001 | 3.9 | 1.3 | 1 | 0.8 | 0.1
1784 | 30/07/2025 10:06:58.396 | 96.672 | 76 | 100 | 70 | 52 | 26.712 | 9.543 | 7.031 | 134.524 | 29.257 | 28.238 | 28.02 | 603.354 | 25.879 | 26.779 | 1325.699 | 27.052 | 27.285 | 36.483 | 31.001 | 2.7 | 1.2 | 0.9 | 0 | 0.1
1785 | 30/07/2025 10:07:00.034 | 96.624 | 76 | 100 | 71 | 53 | 29.782 | 9.576 | 7.06 | 134.591 | 29.264 | 28.265 | 28.023 | 603.408 | 25.859 | 26.769 | 1317.67 | 27.047 | 27.326 | 36.874 | 31.001 | 2.7 | 1.2 | 0.9 | 0 | 0.1
1786 | 30/07/2025 10:07:01.678 | 96.576 | 76 | 100 | 70 | 52 | 30.873 | 9.511 | 7.072 | 134.915 | 29.257 | 28.251 | 27.975 | 603.278 | 25.865 | 26.782 | 1327.423 | 27.062 | 27.304 | 36.8 | 27.001 | 2.7 | 1.8 | 0.9 | 0 | 0.1
1787 | 30/07/2025 10:07:03.326 | 96.432 | 76 | 99 | 70 | 52 | 28.226 | 9.415 | 7.006 | 134.566 | 29.272 | 28.233 | 28.009 | 604.621 | 25.878 | 26.785 | 1330.292 | 27.067 | 27.312 | 36.662 | 29.001 | 2.6 | 0.8 | 1.5 | 0 | 0.2
1788 | 30/07/2025 10:07:04.962 | 96.672 | 75 | 100 | 71 | 52 | 27.528 | 9.287 | 7.004 | 134.507 | 29.25 | 28.252 | 28.011 | 604.574 | 25.881 | 26.789 | 1317.392 | 27.081 | 27.292 | 36.479 | 21.001 | 2.6 | 2.2 | 1.5 | 0 | 0.2
1789 | 30/07/2025 10:07:06.606 | 96.816 | 74 | 100 | 70 | 53 | 29.344 | 9.289 | 7.004 | 134.428 | 29.267 | 28.254 | 28.019 | 604.722 | 25.864 | 26.78 | 1312.627 | 27.062 | 27.283 | 36.434 | 29.001 | 2.1 | 2.1 | 0.6 | 0.8 | 0.2
1790 | 30/07/2025 10:07:08.241 | 96.912 | 77 | 100 | 71 | 52 | 26.797 | 9.284 | 7.005 | 134.53 | 29.252 | 28.253 | 28.007 | 604.535 | 25.859 | 26.805 | 1310.099 | 27.049 | 27.32 | 36.668 | 29.001 | 2.1 | 2.1 | 0.6 | 0.8 | 0.2
1791 | 30/07/2025 10:07:09.879 | 97.152 | 77 | 100 | 71 | 53 | 30.109 | 9.501 | 7.005 | 134.69 | 29.249 | 28.239 | 27.972 | 604.506 | 25.889 | 26.802 | 1312.686 | 27.059 | 27.296 | 36.611 | 32.001 | 2.1 | 2.4 | 0.6 | 0.8 | 0.2
1792 | 30/07/2025 10:07:11.516 | 96.528 | 76 | 100 | 70 | 52 | 30.837 | 9.288 | 7.031 | 134.79 | 29.236 | 28.228 | 28.009 | 604.634 | 25.875 | 26.8 | 1317.234 | 27.071 | 27.302 | 36.493 | 28.001 | 3.8 | 1.8 | 0.3 | 0.8 | 0.2
1793 | 30/07/2025 10:07:13.152 | 96.192 | 75 | 100 | 70 | 53 | 27.624 | 9.507 | 7.033 | 134.43 | 29.227 | 28.244 | 27.991 | 604.489 | 25.877 | 26.801 | 1330.96 | 27.061 | 27.286 | 36.308 | 24.001 | 3.8 | 1.2 | 0.3 | 0.8 | 0.2
1794 | 30/07/2025 10:07:14.788 | 96.144 | 75 | 100 | 70 | 52 | 30.801 | 9.463 | 7.033 | 134.594 | 29.23 | 28.271 | 27.998 | 604.61 | 25.867 | 26.798 | 1334.459 | 27.059 | 27.31 | 36.501 | 28.001 | 3.4 | 1.1 | 0.7 | 1.6 | 0.2
1795 | 30/07/2025 10:07:16.423 | 96.384 | 76 | 100 | 70 | 52 | 28.855 | 9.288 | 7.008 | 134.562 | 29.247 | 28.242 | 27.983 | 605.741 | 25.863 | 26.793 | 1325.222 | 27.039 | 27.303 | 36.884 | 26.001 | 3.4 | 1.2 | 0.7 | 1.6 | 0.2
1796 | 30/07/2025 10:07:18.057 | 96.672 | 75 | 100 | 71 | 52 | 27.038 | 9.576 | 7.005 | 134.696 | 29.251 | 28.249 | 27.975 | 606.959 | 25.872 | 26.79 | 1324.592 | 27.076 | 27.3 | 36.655 | 26.001 | 3.4 | 1.2 | 0.7 | 1.6 | 0.2
1797 | 30/07/2025 10:07:19.695 | 96.696 | 74 | 100 | 71 | 52 | 30.372 | 9.583 | 7.003 | 134.591 | 29.255 | 28.228 | 28.009 | 607.098 | 25.862 | 26.801 | 1319.074 | 27.093 | 27.302 | 36.453 | 27.001 | 2.6 | 1 | 1.3 | 0.5 | 0.2
1798 | 30/07/2025 10:07:21.334 | 96.792 | 76 | 100 | 70 | 52 | 30.631 | 9.288 | 6.958 | 134.625 | 29.279 | 28.247 | 28.007 | 608.266 | 25.883 | 26.793 | 1327.177 | 27.062 | 27.286 | 36.564 | 28.001 | 2.6 | 0.5 | 1.3 | 0.5 | 0.2
1799 | 30/07/2025 10:07:22.971 | 97.224 | 76 | 100 | 70 | 53 | 26.983 | 9.577 | 6.935 | 134.769 | 29.262 | 28.249 | 28.004 | 608.287 | 25.861 | 26.787 | 1329.443 | 27.037 | 27.319 | 36.654 | 23.001 | 4.4 | 0.7 | 3 | 0.5 | 0.2
1800 | 30/07/2025 10:07:24.611 | 97.008 | 76 | 100 | 70 | 52 | 30.851 | 9.576 | 6.986 | 134.708 | 29.273 | 28.247 | 27.985 | 608.229 | 25.873 | 26.794 | 1329.441 | 27.036 | 27.298 | 36.607 | 26.001 | 4.4 | 3.2 | 3 | 0.5 | 0.2
1801 | 30/07/2025 10:07:26.246 | 96.936 | 76 | 100 | 70 | 52 | 28.035 | 9.432 | 7.005 | 134.728 | 29.268 | 28.238 | 28.003 | 608.19 | 25.868 | 26.79 | 1319.292 | 27.08 | 27.321 | 36.65 | 26.001 | 4.4 | 3.2 | 3 | 0.5 | 0.2
1802 | 30/07/2025 10:07:27.881 | 96.864 | 75 | 100 | 70 | 52 | 27.465 | 9.579 | 7.032 | 134.6 | 29.268 | 28.225 | 28.008 | 608.151 | 25.851 | 26.787 | 1317.635 | 27.063 | 27.293 | 36.434 | 26.001 | 2.8 | 1.6 | 1.6 | 1.1 | 0.2
1803 | 30/07/2025 10:07:29.517 | 97.176 | 75 | 100 | 70 | 53 | 30.6 | 9.508 | 7.034 | 134.539 | 29.264 | 28.248 | 28.016 | 608.314 | 25.847 | 26.773 | 1307.538 | 27.051 | 27.297 | 36.758 | 22.001 | 2.8 | 1.9 | 1.6 | 1.1 | 0.2
1804 | 30/07/2025 10:07:31.154 | 97.632 | 77 | 100 | 70 | 52 | 30.505 | 9.432 | 7.034 | 133.085 | 29.269 | 28.248 | 27.976 | 608.224 | 25.853 | 26.762 | 1315.144 | 27.052 | 27.314 | 36.776 | 31.001 | 2.3 | 1.5 | 0.4 | 0.7 | 0.2
1805 | 30/07/2025 10:07:32.790 | 97.512 | 77 | 100 | 70 | 52 | 30.17 | 9.498 | 7.008 | 133.313 | 29.264 | 28.262 | 27.99 | 608.089 | 25.854 | 26.766 | 1315.417 | 27.063 | 27.301 | 36.791 | 25.001 | 2.3 | 1.5 | 0.4 | 0.7 | 0.2
1806 | 30/07/2025 10:07:34.425 | 98.04 | 76 | 100 | 72 | 52 | 30.908 | 9.288 | 7.004 | 133.138 | 29.269 | 28.228 | 27.982 | 608.215 | 25.867 | 26.787 | 1317.254 | 27.096 | 27.307 | 36.648 | 30.001 | 1.8 | 2.2 | 1 | 0.2 | 0.2
1807 | 30/07/2025 10:07:36.060 | 97.92 | 77 | 100 | 70 | 52 | 27.612 | 9.432 | 7.003 | 133.131 | 29.274 | 28.247 | 28.011 | 608.364 | 25.879 | 26.771 | 1299.495 | 27.061 | 27.285 | 36.471 | 30.001 | 1.8 | 2.2 | 1 | 0.2 | 0.2
1808 | 30/07/2025 10:07:37.698 | 97.656 | 77 | 100 | 70 | 52 | 28.098 | 9.284 | 7.006 | 133.148 | 29.26 | 28.268 | 28.004 | 609.405 | 25.875 | 26.773 | 1297.629 | 27.057 | 27.31 | 36.565 | 24.001 | 1.8 | 1.1 | 1 | 0.2 | 0.2
1809 | 30/07/2025 10:07:39.334 | 97.584 | 78 | 100 | 71 | 53 | 30.649 | 9.258 | 7.007 | 134.831 | 29.256 | 28.242 | 27.99 | 609.362 | 25.883 | 26.792 | 1296.338 | 27.05 | 27.313 | 36.743 | 29.001 | 3.4 | 1.2 | 1.5 | 0.8 | 0.2
1810 | 30/07/2025 10:07:40.968 | 97.464 | 76 | 100 | 73 | 52 | 29.975 | 9.286 | 7.033 | 134.687 | 29.247 | 28.236 | 27.986 | 609.534 | 25.881 | 26.79 | 1297.673 | 27.061 | 27.299 | 38.517 | 25.001 | 3.4 | 1.5 | 1.5 | 0.8 | 0.2
1811 | 30/07/2025 10:07:42.602 | 97.68 | 77 | 100 | 70 | 52 | 30.428 | 9.465 | 7.033 | 134.719 | 29.249 | 28.227 | 27.983 | 609.567 | 25.889 | 26.793 | 1297.404 | 27.064 | 27.291 | 38.561 | 21.001 | 2.2 | 1.9 | 1 | 0.5 | 0.2
1812 | 30/07/2025 10:07:44.240 | 97.248 | 78 | 100 | 71 | 52 | 30.696 | 9.288 | 7.033 | 134.585 | 29.254 | 28.252 | 28.018 | 609.466 | 25.863 | 26.798 | 1304.158 | 27.056 | 27.285 | 36.588 | 21.001 | 2.2 | 1.9 | 1 | 0.5 | 0.2
1813 | 30/07/2025 10:07:45.879 | 97.248 | 78 | 100 | 71 | 52 | 27.227 | 9.287 | 7.033 | 134.472 | 29.245 | 28.246 | 27.994 | 609.37 | 25.868 | 26.812 | 1307.248 | 27.058 | 27.324 | 38.556 | 26.001 | 2.2 | 1.2 | 1 | 0.5 | 0.2
1814 | 30/07/2025 10:07:47.515 | 97.008 | 76 | 100 | 70 | 52 | 28.531 | 9.405 | 7.034 | 134.788 | 29.238 | 28.255 | 27.973 | 609.455 | 25.888 | 26.792 | 1302.281 | 27.052 | 27.297 | 36.798 | 25.001 | 2.5 | 0.6 | 1.3 | 0 | 0.2
1815 | 30/07/2025 10:07:49.151 | 97.656 | 77 | 100 | 70 | 52 | 30.798 | 9.286 | 7.07 | 134.575 | 29.243 | 28.231 | 28.007 | 609.44 | 25.875 | 26.78 | 1307.004 | 27.074 | 27.312 | 36.695 | 32.001 | 2.5 | 2.2 | 1.3 | 0 | 0.2
1816 | 30/07/2025 10:07:50.788 | 97.176 | 78 | 100 | 71 | 52 | 29.469 | 9.288 | 7.071 | 134.471 | 29.246 | 28.242 | 27.999 | 609.546 | 25.865 | 26.787 | 1312.249 | 27.066 | 27.279 | 36.431 | 24.001 | 1.3 | 2 | 1.8 | 1.2 | 0.2
1817 | 30/07/2025 10:07:52.423 | 97.104 | 77 | 100 | 70 | 52 | 30.63 | 9.507 | 7.069 | 134.408 | 29.257 | 28.26 | 28.014 | 610.752 | 25.866 | 26.783 | 1306.497 | 27.071 | 27.301 | 36.728 | 27.001 | 1.3 | 2.4 | 1.8 | 1.2 | 0.2
1818 | 30/07/2025 10:07:54.061 | 97.392 | 77 | 100 | 70 | 52 | 30.455 | 9.577 | 7.072 | 134.597 | 29.263 | 28.243 | 27.99 | 610.726 | 25.864 | 26.787 | 1297.239 | 27.029 | 27.301 | 36.844 | 27.001 | 1.3 | 2.4 | 1.8 | 1.2 | 0.2
1819 | 30/07/2025 10:07:55.697 | 97.44 | 78 | 100 | 71 | 52 | 26.766 | 9.581 | 7.07 | 134.688 | 29.264 | 28.247 | 27.985 | 610.633 | 25.982 | 26.786 | 1287.439 | 27.066 | 27.296 | 36.565 | 29.001 | 2.8 | 1.4 | 1.2 | 1.4 | 0.1
1820 | 30/07/2025 10:07:57.333 | 96.816 | 76 | 100 | 70 | 52 | 29.055 | 9.288 | 7.004 | 134.477 | 29.266 | 28.22 | 27.996 | 610.729 | 26.007 | 26.795 | 1282.201 | 27.092 | 27.303 | 36.344 | 33.001 | 2.8 | 0.7 | 1.2 | 1.4 | 0.1
1821 | 30/07/2025 10:07:58.969 | 97.824 | 77 | 100 | 70 | 52 | 30.806 | 9.514 | 7.004 | 134.577 | 29.278 | 28.248 | 28.008 | 610.651 | 25.881 | 26.78 | 1276.469 | 27.056 | 27.278 | 36.518 | 31.001 | 3.4 | 1.3 | 1.2 | 0.5 | 0.1
1822 | 30/07/2025 10:08:00.604 | 97.704 | 77 | 100 | 70 | 52 | 27.902 | 9.431 | 7.007 | 134.458 | 29.27 | 28.256 | 27.99 | 610.614 | 25.866 | 26.799 | 1267.889 | 27.06 | 27.305 | 36.782 | 27.001 | 3.4 | 1.9 | 1.2 | 0.5 | 0.1
1823 | 30/07/2025 10:08:02.239 | 97.44 | 77 | 100 | 70 | 52 | 30.686 | 9.279 | 7.004 | 134.812 | 29.288 | 28.253 | 27.999 | 610.783 | 25.941 | 26.776 | 1264.549 | 27.041 | 27.303 | 36.758 | 27.001 | 3.4 | 1.9 | 1.2 | 0.5 | 0.1
1824 | 30/07/2025 10:08:03.877 | 97.224 | 77 | 100 | 71 | 52 | 29.971 | 9.361 | 7.005 | 134.666 | 29.261 | 28.251 | 27.991 | 610.146 | 25.846 | 26.776 | 1274.497 | 27.091 | 27.33 | 36.732 | 25.001 | 1.4 | 1.6 | 0.6 | 0.5 | 0.1
1825 | 30/07/2025 10:08:05.519 | 96.648 | 75 | 100 | 70 | 52 | 26.638 | 9.514 | 7.003 | 134.64 | 29.261 | 28.226 | 28.015 | 609.382 | 25.904 | 26.775 | 1269.349 | 27.069 | 27.293 | 36.511 | 31.001 | 1.4 | 2.3 | 0.6 | 0.5 | 0.1
1826 | 30/07/2025 10:08:07.154 | 96.12 | 76 | 100 | 70 | 52 | 29.739 | 9.463 | 7.009 | 134.657 | 29.259 | 28.253 | 28.011 | 609.485 | 25.9 | 26.767 | 1277.305 | 27.046 | 27.302 | 36.491 | 28.001 | 2.1 | 2.1 | 1.4 | 0.5 | 0.2
1827 | 30/07/2025 10:08:08.799 | 94.656 | 75 | 100 | 70 | 52 | 27.142 | 9.546 | 7.068 | 134.769 | 29.269 | 28.245 | 27.998 | 609.663 | 25.987 | 26.77 | 1278.221 | 27.038 | 27.307 | 36.644 | 23.001 | 2.1 | 1.4 | 1.4 | 0.5 | 0.2
1828 | 30/07/2025 10:08:10.440 | 94.92 | 75 | 100 | 70 | 52 | 28.654 | 9.508 | 7.061 | 134.648 | 29.257 | 28.257 | 27.997 | 611.349 | 25.858 | 26.771 | 1268.27 | 27.054 | 27.307 | 36.629 | 26.001 | 4.4 | 1.3 | 0.7 | 0.1 | 0.2
1829 | 30/07/2025 10:08:12.076 | 94.2 | 72 | 100 | 70 | 52 | 30.743 | 9.437 | 7.033 | 134.536 | 29.252 | 28.23 | 27.969 | 611.803 | 25.964 | 26.805 | 1262.19 | 27.067 | 27.308 | 36.658 | 26.001 | 4.4 | 1.3 | 0.7 | 0.1 | 0.2
1830 | 30/07/2025 10:08:13.712 | 94.008 | 74 | 100 | 71 | 51 | 29.368 | 9.564 | 7.031 | 134.518 | 29.264 | 28.242 | 28.013 | 613.224 | 26.025 | 26.789 | 1274.569 | 27.054 | 27.288 | 36.54 | 29.001 | 4.4 | 2.9 | 0.7 | 0.1 | 0.2
1831 | 30/07/2025 10:08:15.348 | 93.84 | 72 | 100 | 71 | 52 | 26.861 | 9.45 | 7.034 | 134.474 | 29.257 | 28.262 | 28.007 | 613.076 | 26.036 | 26.801 | 1269.205 | 27.06 | 27.315 | 36.788 | 25.001 | 5.3 | 2.1 | 0.6 | 0 | 0.3
1832 | 30/07/2025 10:08:16.996 | 94.368 | 72 | 100 | 70 | 53 | 30.164 | 9.285 | 7.033 | 134.654 | 29.247 | 28.246 | 27.99 | 613.06 | 25.975 | 26.81 | 1268.749 | 27.045 | 27.314 | 36.738 | 25.001 | 5.3 | 2.3 | 0.6 | 0 | 0.3
1833 | 30/07/2025 10:08:18.634 | 93.936 | 71 | 100 | 71 | 51 | 26.895 | 9.506 | 7.033 | 134.681 | 29.241 | 28.264 | 27.968 | 613.022 | 25.914 | 26.802 | 1269.845 | 27.084 | 27.308 | 36.692 | 28.001 | 2.6 | 1.7 | 0.6 | 0.5 | 0.2
1834 | 30/07/2025 10:08:20.270 | 95.4 | 74 | 100 | 71 | 52 | 29.192 | 9.505 | 7.031 | 134.85 | 29.245 | 28.229 | 28.003 | 613.177 | 26.042 | 26.79 | 1284.145 | 27.082 | 27.298 | 36.694 | 28.001 | 2.6 | 1.7 | 0.6 | 0.5 | 0.2
1835 | 30/07/2025 10:08:21.912 | 95.688 | 75 | 100 | 71 | 52 | 30.873 | 9.58 | 7.032 | 134.616 | 29.23 | 28.249 | 28.017 | 613.097 | 26.013 | 26.788 | 1291.166 | 27.065 | 27.289 | 38.244 | 26.001 | 2.6 | 2.7 | 0.6 | 0.5 | 0.2
1836 | 30/07/2025 10:08:23.546 | 95.616 | 73 | 100 | 70 | 52 | 28.971 | 9.483 | 7.036 | 133.14 | 29.245 | 28.245 | 27.998 | 613.072 | 26.024 | 26.81 | 1290.601 | 27.049 | 27.323 | 36.733 | 23.001 | 2.4 | 1.6 | 0.7 | 0.5 | 0.2
1837 | 30/07/2025 10:08:25.189 | 96.048 | 75 | 100 | 72 | 52 | 27.085 | 9.377 | 7.071 | 133.345 | 29.239 | 28.252 | 27.974 | 613.056 | 26.024 | 26.795 | 1299.082 | 27.053 | 27.303 | 36.663 | 25.001 | 2.4 | 1.6 | 0.7 | 0.5 | 0.2
1838 | 30/07/2025 10:08:26.826 | 96.744 | 75 | 100 | 70 | 52 | 30.008 | 9.4 | 7.074 | 133.223 | 29.257 | 28.242 | 27.963 | 612.892 | 26.022 | 26.803 | 1311.576 | 27.074 | 27.308 | 36.716 | 28.001 | 3 | 3.5 | 1 | 0.3 | 0.2
1839 | 30/07/2025 10:08:28.461 | 97.776 | 77 | 100 | 70 | 52 | 26.66 | 9.498 | 7.069 | 133.153 | 29.262 | 28.232 | 28.024 | 613.121 | 26.021 | 26.785 | 1311.763 | 27.064 | 27.297 | 36.326 | 30.001 | 3 | 2.9 | 1 | 0.3 | 0.2
1840 | 30/07/2025 10:08:30.097 | 97.944 | 76 | 100 | 70 | 52 | 29.57 | 9.312 | 7.072 | 133.003 | 29.273 | 28.265 | 28.002 | 613.112 | 25.864 | 26.79 | 1309.666 | 27.076 | 27.299 | 36.491 | 30.001 | 3 | 2.9 | 1 | 0.3 | 0.2
1841 | 30/07/2025 10:08:31.734 | 98.064 | 77 | 100 | 70 | 52 | 30.909 | 9.318 | 7.07 | 133.542 | 29.282 | 28.25 | 28 | 613.18 | 25.862 | 26.796 | 1299.82 | 27.027 | 27.306 | 36.667 | 22.001 | 1.8 | 2.7 | 2 | 0.5 | 0.2
1842 | 30/07/2025 10:08:33.372 | 98.544 | 78 | 100 | 71 | 52 | 28.21 | 9.289 | 7.031 | 133.203 | 29.26 | 28.245 | 27.973 | 613.052 | 26.004 | 26.787 | 1287.442 | 27.07 | 27.309 | 36.513 | 26.001 | 1.8 | 3.7 | 2 | 0.5 | 0.2
1843 | 30/07/2025 10:08:35.012 | 98.352 | 77 | 100 | 70 | 51 | 27.408 | 9.579 | 7.033 | 133.246 | 29.267 | 28.226 | 27.995 | 613.188 | 26.011 | 26.789 | 1291.916 | 27.081 | 27.296 | 36.613 | 32.001 | 2.8 | 2.2 | 0.1 | 0.7 | 0.2
1844 | 30/07/2025 10:08:36.645 | 98.76 | 77 | 100 | 71 | 52 | 29.371 | 9.441 | 7.032 | 133.193 | 29.256 | 28.233 | 28.012 | 613.166 | 26.008 | 26.768 | 1287.593 | 27.064 | 27.293 | 36.372 | 28.001 | 2.8 | 1.1 | 0.1 | 0.7 | 0.2
1845 | 30/07/2025 10:08:38.286 | 98.952 | 78 | 100 | 70 | 52 | 26.742 | 9.425 | 7.035 | 132.868 | 29.263 | 28.249 | 27.995 | 613.069 | 26.01 | 26.78 | 1283.541 | 27.04 | 27.306 | 36.656 | 28.001 | 2.8 | 1.1 | 0.1 | 0.7 | 0.2
1846 | 30/07/2025 10:08:39.923 | 98.592 | 77 | 100 | 70 | 52 | 30.156 | 9.55 | 7.032 | 133.298 | 29.266 | 28.252 | 28.001 | 613.293 | 26.017 | 26.767 | 1288.082 | 27.04 | 27.309 | 36.87 | 23.001 | 2.3 | 2.1 | 0.6 | 0.6 | 0.1
1847 | 30/07/2025 10:08:41.560 | 98.352 | 77 | 100 | 71 | 52 | 30.911 | 9.284 | 7.072 | 133.301 | 29.246 | 28.241 | 27.974 | 613.003 | 26.005 | 26.77 | 1282.625 | 27.089 | 27.316 | 36.78 | 23.001 | 2.3 | 1.8 | 0.6 | 0.6 | 0.1
1848 | 30/07/2025 10:08:43.197 | 98.496 | 76 | 100 | 70 | 52 | 27.495 | 9.422 | 7.033 | 133.234 | 29.26 | 28.222 | 28.012 | 613.131 | 26.031 | 26.783 | 1289.259 | 27.064 | 27.292 | 36.504 | 27.001 | 2.5 | 2 | 0.7 | 0.4 | 0.1
1849 | 30/07/2025 10:08:44.837 | 98.496 | 76 | 100 | 71 | 51 | 30.893 | 9.433 | 7.031 | 132.951 | 29.249 | 28.247 | 27.998 | 613.065 | 26.012 | 26.793 | 1296.559 | 27.087 | 27.288 | 36.559 | 27.001 | 2.5 | 2.1 | 0.7 | 0.4 | 0.1
1850 | 30/07/2025 10:08:46.475 | 98.424 | 76 | 100 | 71 | 51 | 28.763 | 9.507 | 7.033 | 133.183 | 29.263 | 28.247 | 28.007 | 613.056 | 26.044 | 26.791 | 1307.121 | 27.042 | 27.301 | 36.826 | 29.001 | 3.4 | 1.9 | 1.7 | 0 | 0.1
1851 | 30/07/2025 10:08:48.113 | 98.256 | 78 | 100 | 70 | 53 | 27.104 | 9.286 | 7.031 | 133.254 | 29.25 | 28.254 | 27.993 | 613.082 | 26.025 | 26.78 | 1297.719 | 27.053 | 27.301 | 36.801 | 29.001 | 3.4 | 1.9 | 1.7 | 0 | 0.1
1852 | 30/07/2025 10:08:49.749 | 98.112 | 77 | 100 | 70 | 52 | 30.496 | 9.432 | 7.034 | 133.291 | 29.247 | 28.23 | 27.967 | 612.938 | 26.023 | 26.813 | 1292.565 | 27.066 | 27.312 | 36.675 | 25.001 | 3.4 | 2.4 | 1.7 | 0 | 0.1
1853 | 30/07/2025 10:08:51.385 | 98.184 | 76 | 100 | 70 | 50 | 30.82 | 9.284 | 7.033 | 133.154 | 29.255 | 28.239 | 28.032 | 613.4 | 26.029 | 26.797 | 1287.643 | 27.074 | 27.295 | 36.477 | 27.001 | 3 | 1.2 | 0.6 | 0 | 0.1
1854 | 30/07/2025 10:08:53.029 | 97.824 | 77 | 100 | 71 | 53 | 27.272 | 9.521 | 7.032 | 133.046 | 29.236 | 28.257 | 28.006 | 613.038 | 26.025 | 26.807 | 1287.47 | 27.064 | 27.313 | 36.609 | 25.001 | 3 | 1.4 | 0.6 | 0 | 0.1
1855 | 30/07/2025 10:08:54.666 | 97.848 | 77 | 100 | 71 | 52 | 30.946 | 9.477 | 7.006 | 133.501 | 29.24 | 28.249 | 28.01 | 613.181 | 26.008 | 26.783 | 1287.555 | 27.036 | 27.313 | 36.554 | 27.001 | 1.9 | 2.2 | 0.6 | 0.7 | 0.2
1856 | 30/07/2025 10:08:56.307 | 97.416 | 76 | 100 | 70 | 52 | 28.39 | 9.498 | 7.006 | 134.583 | 29.231 | 28.251 | 27.967 | 612.878 | 26.017 | 26.798 | 1287.564 | 27.082 | 27.296 | 36.859 | 27.001 | 1.9 | 2.2 | 0.6 | 0.7 | 0.2
1857 | 30/07/2025 10:08:57.944 | 97.824 | 76 | 100 | 71 | 52 | 27.525 | 9.284 | 7.003 | 134.792 | 29.26 | 28.239 | 28.012 | 613.036 | 26.034 | 26.789 | 1288.601 | 27.065 | 27.299 | 36.786 | 25.001 | 1.9 | 2.3 | 0.6 | 0.7 | 0.2
1858 | 30/07/2025 10:08:59.580 | 97.848 | 77 | 100 | 69 | 52 | 30.611 | 9.583 | 7.003 | 134.437 | 29.253 | 28.252 | 28.012 | 612.569 | 26.012 | 26.779 | 1297.779 | 27.066 | 27.284 | 36.406 | 26.001 | 3.6 | 1 | 0 | 0 | 0.2
1859 | 30/07/2025 10:09:01.214 | 97.92 | 77 | 100 | 71 | 52 | 30.532 | 9.58 | 7.006 | 134.535 | 29.265 | 28.246 | 27.986 | 611.883 | 26.017 | 26.804 | 1309.953 | 27.053 | 27.308 | 36.795 | 30.001 | 3.6 | 0.6 | 0 | 0 | 0.2
1860 | 30/07/2025 10:09:02.850 | 98.04 | 77 | 100 | 70 | 52 | 26.933 | 9.428 | 6.934 | 133.023 | 29.276 | 28.25 | 27.991 | 610.686 | 26.02 | 26.783 | 1312.457 | 27.06 | 27.303 | 36.692 | 22.001 | 4.4 | 1 | 0.6 | 0 | 0.3
1861 | 30/07/2025 10:09:04.489 | 97.584 | 76 | 100 | 71 | 52 | 30.956 | 9.321 | 6.936 | 133.213 | 29.278 | 28.237 | 27.961 | 610.584 | 26.011 | 26.796 | 1315.968 | 27.074 | 27.308 | 36.789 | 22.001 | 4.4 | 1 | 0.6 | 0 | 0.3
1862 | 30/07/2025 10:09:06.126 | 97.56 | 76 | 100 | 71 | 53 | 27.735 | 9.361 | 6.933 | 133.084 | 29.265 | 28.237 | 28.021 | 609.531 | 26.017 | 26.779 | 1311.985 | 27.063 | 27.291 | 36.591 | 22.001 | 4.4 | 1 | 0.6 | 0 | 0.3
1863 | 30/07/2025 10:09:07.762 | 97.368 | 77 | 100 | 72 | 52 | 27.924 | 9.287 | 6.969 | 132.921 | 29.265 | 28.259 | 28.008 | 609.395 | 26.004 | 26.782 | 1309.796 | 27.08 | 27.296 | 36.595 | 25.001 | 4.4 | 0.8 | 1.2 | 0.6 | 0.2
1864 | 30/07/2025 10:09:09.400 | 97.728 | 75 | 100 | 70 | 52 | 30.723 | 9.28 | 7.005 | 133.332 | 29.258 | 28.243 | 27.996 | 609.275 | 26.021 | 26.79 | 1304.629 | 27.023 | 27.31 | 36.694 | 27.001 | 4.4 | 1.2 | 1.2 | 0.6 | 0.2
1865 | 30/07/2025 10:09:11.036 | 98.376 | 77 | 100 | 70 | 52 | 30.026 | 9.506 | 7.004 | 133.242 | 29.256 | 28.249 | 27.977 | 609.241 | 26.016 | 26.782 | 1297.046 | 27.062 | 27.312 | 36.453 | 27.001 | 3.2 | 3.1 | 0.3 | 1 | 0.2
1866 | 30/07/2025 10:09:12.672 | 98.952 | 77 | 100 | 71 | 52 | 30.425 | 9.325 | 7.004 | 133.425 | 29.282 | 28.237 | 27.983 | 609.404 | 25.999 | 26.777 | 1295.956 | 27.065 | 27.302 | 36.644 | 24.001 | 3.2 | 2.2 | 0.3 | 1 | 0.2
1867 | 30/07/2025 10:09:14.306 | 99.12 | 77 | 100 | 71 | 52 | 30.768 | 9.432 | 7.002 | 133.131 | 29.255 | 28.222 | 28.002 | 609.44 | 26.01 | 26.762 | 1303.071 | 27.077 | 27.295 | 36.398 | 24.001 | 3.2 | 2.2 | 0.3 | 1 | 0.2
1868 | 30/07/2025 10:09:15.947 | 99.072 | 77 | 100 | 71 | 53 | 27.124 | 9.436 | 7.006 | 132.886 | 29.255 | 28.25 | 27.98 | 608.109 | 26.017 | 26.777 | 1311.145 | 27.052 | 27.283 | 36.746 | 26.001 | 1.7 | 0.2 | 0.9 | 0.6 | 0.2
1869 | 30/07/2025 10:09:17.584 | 98.76 | 77 | 100 | 71 | 52 | 28.528 | 9.582 | 7.005 | 133.377 | 29.269 | 28.254 | 28.004 | 608.224 | 26.013 | 26.765 | 1307.077 | 27.041 | 27.309 | 36.498 | 27.001 | 1.7 | 3 | 0.9 | 0.6 | 0.2
1870 | 30/07/2025 10:09:19.219 | 98.208 | 78 | 100 | 71 | 52 | 30.785 | 9.29 | 7.005 | 133.082 | 29.256 | 28.244 | 27.974 | 608.094 | 26.016 | 26.786 | 1314.615 | 27.093 | 27.308 | 36.64 | 28.001 | 2.6 | 1.5 | 0.1 | 0.5 | 0.2
1871 | 30/07/2025 10:09:20.855 | 98.544 | 77 | 100 | 71 | 52 | 27.536 | 9.431 | 7.004 | 133.251 | 29.251 | 28.234 | 28 | 608.18 | 26.011 | 26.782 | 1311.929 | 27.063 | 27.297 | 36.595 | 26.001 | 2.6 | 1.8 | 0.1 | 0.5 | 0.2
1872 | 30/07/2025 10:09:22.488 | 98.4 | 76 | 100 | 71 | 52 | 30.615 | 9.464 | 7.005 | 133.082 | 29.249 | 28.24 | 27.998 | 608.112 | 26.032 | 26.809 | 1309.507 | 27.078 | 27.293 | 36.363 | 26.001 | 3.9 | 1 | 0.1 | 0.9 | 0.1
1873 | 30/07/2025 10:09:24.122 | 98.976 | 79 | 100 | 70 | 52 | 30.439 | 9.433 | 7.02 | 133.175 | 29.252 | 28.246 | 28.006 | 608.234 | 26.03 | 26.8 | 1309.521 | 27.046 | 27.313 | 36.794 | 26.001 | 3.9 | 1 | 0.1 | 0.9 | 0.1
1874 | 30/07/2025 10:09:25.755 | 99.336 | 79 | 100 | 70 | 52 | 26.808 | 9.288 | 7.031 | 133.287 | 29.252 | 28.254 | 27.996 | 606.999 | 26.035 | 26.802 | 1309.773 | 27.047 | 27.329 | 36.589 | 27.001 | 3.9 | 1.8 | 0.1 | 0.9 | 0.1
1875 | 30/07/2025 10:09:27.387 | 99.336 | 77 | 100 | 70 | 52 | 29.166 | 9.437 | 7.035 | 133.02 | 29.24 | 28.238 | 27.965 | 606.823 | 26.014 | 26.8 | 1307.24 | 27.072 | 27.295 | 36.803 | 25.001 | 2 | 2 | 0.1 | 1 | 0.1
1876 | 30/07/2025 10:09:29.020 | 99.312 | 79 | 99 | 70 | 52 | 30.841 | 9.488 | 7.032 | 133.25 | 29.244 | 28.236 | 28.015 | 607.146 | 26.008 | 26.791 | 1305.542 | 27.057 | 27.286 | 36.488 | 24.001 | 2 | 2 | 0.1 | 1 | 0.1
1877 | 30/07/2025 10:09:30.653 | 99.408 | 79 | 100 | 71 | 52 | 28.067 | 9.433 | 7.033 | 133.008 | 29.239 | 28.251 | 28.004 | 606.929 | 26.031 | 26.795 | 1305.184 | 27.059 | 27.275 | 36.634 | 25.001 | 1.9 | 1.8 | 0.8 | 0.6 | 0.1
1878 | 30/07/2025 10:09:32.289 | 99.216 | 79 | 100 | 70 | 52 | 30.675 | 9.449 | 7.016 | 133.223 | 29.25 | 28.252 | 28.019 | 608.002 | 26.026 | 26.794 | 1299.763 | 27.037 | 27.306 | 36.708 | 25.001 | 1.9 | 1.8 | 0.8 | 0.6 | 0.1
1879 | 30/07/2025 10:09:33.925 | 99.768 | 77 | 100 | 70 | 52 | 30.093 | 9.433 | 7.005 | 133.203 | 29.255 | 28.253 | 27.975 | 608.072 | 26.015 | 26.796 | 1297.134 | 27.079 | 27.303 | 36.626 | 28.001 | 1.9 | 1.9 | 0.8 | 0.6 | 0.1
1880 | 30/07/2025 10:09:35.559 | 99.336 | 77 | 100 | 71 | 52 | 26.804 | 9.445 | 7.004 | 133.406 | 29.272 | 28.23 | 28.004 | 607.58 | 26.019 | 26.791 | 1294.67 | 27.06 | 27.293 | 36.711 | 24.001 | 2.1 | 0.6 | 0.9 | 0.6 | 0.2
1881 | 30/07/2025 10:09:37.194 | 99.384 | 78 | 100 | 70 | 52 | 29.69 | 9.521 | 7.003 | 134.481 | 29.257 | 28.25 | 28.009 | 605.849 | 26.011 | 26.784 | 1306.634 | 27.069 | 27.29 | 36.415 | 24.001 | 2.1 | 1.1 | 0.9 | 0.6 | 0.2
1882 | 30/07/2025 10:09:38.829 | 99.072 | 78 | 100 | 71 | 51 | 30.925 | 9.567 | 7.007 | 134.631 | 29.264 | 28.243 | 27.994 | 604.37 | 26.012 | 26.794 | 1317.197 | 27.047 | 27.3 | 36.789 | 29.001 | 3.3 | 1.4 | 0.7 | 0 | 0.2
1883 | 30/07/2025 10:09:40.463 | 98.736 | 78 | 100 | 69 | 52 | 28.466 | 9.517 | 7.004 | 134.654 | 29.264 | 28.264 | 28.009 | 604.573 | 26.006 | 26.789 | 1319.045 | 27.044 | 27.321 | 36.661 | 30.001 | 3.3 | 2 | 0.7 | 0 | 0.2
1884 | 30/07/2025 10:09:42.097 | 98.88 | 77 | 99 | 70 | 52 | 30.807 | 9.496 | 7.006 | 134.761 | 29.269 | 28.239 | 27.948 | 604.222 | 26.02 | 26.79 | 1327.469 | 27.062 | 27.298 | 36.753 | 30.001 | 3.3 | 2 | 0.7 | 0 | 0.2
1885 | 30/07/2025 10:09:43.733 | 98.952 | 77 | 100 | 70 | 52 | 29.613 | 9.578 | 7.032 | 134.687 | 29.265 | 28.228 | 28.014 | 604.673 | 26.005 | 26.777 | 1317.399 | 27.067 | 27.294 | 36.574 | 28.001 | 2.1 | 1 | 1.1 | 0.5 | 0.4
1886 | 30/07/2025 10:09:45.367 | 99.72 | 79 | 100 | 70 | 52 | 26.801 | 9.519 | 7.033 | 134.398 | 29.258 | 28.256 | 27.996 | 604.474 | 25.992 | 26.771 | 1310.023 | 27.085 | 27.288 | 36.502 | 31.001 | 2.1 | 1.9 | 1.1 | 0.5 | 0.4
1887 | 30/07/2025 10:09:47.001 | 99.72 | 79 | 100 | 72 | 52 | 30.15 | 9.35 | 7.032 | 134.848 | 29.268 | 28.251 | 28 | 604.52 | 26.005 | 26.761 | 1308.831 | 27.025 | 27.319 | 36.649 | 29.001 | 1.7 | 1.8 | 0.6 | 0.8 | 0.4
1888 | 30/07/2025 10:09:48.637 | 99.888 | 79 | 100 | 70 | 51 | 26.898 | 9.427 | 7.025 | 134.632 | 29.251 | 28.245 | 27.983 | 604.404 | 26 | 26.769 | 1306.963 | 27.054 | 27.307 | 36.713 | 28.001 | 1.7 | 1.2 | 0.6 | 0.8 | 0.4
1889 | 30/07/2025 10:09:50.271 | 100.104 | 80 | 100 | 70 | 50 | 29.142 | 9.533 | 7.003 | 134.673 | 29.274 | 28.243 | 27.999 | 603.269 | 26.018 | 26.768 | 1300.842 | 27.071 | 27.299 | 36.794 | 28.001 | 1.7 | 1.2 | 0.6 | 0.8 | 0.4
1890 | 30/07/2025 10:09:51.904 | 100.128 | 81 | 100 | 70 | 52 | 30.922 | 9.506 | 7.069 | 134.608 | 29.241 | 28.229 | 27.989 | 603.254 | 26.017 | 26.768 | 1297.05 | 27.073 | 27.302 | 36.413 | 25.001 | 4.4 | 0.9 | 0 | 0.5 | 0.3
1891 | 30/07/2025 10:09:53.537 | 99.984 | 77 | 100 | 70 | 52 | 28.767 | 9.304 | 7.073 | 134.327 | 29.247 | 28.256 | 27.987 | 604.533 | 26.019 | 26.78 | 1297.438 | 27.055 | 27.29 | 36.647 | 33.001 | 4.4 | 2.5 | 0 | 0.5 | 0.3
1892 | 30/07/2025 10:09:55.172 | 99.528 | 77 | 100 | 71 | 51 | 27.026 | 9.288 | 7.071 | 134.869 | 29.245 | 28.255 | 28.009 | 604.589 | 25.996 | 26.783 | 1295.034 | 27.038 | 27.309 | 36.666 | 28.001 | 3.2 | 1.7 | 0.6 | 0.6 | 0.2
1893 | 30/07/2025 10:09:56.806 | 99.528 | 78 | 100 | 70 | 52 | 29.926 | 9.497 | 7.072 | 134.834 | 29.254 | 28.246 | 27.984 | 603.233 | 26.035 | 26.798 | 1287.805 | 27.047 | 27.298 | 36.756 | 31.001 | 3.2 | 2.7 | 0.6 | 0.6 | 0.2
1894 | 30/07/2025 10:09:58.440 | 99.36 | 79 | 100 | 70 | 52 | 26.701 | 9.409 | 7.069 | 134.74 | 29.246 | 28.24 | 28 | 603.274 | 26.029 | 26.797 | 1291.171 | 27.073 | 27.308 | 36.603 | 27.001 | 1.9 | 3 | 0.6 | 1.3 | 0.2
1895 | 30/07/2025 10:10:00.075 | 99.36 | 78 | 100 | 70 | 52 | 29.66 | 9.434 | 7.034 | 134.392 | 29.221 | 28.236 | 27.997 | 603.365 | 26.025 | 26.802 | 1287.284 | 27.082 | 27.291 | 36.421 | 27.001 | 1.9 | 3 | 0.6 | 1.3 | 0.2
1896 | 30/07/2025 10:10:01.711 | 99.48 | 77 | 100 | 71 | 52 | 30.933 | 9.499 | 7.034 | 134.643 | 29.23 | 28.248 | 27.996 | 603.32 | 26.03 | 26.78 | 1277.648 | 27.045 | 27.296 | 36.662 | 30.001 | 1.9 | 2.1 | 0.6 | 1.3 | 0.2
1897 | 30/07/2025 10:10:03.346 | 99.624 | 79 | 100 | 70 | 52 | 28.299 | 9.484 | 7.072 | 134.781 | 29.221 | 28.248 | 27.986 | 603.311 | 26.009 | 26.788 | 1277.097 | 27.055 | 27.323 | 36.574 | 28.001 | 2.5 | 2.6 | 0.1 | 0.5 | 0.2
1898 | 30/07/2025 10:10:04.982 | 99.024 | 79 | 100 | 70 | 53 | 27.497 | 9.285 | 7.073 | 134.802 | 29.239 | 28.233 | 27.957 | 603.084 | 26.021 | 26.792 | 1284.772 | 27.076 | 27.304 | 36.713 | 28.001 | 2.5 | 1.7 | 0.1 | 0.5 | 0.2
1899 | 30/07/2025 10:10:06.618 | 98.904 | 77 | 100 | 70 | 52 | 29.569 | 9.428 | 7.072 | 134.384 | 29.236 | 28.242 | 28.013 | 603.361 | 26.015 | 26.801 | 1284.946 | 27.087 | 27.299 | 36.585 | 26.001 | 2.4 | 2.1 | 1.1 | 0.7 | 0.1
1900 | 30/07/2025 10:10:08.254 | 99.504 | 79 | 100 | 71 | 52 | 26.835 | 9.518 | 7.071 | 134.315 | 29.255 | 28.242 | 28.003 | 603.196 | 26.026 | 26.789 | 1287.539 | 27.056 | 27.278 | 36.42 | 26.001 | 2.4 | 2.1 | 1.1 | 0.7 | 0.1
1901 | 30/07/2025 10:10:09.891 | 99.816 | 78 | 100 | 70 | 52 | 30.074 | 9.283 | 7.071 | 134.696 | 29.271 | 28.259 | 28 | 603.451 | 26.011 | 26.77 | 1287.619 | 27.031 | 27.304 | 36.604 | 23.001 | 2.4 | 0.8 | 1.1 | 0.7 | 0.1
1902 | 30/07/2025 10:10:11.528 | 99.504 | 78 | 100 | 70 | 52 | 30.93 | 9.353 | 7.035 | 134.733 | 29.26 | 28.246 | 27.962 | 603.07 | 26.019 | 26.803 | 1286.96 | 27.065 | 27.306 | 36.609 | 28.001 | 3.2 | 2.4 | 1.3 | 1.1 | 0.1
1903 | 30/07/2025 10:10:13.164 | 99.216 | 78 | 100 | 70 | 52 | 27.744 | 9.438 | 7.032 | 134.703 | 29.293 | 28.24 | 27.998 | 603.415 | 26.013 | 26.785 | 1287.333 | 27.07 | 27.299 | 36.591 | 22.001 | 3.2 | 1.8 | 1.3 | 1.1 | 0.1
1904 | 30/07/2025 10:10:14.798 | 98.904 | 77 | 100 | 71 | 52 | 30.935 | 9.287 | 7.033 | 134.662 | 29.28 | 28.231 | 28.003 | 603.333 | 25.998 | 26.786 | 1287.346 | 27.061 | 27.298 | 36.494 | 23.001 | 1.5 | 1.4 | 0 | 0.5 | 0.1
1905 | 30/07/2025 10:10:16.434 | 99.072 | 78 | 100 | 70 | 52 | 29.014 | 9.319 | 7.004 | 134.489 | 29.264 | 28.25 | 28.017 | 603.489 | 26.014 | 26.772 | 1279.742 | 27.066 | 27.292 | 36.514 | 25.001 | 1.5 | 2.8 | 0 | 0.5 | 0.1
1906 | 30/07/2025 10:10:18.069 | 98.904 | 78 | 100 | 70 | 52 | 27.155 | 9.286 | 7.005 | 134.659 | 29.257 | 28.254 | 28.001 | 603.282 | 25.989 | 26.778 | 1290.108 | 27.046 | 27.308 | 36.695 | 25.001 | 1.5 | 2.8 | 0 | 0.5 | 0.1
1907 | 30/07/2025 10:10:19.703 | 98.616 | 78 | 100 | 69 | 52 | 30.532 | 9.485 | 7.006 | 134.815 | 29.257 | 28.244 | 27.98 | 603.174 | 26.022 | 26.779 | 1306.263 | 27.062 | 27.298 | 36.598 | 30.001 | 1.9 | 1.3 | 0.7 | 0 | 0
1908 | 30/07/2025 10:10:21.338 | 97.824 | 77 | 100 | 70 | 53 | 30.891 | 9.284 | 7.004 | 134.72 | 29.254 | 28.228 | 28.021 | 603.521 | 26.013 | 26.777 | 1306.279 | 27.056 | 27.308 | 36.531 | 26.001 | 1.9 | 1.5 | 0.7 | 0 | 0
1909 | 30/07/2025 10:10:22.973 | 97.896 | 77 | 100 | 70 | 52 | 27.347 | 9.428 | 7.005 | 134.366 | 29.257 | 28.249 | 27.983 | 603.277 | 26.015 | 26.777 | 1297.185 | 27.066 | 27.286 | 36.56 | 29.001 | 4.7 | 2.6 | 0.9 | 0 | 0.1
1910 | 30/07/2025 10:10:24.610 | 98.088 | 77 | 100 | 70 | 53 | 31.018 | 9.324 | 7.005 | 134.382 | 29.244 | 28.257 | 28.009 | 603.295 | 26.009 | 26.768 | 1288.049 | 27.052 | 27.307 | 36.641 | 29.001 | 4.7 | 2.5 | 0.9 | 0 | 0.1
1911 | 30/07/2025 10:10:26.244 | 97.68 | 77 | 100 | 70 | 52 | 28.291 | 9.509 | 7.006 | 134.703 | 29.25 | 28.249 | 27.98 | 603.298 | 26.016 | 26.78 | 1296.759 | 27.025 | 27.298 | 36.733 | 29.001 | 4.7 | 2.5 | 0.9 | 0 | 0.1
1912 | 30/07/2025 10:10:27.881 | 98.136 | 78 | 100 | 71 | 51 | 27.449 | 9.289 | 7.005 | 134.746 | 29.254 | 28.243 | 28.01 | 603.303 | 26.035 | 26.782 | 1299.986 | 27.071 | 27.303 | 36.759 | 31.001 | 3.3 | 2.2 | 0 | 0.5 | 0.1
1913 | 30/07/2025 10:10:29.517 | 98.016 | 77 | 100 | 70 | 52 | 30.622 | 9.325 | 7.003 | 134.446 | 29.253 | 28.242 | 28.007 | 603.218 | 26.028 | 26.805 | 1292.755 | 27.079 | 27.31 | 36.226 | 28.001 | 3.3 | 1.2 | 0 | 0.5 | 0.1
1914 | 30/07/2025 10:10:31.151 | 97.44 | 77 | 100 | 70 | 52 | 30.474 | 9.433 | 7.005 | 134.369 | 29.241 | 28.248 | 27.994 | 603.405 | 26.035 | 26.784 | 1295.222 | 27.053 | 27.287 | 36.681 | 31.001 | 2.3 | 2 | 0.6 | 0 | 0.1
1915 | 30/07/2025 10:10:32.786 | 97.704 | 78 | 100 | 71 | 50 | 30.101 | 9.516 | 7.006 | 134.528 | 29.248 | 28.269 | 28.005 | 603.395 | 26.023 | 26.815 | 1285.592 | 27.064 | 27.309 | 36.772 | 27.001 | 2.3 | 3.4 | 0.6 | 0 | 0.1
1916 | 30/07/2025 10:10:34.422 | 97.416 | 77 | 100 | 69 | 52 | 30.951 | 9.447 | 7.003 | 134.801 | 29.234 | 28.244 | 27.992 | 603.183 | 26.038 | 26.804 | 1283.009 | 27.037 | 27.311 | 36.839 | 26.001 | 2.3 | 2.3 | 0.7 | 0 | 0.2
1917 | 30/07/2025 10:10:36.059 | 97.512 | 77 | 100 | 71 | 53 | 27.702 | 9.569 | 7.005 | 134.704 | 29.221 | 28.234 | 28 | 603.258 | 26.011 | 26.787 | 1284.894 | 27.064 | 27.316 | 36.599 | 26.001 | 2.3 | 2.3 | 0.7 | 0 | 0.2
1918 | 30/07/2025 10:10:37.695 | 97.2 | 77 | 100 | 71 | 52 | 27.957 | 9.287 | 7.023 | 134.483 | 29.242 | 28.234 | 28.011 | 603.256 | 26.025 | 26.811 | 1289.983 | 27.064 | 27.287 | 36.469 | 24.001 | 2.3 | 1.3 | 0.7 | 0 | 0.2
1919 | 30/07/2025 10:10:39.329 | 97.056 | 77 | 100 | 72 | 52 | 30.725 | 9.573 | 7.034 | 134.51 | 29.254 | 28.247 | 28.009 | 603.401 | 26.027 | 26.791 | 1286.267 | 27.058 | 27.294 | 36.728 | 26.001 | 2.5 | 1.6 | 1.8 | 0.9 | 0.1
1920 | 30/07/2025 10:10:40.967 | 97.104 | 76 | 100 | 70 | 52 | 27.086 | 9.578 | 7.035 | 134.594 | 29.246 | 28.247 | 27.996 | 603.186 | 26.026 | 26.796 | 1287.244 | 27.028 | 27.307 | 36.73 | 26.001 | 2.5 | 1.9 | 1.8 | 0.9 | 0.1
1921 | 30/07/2025 10:10:42.604 | 96.864 | 76 | 100 | 71 | 52 | 30.475 | 9.371 | 7.032 | 134.713 | 29.255 | 28.256 | 27.991 | 603.302 | 26.018 | 26.792 | 1296.518 | 27.059 | 27.314 | 36.518 | 28.001 | 1.6 | 0.8 | 2.4 | 0.8 | 0.1
1922 | 30/07/2025 10:10:44.246 | 96.864 | 76 | 100 | 70 | 52 | 30.788 | 9.419 | 7.033 | 134.548 | 29.259 | 28.224 | 27.994 | 603.226 | 26.014 | 26.789 | 1301.471 | 27.085 | 27.303 | 36.482 | 28.001 | 1.6 | 0.8 | 2.4 | 0.8 | 0.1
1923 | 30/07/2025 10:10:45.883 | 97.296 | 76 | 100 | 71 | 52 | 27.17 | 9.431 | 7.032 | 134.446 | 29.266 | 28.24 | 28.002 | 603.288 | 26.026 | 26.799 | 1317.202 | 27.062 | 27.278 | 36.332 | 29.001 | 1.6 | 1.4 | 2.4 | 0.8 | 0.1
1924 | 30/07/2025 10:10:47.518 | 97.224 | 78 | 100 | 71 | 52 | 28.552 | 9.475 | 7.033 | 134.619 | 29.248 | 28.252 | 27.997 | 603.271 | 26.008 | 26.784 | 1317.142 | 27.048 | 27.316 | 36.643 | 29.001 | 2.4 | 1.6 | 0.1 | 1 | 0.2
1925 | 30/07/2025 10:10:49.157 | 97.656 | 78 | 100 | 70 | 52 | 30.868 | 9.502 | 7.073 | 134.702 | 29.257 | 28.24 | 27.973 | 603.127 | 25.994 | 26.795 | 1324.475 | 27.05 | 27.308 | 36.72 | 32.001 | 2.4 | 1.4 | 0.1 | 1 | 0.2
1926 | 30/07/2025 10:10:50.794 | 96.792 | 77 | 100 | 71 | 52 | 29.686 | 9.467 | 7.035 | 134.535 | 29.269 | 28.233 | 27.995 | 603.357 | 26.014 | 26.77 | 1313.525 | 27.06 | 27.3 | 36.7 | 25.001 | 3.3 | 1.9 | 1.2 | 0.2 | 0.2
1927 | 30/07/2025 10:10:52.428 | 96.552 | 75 | 100 | 70 | 53 | 30.673 | 9.29 | 7.033 | 134.644 | 29.252 | 28.224 | 27.991 | 603.215 | 26.004 | 26.782 | 1305.553 | 27.064 | 27.289 | 36.508 | 23.001 | 3.3 | 2.9 | 1.2 | 0.2 | 0.2
1928 | 30/07/2025 10:10:54.066 | 96.84 | 77 | 100 | 70 | 52 | 30.624 | 9.524 | 7.058 | 134.33 | 29.267 | 28.248 | 28.016 | 603.378 | 26.011 | 26.764 | 1297.309 | 27.056 | 27.283 | 36.457 | 23.001 | 3.3 | 2.9 | 1.2 | 0.2 | 0.2
1929 | 30/07/2025 10:10:55.702 | 97.008 | 76 | 100 | 70 | 52 | 26.973 | 9.429 | 7.072 | 134.561 | 29.262 | 28.257 | 27.989 | 603.298 | 25.993 | 26.765 | 1304.336 | 27.05 | 27.31 | 36.686 | 21.001 | 3.1 | 1.7 | 0.6 | 0.8 | 0.2
1930 | 30/07/2025 10:10:57.337 | 96.84 | 76 | 100 | 71 | 52 | 29.267 | 9.435 | 7.071 | 134.963 | 29.268 | 28.246 | 27.977 | 603.162 | 26.019 | 26.785 | 1304.429 | 27.062 | 27.3 | 36.632 | 27.001 | 3.1 | 2.6 | 0.6 | 0.8 | 0.2
1931 | 30/07/2025 10:10:58.977 | 97.176 | 76 | 100 | 70 | 52 | 30.943 | 9.287 | 7.069 | 134.589 | 29.252 | 28.228 | 28.006 | 603.375 | 26.025 | 26.766 | 1301.834 | 27.063 | 27.308 | 36.362 | 24.001 | 1.8 | 1.9 | 1.2 | 1 | 0.2
1932 | 30/07/2025 10:11:00.618 | 96.504 | 78 | 100 | 71 | 52 | 28.043 | 9.288 | 7.067 | 134.777 | 29.273 | 28.231 | 28.035 | 603.382 | 26.018 | 26.773 | 1297.014 | 27.064 | 27.285 | 36.579 | 29.001 | 1.8 | 3 | 1.2 | 1 | 0.2
1933 | 30/07/2025 10:11:02.254 | 96.504 | 77 | 100 | 70 | 52 | 30.735 | 9.406 | 7.073 | 134.524 | 29.25 | 28.258 | 28.007 | 603.357 | 26.018 | 26.796 | 1299.826 | 27.063 | 27.313 | 36.59 | 29.001 | 1.8 | 3 | 1.2 | 1 | 0.2
1934 | 30/07/2025 10:11:03.888 | 96.6 | 76 | 100 | 70 | 52 | 30.057 | 9.483 | 7.072 | 134.668 | 29.251 | 28.245 | 27.996 | 601.993 | 26.037 | 26.8 | 1304.262 | 27.025 | 27.31 | 36.776 | 25.001 | 2.6 | 2.4 | 1.9 | 0.6 | 0.2
1935 | 30/07/2025 10:11:05.523 | 97.296 | 78 | 100 | 71 | 52 | 26.793 | 9.351 | 7.072 | 134.647 | 29.244 | 28.242 | 27.999 | 602.121 | 26.027 | 26.792 | 1315.085 | 27.067 | 27.307 | 36.846 | 23.001 | 2.6 | 1.8 | 1.9 | 0.6 | 0.2
1936 | 30/07/2025 10:11:07.157 | 97.896 | 78 | 100 | 70 | 52 | 29.665 | 9.316 | 7.071 | 134.502 | 29.24 | 28.236 | 28.004 | 602.047 | 26.015 | 26.806 | 1308.935 | 27.082 | 27.292 | 36.696 | 25.001 | 1.8 | 2.1 | 0.3 | 0 | 0.2
1937 | 30/07/2025 10:11:08.793 | 97.968 | 79 | 100 | 71 | 51 | 27.294 | 9.437 | 7.069 | 134.598 | 29.236 | 28.247 | 28.014 | 602.371 | 26.021 | 26.792 | 1309.702 | 27.061 | 27.288 | 36.42 | 25.001 | 1.8 | 0.8 | 0.3 | 0 | 0.2
1938 | 30/07/2025 10:11:10.427 | 98.664 | 81 | 100 | 70 | 53 | 28.53 | 9.428 | 7.073 | 134.557 | 29.23 | 28.264 | 27.993 | 602.094 | 26.022 | 26.809 | 1325.271 | 27.056 | 27.312 | 36.662 | 28.001 | 3.2 | 1.3 | 0 | 0.8 | 0.1
1939 | 30/07/2025 10:11:12.062 | 98.976 | 79 | 100 | 70 | 52 | 30.841 | 9.556 | 7.071 | 133.319 | 29.257 | 28.246 | 27.99 | 602.02 | 26.046 | 26.79 | 1337.186 | 27.037 | 27.297 | 36.872 | 28.001 | 3.2 | 1.3 | 0 | 0.8 | 0.1
1940 | 30/07/2025 10:11:13.699 | 99.504 | 80 | 100 | 71 | 52 | 29.466 | 9.528 | 7.071 | 133.138 | 29.257 | 28.248 | 27.995 | 602.154 | 26.015 | 26.786 | 1336.945 | 27.082 | 27.311 | 36.69 | 29.001 | 3.2 | 1.5 | 0 | 0.8 | 0.1
1941 | 30/07/2025 10:11:15.333 | 99.096 | 79 | 100 | 70 | 52 | 26.849 | 9.436 | 7.072 | 133.087 | 29.245 | 28.232 | 28.003 | 602.108 | 26.023 | 26.789 | 1339.147 | 27.059 | 27.279 | 36.644 | 30.001 | 1.9 | 2.6 | 0.9 | 0.6 | 0.2
1942 | 30/07/2025 10:11:16.968 | 98.448 | 78 | 100 | 70 | 51 | 30.025 | 9.287 | 7.071 | 133.232 | 29.265 | 28.256 | 28.016 | 602.191 | 26.016 | 26.81 | 1327.144 | 27.043 | 27.304 | 36.622 | 27.001 | 1.9 | 1.2 | 0.9 | 0.6 | 0.2
1943 | 30/07/2025 10:11:18.602 | 98.352 | 79 | 100 | 70 | 52 | 26.855 | 9.331 | 7.073 | 134.536 | 29.272 | 28.248 | 27.999 | 601.923 | 26.025 | 26.807 | 1323.019 | 27.038 | 27.311 | 36.756 | 31.001 | 2 | 2.5 | 1.2 | 1.2 | 0.1
1944 | 30/07/2025 10:11:20.237 | 98.424 | 78 | 100 | 71 | 53 | 28.987 | 9.434 | 7.069 | 134.645 | 29.263 | 28.257 | 27.981 | 600.618 | 26.009 | 26.787 | 1303.336 | 27.046 | 27.312 | 36.634 | 31.001 | 2 | 2.5 | 1.2 | 1.2 | 0.1
1945 | 30/07/2025 10:11:21.876 | 97.824 | 77 | 100 | 71 | 54 | 30.903 | 9.579 | 7.069 | 134.541 | 29.262 | 28.226 | 27.982 | 602.078 | 26.014 | 26.809 | 1289.99 | 27.094 | 27.305 | 36.511 | 32.001 | 2 | 0.9 | 1.2 | 1.2 | 0.1
1946 | 30/07/2025 10:11:23.512 | 97.344 | 77 | 100 | 70 | 53 | 29.042 | 9.503 | 7.069 | 134.589 | 29.283 | 28.246 | 28.019 | 600.684 | 26.015 | 26.783 | 1294.922 | 27.068 | 27.278 | 36.352 | 27.001 | 2.1 | 2 | 0.7 | 0.5 | 0.1
1947 | 30/07/2025 10:11:25.145 | 97.104 | 77 | 100 | 70 | 52 | 27.101 | 9.433 | 7.071 | 134.576 | 29.251 | 28.26 | 27.999 | 600.632 | 25.999 | 26.778 | 1295.711 | 27.051 | 27.323 | 36.821 | 30.001 | 2.1 | 2.6 | 0.7 | 0.5 | 0.1
1948 | 30/07/2025 10:11:26.781 | 97.2 | 75 | 100 | 71 | 53 | 30.215 | 9.431 | 7.07 | 134.789 | 29.266 | 28.253 | 28.007 | 600.732 | 26.026 | 26.766 | 1290.038 | 27.03 | 27.316 | 36.561 | 25.001 | 2.2 | 1.3 | 0.3 | 0.6 | 0.1
1949 | 30/07/2025 10:11:28.416 | 96.72 | 77 | 100 | 71 | 52 | 26.839 | 9.433 | 7.07 | 134.632 | 29.263 | 28.253 | 27.978 | 600.554 | 26.01 | 26.762 | 1292.203 | 27.088 | 27.313 | 36.605 | 27.001 | 2.2 | 1.1 | 0.3 | 0.6 | 0.1
1950 | 30/07/2025 10:11:30.052 | 96.504 | 76 | 100 | 70 | 51 | 29.74 | 9.431 | 7.071 | 134.744 | 29.263 | 28.223 | 28.002 | 602.094 | 26.015 | 26.776 | 1293.406 | 27.057 | 27.302 | 36.638 | 27.001 | 2.2 | 1.1 | 0.3 | 0.6 | 0.1
1951 | 30/07/2025 10:11:31.686 | 96.84 | 77 | 100 | 70 | 53 | 31.008 | 9.438 | 7.07 | 134.511 | 29.248 | 28.246 | 28.005 | 602.132 | 26.009 | 26.764 | 1287.767 | 27.06 | 27.292 | 36.443 | 27.001 | 2.2 | 1.9 | 0.6 | 0 | 0.1
1952 | 30/07/2025 10:11:33.320 | 96.672 | 76 | 99 | 71 | 52 | 28.341 | 9.428 | 7.074 | 134.458 | 29.256 | 28.248 | 27.99 | 601.924 | 26.016 | 26.782 | 1284.893 | 27.056 | 27.316 | 36.841 | 28.001 | 2.2 | 1.5 | 0.6 | 0 | 0.1
1953 | 30/07/2025 10:11:34.956 | 96.768 | 76 | 100 | 70 | 52 | 27.492 | 9.453 | 7.032 | 134.717 | 29.25 | 28.251 | 27.984 | 601.614 | 26.041 | 26.785 | 1287.29 | 27.06 | 27.305 | 36.631 | 24.001 | 3.3 | 1.6 | 0.6 | 0.8 | 0.2
1954 | 30/07/2025 10:11:36.591 | 97.44 | 78 | 100 | 71 | 52 | 29.584 | 9.466 | 7.036 | 134.524 | 29.26 | 28.241 | 27.957 | 600.466 | 26.033 | 26.802 | 1287.082 | 27.076 | 27.303 | 36.56 | 29.001 | 3.3 | 2.1 | 0.6 | 0.8 | 0.2
1955 | 30/07/2025 10:11:38.228 | 97.176 | 77 | 100 | 71 | 53 | 26.807 | 9.23 | 7.031 | 134.822 | 29.252 | 28.235 | 28.02 | 600.818 | 26.025 | 26.794 | 1284.759 | 27.064 | 27.293 | 36.418 | 29.001 | 3.3 | 2.1 | 0.6 | 0.8 | 0.2
1956 | 30/07/2025 10:11:39.861 | 97.248 | 77 | 100 | 71 | 52 | 30.141 | 9.295 | 7.033 | 134.365 | 29.242 | 28.267 | 27.998 | 600.632 | 26.01 | 26.793 | 1282.731 | 27.069 | 27.297 | 36.558 | 24.001 | 2.2 | 1.2 | 0.4 | 0.5 | 0.2
1957 | 30/07/2025 10:11:41.496 | 96.912 | 77 | 100 | 71 | 52 | 31.003 | 9.464 | 7.033 | 134.78 | 29.236 | 28.245 | 27.988 | 600.716 | 26.023 | 26.812 | 1292.48 | 27.028 | 27.304 | 36.807 | 25.001 | 2.2 | 3.1 | 0.4 | 0.5 | 0.2
1958 | 30/07/2025 10:11:43.132 | 97.08 | 75 | 100 | 70 | 52 | 27.813 | 9.497 | 7.033 | 134.709 | 29.238 | 28.242 | 27.992 | 599.307 | 26.017 | 26.788 | 1287.727 | 27.07 | 27.298 | 36.6 | 24.001 | 3 | 3.4 | 0.6 | 0.9 | 0.2
1959 | 30/07/2025 10:11:44.767 | 96.576 | 77 | 100 | 70 | 52 | 30.925 | 9.466 | 7.033 | 134.801 | 29.244 | 28.226 | 27.981 | 599.168 | 26.027 | 26.799 | 1287.589 | 27.051 | 27.298 | 36.653 | 27.001 | 3 | 3.6 | 0.6 | 0.9 | 0.2
1960 | 30/07/2025 10:11:46.399 | 96.216 | 76 | 100 | 70 | 51 | 28.895 | 9.579 | 7.068 | 134.568 | 29.226 | 28.226 | 28.008 | 599.538 | 26.016 | 26.781 | 1279.535 | 27.063 | 27.287 | 36.464 | 29.001 | 3.1 | 2.3 | 0 | 1 | 0.3
1961 | 30/07/2025 10:11:48.035 | 96.432 | 76 | 100 | 70 | 52 | 27.074 | 9.551 | 7.074 | 134.554 | 29.249 | 28.257 | 28.001 | 599.238 | 26.021 | 26.804 | 1309.114 | 27.059 | 27.305 | 36.621 | 29.001 | 3.1 | 2.3 | 0 | 1 | 0.3
1962 | 30/07/2025 10:11:49.669 | 96.456 | 77 | 100 | 70 | 51 | 30.442 | 9.326 | 7.07 | 134.736 | 29.269 | 28.246 | 27.984 | 599.299 | 26.029 | 26.787 | 1267.448 | 27.043 | 27.295 | 38.48 | 34.001 | 3.1 | 1.2 | 0 | 1 | 0.3
1963 | 30/07/2025 10:11:51.305 | 96.816 | 77 | 100 | 71 | 52 | 30.794 | 9.507 | 7.071 | 134.671 | 29.263 | 28.249 | 27.97 | 599.309 | 26.025 | 26.786 | 1269.068 | 27.084 | 27.307 | 38.415 | 29.001 | 2.2 | 2.9 | 0.3 | 0 | 0.4
1964 | 30/07/2025 10:11:52.941 | 96.816 | 76 | 100 | 71 | 52 | 29.506 | 9.429 | 7.07 | 134.656 | 29.272 | 28.237 | 28.017 | 600.765 | 26.019 | 26.788 | 1272.213 | 27.065 | 27.299 | 38.335 | 21.001 | 2.2 | 1.9 | 0.3 | 0 | 0.4
1965 | 30/07/2025 10:11:54.578 | 96.864 | 77 | 100 | 70 | 52 | 30.979 | 9.568 | 7.032 | 134.476 | 29.264 | 28.259 | 28.006 | 600.71 | 26.007 | 26.793 | 1277.073 | 27.083 | 27.292 | 38.105 | 31.001 | 2.2 | 4 | 0.6 | 0.6 | 0.3
1966 | 30/07/2025 10:11:56.214 | 97.008 | 77 | 100 | 71 | 52 | 28.275 | 9.332 | 7.034 | 134.661 | 29.274 | 28.248 | 27.994 | 599.44 | 26.014 | 26.786 | 1290.464 | 27.033 | 27.303 | 36.747 | 31.001 | 2.2 | 4 | 0.6 | 0.6 | 0.3
1967 | 30/07/2025 10:11:57.850 | 97.08 | 76 | 100 | 71 | 50 | 27.493 | 9.432 | 7.07 | 134.611 | 29.261 | 28.249 | 27.987 | 599.404 | 25.994 | 26.784 | 1315.403 | 27.051 | 27.314 | 38.39 | 29.001 | 2.2 | 2 | 0.6 | 0.6 | 0.3
1968 | 30/07/2025 10:11:59.485 | 97.032 | 77 | 100 | 70 | 52 | 30.647 | 9.529 | 6.937 | 134.661 | 29.259 | 28.227 | 27.981 | 598.134 | 26.012 | 26.782 | 1319.569 | 27.067 | 27.307 | 38.422 | 29.001 | 3.4 | 3 | 0.6 | 0 | 0.2
1969 | 30/07/2025 10:12:01.119 | 97.128 | 76 | 100 | 70 | 52 | 30.61 | 9.438 | 6.933 | 134.646 | 29.27 | 28.24 | 28.016 | 599.475 | 26.013 | 26.771 | 1327.513 | 27.059 | 27.286 | 36.445 | 23.001 | 3.4 | 4.8 | 0.6 | 0 | 0.2
1970 | 30/07/2025 10:12:02.753 | 97.368 | 78 | 100 | 70 | 52 | 30.221 | 9.435 | 6.919 | 134.588 | 29.266 | 28.251 | 27.993 | 599.34 | 26.003 | 26.78 | 1324.407 | 27.06 | 27.287 | 36.557 | 26.001 | 3.4 | 1.9 | 0.6 | 0.5 | 0.2
1971 | 30/07/2025 10:12:04.390 | 97.32 | 78 | 100 | 70 | 52 | 31.003 | 9.501 | 6.91 | 134.638 | 29.261 | 28.252 | 28.01 | 599.399 | 26.008 | 26.763 | 1307.509 | 27.025 | 27.311 | 36.702 | 35.001 | 3.4 | 0.9 | 0.6 | 0.5 | 0.2
1972 | 30/07/2025 10:12:06.027 | 97.152 | 77 | 100 | 70 | 52 | 27.834 | 9.436 | 6.934 | 134.493 | 29.257 | 28.263 | 27.967 | 599.255 | 26.017 | 26.763 | 1307.557 | 27.093 | 27.312 | 36.841 | 35.001 | 3.4 | 0.9 | 0.6 | 0.5 | 0.2
1973 | 30/07/2025 10:12:07.663 | 97.464 | 78 | 100 | 70 | 52 | 28.076 | 9.465 | 6.934 | 134.712 | 29.35 | 28.233 | 28.002 | 599.399 | 26.032 | 26.776 | 1306.745 | 27.071 | 27.292 | 36.608 | 31.001 | 3.6 | 1.5 | 0.6 | 0 | 0.2
1974 | 30/07/2025 10:12:09.297 | 97.032 | 77 | 100 | 70 | 52 | 30.773 | 9.439 | 6.933 | 134.539 | 29.401 | 28.247 | 28.01 | 598.037 | 26.023 | 26.79 | 1300.014 | 27.064 | 27.287 | 36.437 | 21.001 | 3.6 | 2.1 | 0.6 | 0 | 0.2
1975 | 30/07/2025 10:12:10.933 | 97.296 | 77 | 100 | 71 | 51 | 27.091 | 9.43 | 6.941 | 134.542 | 29.409 | 28.25 | 27.996 | 599.313 | 26.037 | 26.781 | 1296.836 | 27.047 | 27.299 | 36.596 | 23.001 | 3.8 | 2 | 0.9 | 0.8 | 0.2
1976 | 30/07/2025 10:12:12.571 | 97.272 | 76 | 100 | 70 | 52 | 30.506 | 9.35 | 6.952 | 134.852 | 29.373 | 28.25 | 27.993 | 599.352 | 26.013 | 26.79 | 1295.627 | 27.042 | 27.323 | 36.61 | 26.001 | 3.8 | 1.8 | 0.9 | 0.8 | 0.2
1977 | 30/07/2025 10:12:14.206 | 97.416 | 76 | 100 | 70 | 52 | 30.915 | 9.577 | 6.954 | 134.767 | 29.388 | 28.237 | 27.961 | 598.984 | 26.026 | 26.806 | 1296.986 | 27.067 | 27.306 | 36.785 | 26.001 | 3.8 | 1.8 | 0.9 | 0.8 | 0.2
1978 | 30/07/2025 10:12:15.842 | 97.728 | 78 | 100 | 70 | 52 | 27.35 | 9.433 | 6.984 | 134.71 | 29.383 | 28.236 | 28.027 | 598.253 | 26.016 | 26.799 | 1306.876 | 27.056 | 27.298 | 36.471 | 26.001 | 4.2 | 1.4 | 2.2 | 0 | 0.2
1979 | 30/07/2025 10:12:17.480 | 97.608 | 78 | 100 | 70 | 54 | 28.68 | 9.438 | 7.005 | 134.354 | 29.382 | 28.26 | 28.003 | 598.157 | 26.019 | 26.8 | 1299.255 | 27.071 | 27.291 | 36.49 | 24.001 | 4.2 | 2.6 | 2.2 | 0 | 0.2
1980 | 30/07/2025 10:12:19.117 | 97.32 | 78 | 100 | 71 | 51 | 30.848 | 9.503 | 7.006 | 134.713 | 29.4 | 28.252 | 27.998 | 598.049 | 26.03 | 26.8 | 1312.367 | 27.024 | 27.305 | 36.811 | 26.001 | 2.1 | 1.9 | 1.2 | 0.5 | 0.1
1981 | 30/07/2025 10:12:20.751 | 96.48 | 78 | 100 | 71 | 52 | 27.505 | 9.436 | 6.989 | 134.547 | 29.383 | 28.246 | 27.971 | 598.002 | 26.013 | 26.805 | 1317.197 | 27.056 | 27.31 | 36.779 | 28.001 | 2.1 | 1.1 | 1.2 | 0.5 | 0.1
1982 | 30/07/2025 10:12:22.386 | 96.384 | 77 | 100 | 70 | 52 | 30.726 | 9.287 | 6.933 | 134.746 | 29.414 | 28.231 | 27.996 | 598.084 | 26.046 | 26.788 | 1311.963 | 27.059 | 27.302 | 36.651 | 28.001 | 3.6 | 1.4 | 0.6 | 0.5 | 0.1
1983 | 30/07/2025 10:12:24.022 | 95.928 | 74 | 100 | 70 | 53 | 30.542 | 9.438 | 6.937 | 134.683 | 29.406 | 28.375 | 28.021 | 598.175 | 26.019 | 26.801 | 1316.668 | 27.079 | 27.3 | 36.351 | 28.001 | 3.6 | 1.4 | 0.6 | 0.5 | 0.1
1984 | 30/07/2025 10:12:25.656 | 95.184 | 74 | 100 | 69 | 53 | 26.983 | 9.431 | 6.954 | 134.357 | 29.42 | 28.247 | 28.002 | 598.081 | 26.007 | 26.805 | 1305.896 | 27.053 | 27.31 | 36.694 | 27.001 | 3.6 | 3 | 0.6 | 0.5 | 0.1
1985 | 30/07/2025 10:12:27.291 | 95.208 | 75 | 100 | 70 | 52 | 29.014 | 9.282 | 7.003 | 134.626 | 29.408 | 28.247 | 28 | 598.24 | 26.014 | 26.789 | 1297.741 | 27.021 | 27.315 | 36.685 | 22.001 | 3.4 | 2.1 | 1.2 | 0.5 | 0.2
1986 | 30/07/2025 10:12:28.934 | 95.472 | 76 | 100 | 71 | 52 | 30.967 | 9.734 | 7.005 | 134.661 | 29.42 | 28.257 | 27.969 | 597.999 | 26.016 | 26.788 | 1304.351 | 27.084 | 27.312 | 36.635 | 26.001 | 3.4 | 1.7 | 1.2 | 0.5 | 0.2
1987 | 30/07/2025 10:12:30.568 | 95.208 | 76 | 100 | 70 | 52 | 27.899 | 9.503 | 7.003 | 134.564 | 29.418 | 28.235 | 28.001 | 598.188 | 26.001 | 26.784 | 1304.643 | 27.069 | 27.301 | 36.556 | 28.001 | 2.9 | 1.6 | 0.6 | 0.1 | 0.1
1988 | 30/07/2025 10:12:32.205 | 95.28 | 75 | 100 | 71 | 52 | 30.792 | 9.451 | 7.004 | 134.515 | 29.402 | 28.255 | 27.992 | 598.105 | 26.007 | 26.792 | 1308.343 | 27.086 | 27.282 | 36.507 | 28.001 | 2.9 | 1.6 | 0.6 | 0.1 | 0.1
1989 | 30/07/2025 10:12:33.840 | 95.712 | 75 | 100 | 71 | 53 | 30.179 | 9.285 | 7.006 | 134.644 | 29.41 | 28.249 | 28 | 598.192 | 26.025 | 26.775 | 1312.509 | 27.045 | 27.304 | 36.931 | 26.001 | 2.9 | 1.3 | 0.6 | 0.1 | 0.1
1990 | 30/07/2025 10:12:35.476 | 96.168 | 75 | 100 | 71 | 52 | 26.88 | 9.287 | 7.032 | 134.577 | 29.411 | 28.255 | 27.987 | 598.141 | 26.002 | 26.763 | 1315.124 | 27.059 | 27.316 | 36.737 | 33.001 | 2.2 | 2.4 | 0.3 | 0.5 | 0.1
1991 | 30/07/2025 10:12:37.111 | 96.048 | 76 | 100 | 70 | 51 | 30.954 | 9.495 | 7.035 | 134.676 | 29.404 | 28.227 | 27.973 | 598.14 | 26.005 | 26.773 | 1309.435 | 27.072 | 27.301 | 36.809 | 27.001 | 2.2 | 2.7 | 0.3 | 0.5 | 0.1
1992 | 30/07/2025 10:12:38.747 | 96.048 | 75 | 100 | 70 | 52 | 27.251 | 9.581 | 7.03 | 134.647 | 29.403 | 28.226 | 28.007 | 598.173 | 26.005 | 26.765 | 1309.015 | 27.077 | 27.312 | 36.496 | 30.001 | 2.2 | 1.3 | 0.6 | 0 | 0.1
1993 | 30/07/2025 10:12:40.381 | 96.528 | 76 | 100 | 70 | 52 | 28.62 | 9.434 | 7.071 | 134.685 | 29.397 | 28.281 | 28.003 | 598.168 | 26.014 | 26.777 | 1308.992 | 27.059 | 27.287 | 36.412 | 27.001 | 2.2 | 1.9 | 0.6 | 0 | 0.1
1994 | 30/07/2025 10:12:42.016 | 96.312 | 76 | 100 | 69 | 53 | 30.868 | 9.368 | 7.07 | 134.701 | 29.394 | 28.26 | 28 | 598.289 | 26.004 | 26.76 | 1311.418 | 27.032 | 27.305 | 36.668 | 27.001 | 2.2 | 1.9 | 0.6 | 0 | 0.1
1995 | 30/07/2025 10:12:43.650 | 95.88 | 74 | 100 | 69 | 52 | 29.664 | 9.289 | 7.072 | 134.586 | 29.395 | 28.257 | 27.969 | 598.012 | 26.019 | 26.794 | 1312.353 | 27.075 | 27.314 | 36.623 | 24.001 | 3.6 | 2 | 0.9 | 0.9 | 0.1
1996 | 30/07/2025 10:12:45.285 | 95.904 | 75 | 100 | 71 | 52 | 26.897 | 9.297 | 7.069 | 134.735 | 29.401 | 28.376 | 27.995 | 598.143 | 26.042 | 26.799 | 1307.299 | 27.059 | 27.293 | 36.735 | 29.001 | 3.6 | 1.8 | 0.9 | 0.9 | 0.1
1997 | 30/07/2025 10:12:46.919 | 95.76 | 76 | 99 | 71 | 52 | 30.221 | 9.523 | 7.069 | 134.568 | 29.393 | 28.259 | 28.005 | 598.047 | 26.033 | 26.798 | 1306.952 | 27.065 | 27.296 | 36.434 | 30.001 | 3.1 | 2.8 | 1.5 | 0.2 | 0.1
1998 | 30/07/2025 10:12:48.557 | 96.024 | 77 | 100 | 70 | 52 | 26.963 | 9.574 | 7.069 | 134.467 | 29.407 | 28.284 | 27.999 | 598.166 | 26.034 | 26.794 | 1302.42 | 27.046 | 27.299 | 37.553 | 29.001 | 3.1 | 2.2 | 1.5 | 0.2 | 0.1
1999 | 30/07/2025 10:12:50.192 | 95.592 | 74 | 100 | 71 | 53 | 29.29 | 9.578 | 7.069 | 134.69 | 29.395 | 28.371 | 28.005 | 598.148 | 26.018 | 26.795 | 1297.706 | 27.043 | 27.328 | 36.854 | 29.001 | 3.1 | 2.2 | 1.5 | 0.2 | 0.1
2000 | 30/07/2025 10:12:51.827 | 95.52 | 75 | 100 | 70 | 52 | 30.999 | 9.49 | 7.073 | 134.666 | 29.384 | 28.387 | 27.945 | 598.018 | 26.019 | 26.789 | 1290.061 | 27.072 | 27.296 | 36.733 | 29.001 | 2.1 | 1.7 | 2.4 | 0.5 | 0.1
2001 | 30/07/2025 10:12:53.467 | 95.76 | 74 | 100 | 70 | 52 | 29.046 | 9.574 | 7.071 | 134.855 | 29.388 | 28.301 | 28.023 | 598.365 | 26.023 | 26.783 | 1288.557 | 27.057 | 27.296 | 36.371 | 29.001 | 2.1 | 1.2 | 2.4 | 0.5 | 0.1
2002 | 30/07/2025 10:12:55.102 | 95.784 | 76 | 100 | 70 | 53 | 27.122 | 9.286 | 7.071 | 134.377 | 29.401 | 28.416 | 28.016 | 598.077 | 26.014 | 26.802 | 1287.434 | 27.081 | 27.296 | 36.455 | 25.001 | 1.5 | 1.7 | 1.9 | 0.5 | 0.1
2003 | 30/07/2025 10:12:56.739 | 96.192 | 76 | 100 | 70 | 52 | 30.171 | 9.284 | 7.072 | 134.468 | 29.385 | 28.397 | 28.008 | 598.122 | 26.015 | 26.79 | 1292.13 | 27.053 | 27.308 | 36.554 | 21.001 | 1.5 | 2.1 | 1.9 | 0.5 | 0.1
2004 | 30/07/2025 10:12:58.373 | 96.36 | 77 | 100 | 71 | 52 | 26.872 | 9.307 | 7.071 | 134.767 | 29.398 | 28.396 | 27.976 | 598.003 | 26.021 | 26.805 | 1287.147 | 27.05 | 27.326 | 36.595 | 25.001 | 2.1 | 2.1 | 0.6 | 1.1 | 0.2
2005 | 30/07/2025 10:13:00.008 | 96.312 | 76 | 100 | 71 | 52 | 29.644 | 9.566 | 7.072 | 134.801 | 29.42 | 28.24 | 27.975 | 598.031 | 26.027 | 26.797 | 1275.361 | 27.067 | 27.305 | 36.62 | 25.001 | 2.1 | 2.1 | 0.6 | 1.1 | 0.2
2006 | 30/07/2025 10:13:01.642 | 96.48 | 76 | 100 | 70 | 52 | 31.021 | 9.491 | 7.056 | 134.672 | 29.408 | 28.262 | 28.002 | 598.174 | 26.012 | 26.79 | 1272.05 | 27.068 | 27.297 | 36.416 | 24.001 | 2.1 | 2.3 | 0.6 | 1.1 | 0.2
2007 | 30/07/2025 10:13:03.514 | 97.032 | 78 | 100 | 71 | 52 | 28.517 | 9.567 | 7.036 | 133.38 | 29.416 | 28.401 | 27.988 | 598.062 | 26.006 | 26.78 | 1277.337 | 27.054 | 27.278 | 36.705 | 24.001 | 1.4 | 1.7 | 0.6 | 0.5 | 0.3
2008 | 30/07/2025 10:13:05.151 | 97.536 | 78 | 100 | 71 | 52 | 27.465 | 9.285 | 7.07 | 133.351 | 29.415 | 28.402 | 28.015 | 598.311 | 26.01 | 26.771 | 1272.16 | 27.031 | 27.306 | 36.643 | 28.001 | 1.4 | 2.1 | 0.6 | 0.5 | 0.3
2009 | 30/07/2025 10:13:06.788 | 97.392 | 77 | 100 | 70 | 52 | 30.697 | 9.516 | 7.052 | 132.968 | 29.399 | 28.399 | 27.968 | 597.974 | 25.991 | 26.781 | 1279.301 | 27.085 | 27.305 | 36.601 | 26.001 | 2.4 | 1.9 | 0.7 | 0.2 | 0.2
2010 | 30/07/2025 10:13:08.424 | 97.56 | 76 | 100 | 70 | 53 | 26.873 | 9.435 | 7.033 | 133.193 | 29.413 | 28.385 | 28.012 | 598.045 | 25.996 | 26.776 | 1286.632 | 27.066 | 27.31 | 36.489 | 30.001 | 2.4 | 2.1 | 0.7 | 0.2 | 0.2
2011 | 30/07/2025 10:13:10.057 | 97.824 | 79 | 100 | 70 | 51 | 30.181 | 9.505 | 7.034 | 132.983 | 29.405 | 28.345 | 28.002 | 598.176 | 25.999 | 26.778 | 1286.977 | 27.072 | 27.29 | 36.383 | 30.001 | 2.4 | 2.1 | 0.7 | 0.2 | 0.2
2012 | 30/07/2025 10:13:11.693 | 97.824 | 77 | 100 | 71 | 52 | 31.025 | 9.463 | 7.034 | 133.331 | 29.416 | 28.4 | 28.007 | 598.218 | 26.023 | 26.775 | 1280.83 | 27.044 | 27.305 | 36.824 | 27.001 | 2.9 | 2.1 | 0.7 | 0.5 | 0.3
2013 | 30/07/2025 10:13:13.329 | 98.16 | 78 | 100 | 70 | 52 | 27.823 | 9.284 | 7.033 | 133.165 | 29.406 | 28.394 | 27.995 | 598.101 | 26.006 | 26.771 | 1277.79 | 27.062 | 27.32 | 36.454 | 29.001 | 2.9 | 1.2 | 0.7 | 0.5 | 0.3
2014 | 30/07/2025 10:13:14.966 | 98.112 | 78 | 100 | 71 | 52 | 28.046 | 9.58 | 7.036 | 133.207 | 29.397 | 28.385 | 27.963 | 598.071 | 26.033 | 26.778 | 1287.403 | 27.083 | 27.306 | 36.774 | 23.001 | 2.9 | 2.1 | 0.6 | 0.8 | 0.2
2015 | 30/07/2025 10:13:16.603 | 98.472 | 77 | 100 | 71 | 53 | 30.82 | 9.351 | 7.031 | 133.271 | 29.404 | 28.24 | 28.02 | 598.301 | 26.015 | 26.776 | 1282.553 | 27.061 | 27.287 | 36.428 | 29.001 | 2.9 | 1.6 | 0.6 | 0.8 | 0.2
2016 | 30/07/2025 10:13:18.242 | 98.616 | 78 | 100 | 69 | 52 | 27.11 | 9.288 | 7.054 | 132.982 | 29.411 | 28.36 | 28.009 | 598.2 | 26.03 | 26.798 | 1278.005 | 27.064 | 27.281 | 36.378 | 29.001 | 2.9 | 1.6 | 0.6 | 0.8 | 0.2
2017 | 30/07/2025 10:13:19.879 | 98.592 | 77 | 100 | 69 | 52 | 30.495 | 9.324 | 7.071 | 133.177 | 29.393 | 28.258 | 28.004 | 598.237 | 26.03 | 26.801 | 1274.485 | 27.028 | 27.313 | 36.704 | 23.001 | 5.3 | 1.4 | 0.6 | 0.8 | 0.2
2018 | 30/07/2025 10:13:21.510 | 98.424 | 77 | 100 | 71 | 51 | 30.921 | 9.289 | 7.073 | 133.096 | 29.384 | 28.394 | 27.964 | 598.043 | 26.015 | 26.805 | 1279.253 | 27.068 | 27.3 | 36.543 | 26.001 | 5.3 | 1 | 0.6 | 0.8 | 0.2
2019 | 30/07/2025 10:13:23.146 | 98.688 | 80 | 100 | 71 | 53 | 27.415 | 9.434 | 7.068 | 133.166 | 29.386 | 28.374 | 27.988 | 598.138 | 26.033 | 26.782 | 1277.163 | 27.064 | 27.286 | 36.637 | 26.001 | 3.9 | 1.7 | 0.9 | 0.9 | 0.2
2020 | 30/07/2025 10:13:24.781 | 98.688 | 78 | 100 | 70 | 52 | 28.688 | 9.5 | 7.07 | 133.011 | 29.38 | 28.399 | 28.022 | 598.126 | 26.018 | 26.8 | 1282.328 | 27.07 | 27.302 | 36.369 | 25.001 | 3.9 | 1.6 | 0.9 | 0.9 | 0.2
2021 | 30/07/2025 10:13:26.417 | 99.096 | 79 | 100 | 70 | 52 | 28.49 | 9.432 | 7.071 | 133.103 | 29.393 | 28.402 | 28.021 | 598.306 | 26.024 | 26.799 | 1282.677 | 27.055 | 27.291 | 36.518 | 27.001 | 2.3 | 1.3 | 0 | 0.1 | 0.2
2022 | 30/07/2025 10:13:28.051 | 98.688 | 78 | 100 | 71 | 51 | 27.586 | 9.282 | 7.07 | 133.232 | 29.38 | 28.255 | 28.002 | 598.155 | 26.014 | 26.791 | 1282.067 | 27.046 | 27.327 | 36.793 | 27.001 | 2.3 | 1.3 | 0 | 0.1 | 0.2
2023 | 30/07/2025 10:13:29.687 | 98.04 | 79 | 100 | 70 | 52 | 30.715 | 9.581 | 7.071 | 134.786 | 29.394 | 28.244 | 27.961 | 598.044 | 26.021 | 26.8 | 1279.532 | 27.066 | 27.3 | 36.763 | 30.001 | 2.3 | 3 | 0 | 0.1 | 0.2
2024 | 30/07/2025 10:13:31.322 | 98.352 | 78 | 100 | 70 | 52 | 30.611 | 9.664 | 7.077 | 134.704 | 29.402 | 28.223 | 28.005 | 598.245 | 26.013 | 26.794 | 1276.554 | 27.071 | 27.296 | 36.479 | 30.001 | 2.7 | 2.9 | 0.6 | 0.9 | 0.2
2025 | 30/07/2025 10:13:32.959 | 98.16 | 77 | 100 | 70 | 52 | 27.041 | 9.459 | 7.123 | 134.402 | 29.408 | 28.414 | 27.996 | 598.152 | 26.018 | 26.791 | 1267.361 | 27.082 | 27.279 | 36.217 | 25.001 | 2.7 | 2.6 | 0.6 | 0.9 | 0.2
2026 | 30/07/2025 10:13:34.595 | 98.328 | 77 | 100 | 70 | 52 | 31.02 | 9.517 | 7.103 | 134.45 | 29.404 | 28.399 | 27.993 | 598.148 | 26.009 | 26.776 | 1270.169 | 27.05 | 27.294 | 36.626 | 26.001 | 3.1 | 2 | 2.7 | 1 | 0.3
2027 | 30/07/2025 10:13:36.231 | 97.896 | 77 | 100 | 70 | 53 | 27.972 | 9.205 | 7.072 | 134.828 | 29.408 | 28.391 | 27.989 | 598.128 | 26.013 | 26.8 | 1292.421 | 27.039 | 27.317 | 36.605 | 26.001 | 3.1 | 2 | 2.7 | 1 | 0.3
2028 | 30/07/2025 10:13:37.867 | 98.112 | 77 | 100 | 70 | 52 | 27.968 | 9.404 | 7.071 | 134.69 | 29.43 | 28.386 | 27.987 | 597.95 | 26.015 | 26.782 | 1300.039 | 27.066 | 27.294 | 36.595 | 22.001 | 3.1 | 0.7 | 2.7 | 1 | 0.3
2029 | 30/07/2025 10:13:39.508 | 97.68 | 77 | 100 | 70 | 52 | 30.826 | 9.292 | 7.068 | 134.555 | 29.413 | 28.377 | 28.012 | 598.134 | 26.001 | 26.777 | 1281.975 | 27.071 | 27.299 | 36.462 | 28.001 | 3.9 | 1.4 | 0.6 | 0 | 0.3
2030 | 30/07/2025 10:13:41.142 | 97.848 | 79 | 100 | 70 | 52 | 30.278 | 9.289 | 7.073 | 134.517 | 29.409 | 28.398 | 27.993 | 598.172 | 25.997 | 26.775 | 1272.758 | 27.058 | 27.287 | 36.453 | 25.001 | 3.9 | 1.6 | 0.6 | 0 | 0.3
2031 | 30/07/2025 10:13:42.775 | 97.08 | 76 | 100 | 71 | 52 | 26.87 | 9.386 | 7.033 | 134.713 | 29.411 | 28.403 | 28.013 | 598.181 | 26.02 | 26.77 | 1265.218 | 27.035 | 27.318 | 36.724 | 26.001 | 1.8 | 1.4 | 1.1 | 1.1 | 0.3
2032 | 30/07/2025 10:13:44.410 | 97.512 | 77 | 100 | 70 | 52 | 30.929 | 9.283 | 7.033 | 134.918 | 29.418 | 28.396 | 27.984 | 598.013 | 26.02 | 26.786 | 1265.306 | 27.046 | 27.307 | 36.787 | 25.001 | 1.8 | 0.6 | 1.1 | 1.1 | 0.3
2033 | 30/07/2025 10:13:46.047 | 97.68 | 77 | 100 | 71 | 52 | 27.394 | 9.433 | 7.033 | 134.675 | 29.409 | 28.382 | 27.99 | 598.761 | 26.016 | 26.768 | 1270.571 | 27.076 | 27.299 | 36.739 | 25.001 | 1.8 | 0.6 | 1.1 | 1.1 | 0.3
2034 | 30/07/2025 10:13:47.685 | 96.912 | 77 | 100 | 70 | 52 | 28.538 | 9.436 | 7.032 | 134.416 | 29.409 | 28.39 | 28.005 | 599.335 | 26.016 | 26.767 | 1277.278 | 27.083 | 27.279 | 36.585 | 23.001 | 1.4 | 2 | 0.6 | 0.7 | 0.3
2035 | 30/07/2025 10:13:49.321 | 97.488 | 78 | 100 | 70 | 52 | 30.916 | 9.35 | 7.033 | 134.686 | 29.413 | 28.4 | 28.006 | 600.735 | 26.041 | 26.766 | 1285.393 | 27.055 | 27.304 | 36.638 | 25.001 | 1.4 | 2.2 | 0.6 | 0.7 | 0.3
2036 | 30/07/2025 10:13:50.955 | 97.776 | 77 | 100 | 71 | 52 | 29.631 | 9.36 | 7.07 | 134.564 | 29.401 | 28.397 | 27.987 | 600.629 | 26.025 | 26.786 | 1302.31 | 27.049 | 27.311 | 36.732 | 26.001 | 2.4 | 1.7 | 0.6 | 0.6 | 0.2
2037 | 30/07/2025 10:13:52.590 | 97.872 | 77 | 100 | 70 | 53 | 30.699 | 9.295 | 7.072 | 134.836 | 29.402 | 28.392 | 27.971 | 600.671 | 26.024 | 26.771 | 1299.028 | 27.057 | 27.296 | 36.734 | 24.001 | 2.4 | 1.2 | 0.6 | 0.6 | 0.2
2038 | 30/07/2025 10:13:54.224 | 98.064 | 78 | 100 | 71 | 52 | 30.672 | 9.484 | 7.071 | 134.582 | 29.38 | 28.381 | 28.008 | 600.591 | 26.024 | 26.795 | 1295.525 | 27.085 | 27.314 | 36.655 | 24.001 | 2.4 | 1.2 | 0.6 | 0.6 | 0.2
2039 | 30/07/2025 10:13:55.859 | 97.896 | 78 | 100 | 71 | 52 | 27.029 | 9.285 | 7.064 | 134.541 | 29.381 | 28.391 | 28.002 | 600.72 | 26.041 | 26.794 | 1293.777 | 27.051 | 27.27 | 36.5 | 23.001 | 3.4 | 1.8 | 0.7 | 0.5 | 0.2
2040 | 30/07/2025 10:13:57.493 | 98.064 | 77 | 100 | 70 | 53 | 29.192 | 9.386 | 7.034 | 134.658 | 29.373 | 28.406 | 28.014 | 600.689 | 26.016 | 26.805 | 1298.48 | 27.04 | 27.312 | 36.553 | 26.001 | 3.4 | 1.2 | 0.7 | 0.5 | 0.2
2041 | 30/07/2025 10:13:59.125 | 98.184 | 80 | 100 | 70 | 52 | 30.983 | 9.434 | 7.072 | 134.773 | 29.373 | 28.389 | 27.965 | 600.427 | 26.029 | 26.806 | 1300.711 | 27.068 | 27.301 | 36.605 | 27.001 | 1.8 | 0.4 | 0.7 | 0.5 | 0.3
2042 | 30/07/2025 10:14:00.760 | 97.728 | 78 | 100 | 70 | 52 | 28.065 | 9.431 | 7.069 | 134.518 | 29.375 | 28.389 | 27.983 | 600.518 | 26.009 | 26.781 | 1297.441 | 27.073 | 27.307 | 36.63 | 25.001 | 1.8 | 0.6 | 0.7 | 0.5 | 0.3
2043 | 30/07/2025 10:14:02.394 | 97.632 | 78 | 100 | 71 | 53 | 30.827 | 9.441 | 7.071 | 134.539 | 29.403 | 28.38 | 28.006 | 600.579 | 26.022 | 26.803 | 1308.106 | 27.06 | 27.3 | 36.527 | 25.001 | 3.3 | 1.4 | 0.5 | 0.2 | 0.3
2044 | 30/07/2025 10:14:04.028 | 97.872 | 77 | 100 | 70 | 53 | 30.163 | 9.483 | 7.07 | 134.386 | 29.392 | 28.401 | 28.013 | 600.733 | 26.018 | 26.783 | 1314.347 | 27.059 | 27.287 | 36.372 | 25.001 | 3.3 | 1.4 | 0.5 | 0.2 | 0.3
2045 | 30/07/2025 10:14:05.660 | 97.992 | 77 | 100 | 70 | 50 | 26.848 | 9.221 | 7.072 | 134.706 | 29.402 | 28.406 | 27.995 | 600.632 | 26.019 | 26.792 | 1309.313 | 27.058 | 27.31 | 36.62 | 24.001 | 3.3 | 2.8 | 0.5 | 0.2 | 0.3
2046 | 30/07/2025 10:14:07.292 | 97.272 | 77 | 100 | 70 | 52 | 29.639 | 9.433 | 7.071 | 134.666 | 29.416 | 28.386 | 27.959 | 600.604 | 26.015 | 26.801 | 1312.717 | 27.059 | 27.303 | 36.682 | 33.001 | 1.7 | 2.2 | 0.8 | 0.8 | 0.3
2047 | 30/07/2025 10:14:08.924 | 96.864 | 76 | 100 | 70 | 52 | 31.038 | 9.576 | 7.068 | 134.567 | 29.406 | 28.374 | 27.997 | 600.735 | 26.023 | 26.791 | 1320.054 | 27.065 | 27.303 | 36.732 | 26.001 | 1.7 | 3 | 0.8 | 0.8 | 0.3
2048 | 30/07/2025 10:14:10.560 | 96.984 | 77 | 100 | 70 | 52 | 28.585 | 9.58 | 7.07 | 134.647 | 29.429 | 28.38 | 28.012 | 600.721 | 26.024 | 26.794 | 1324.914 | 27.065 | 27.275 | 36.776 | 27.001 | 4.4 | 1.6 | 1.2 | 0 | 0.3
2049 | 30/07/2025 10:14:12.194 | 97.104 | 76 | 100 | 70 | 51 | 30.969 | 9.441 | 7.063 | 134.711 | 29.42 | 28.412 | 28.008 | 600.724 | 25.989 | 26.781 | 1332.218 | 27.054 | 27.315 | 36.744 | 27.001 | 4.4 | 1.6 | 1.2 | 0 | 0.3
2050 | 30/07/2025 10:14:13.828 | 96.576 | 77 | 100 | 70 | 53 | 29.788 | 9.291 | 7.007 | 134.642 | 29.408 | 28.397 | 27.983 | 600.501 | 26.004 | 26.801 | 1329.395 | 27.049 | 27.315 | 36.787 | 31.001 | 4.4 | 2.6 | 1.2 | 0 | 0.3
2051 | 30/07/2025 10:14:15.461 | 96.936 | 76 | 100 | 69 | 52 | 26.948 | 9.432 | 7.005 | 134.754 | 29.411 | 28.392 | 27.991 | 600.616 | 26.017 | 26.772 | 1315.128 | 27.068 | 27.304 | 36.607 | 28.001 | 2.3 | 1.8 | 1.5 | 0.8 | 0.2
2052 | 30/07/2025 10:14:17.093 | 97.176 | 77 | 100 | 69 | 52 | 30.265 | 9.433 | 7.003 | 134.539 | 29.406 | 28.376 | 28.004 | 600.693 | 26.006 | 26.773 | 1307.018 | 27.077 | 27.297 | 36.614 | 28.001 | 2.3 | 1.7 | 1.5 | 0.8 | 0.2
2053 | 30/07/2025 10:14:18.726 | 96.048 | 76 | 100 | 70 | 53 | 27.145 | 9.292 | 7.028 | 134.52 | 29.414 | 28.393 | 28.011 | 602.355 | 26.006 | 26.767 | 1314.115 | 27.065 | 27.289 | 36.475 | 27.001 | 2.1 | 1.3 | 0.6 | 0.7 | 0.3
2054 | 30/07/2025 10:14:20.361 | 95.568 | 75 | 100 | 70 | 52 | 29.22 | 9.341 | 7.035 | 134.471 | 29.402 | 28.409 | 27.999 | 602.052 | 25.997 | 26.77 | 1312.177 | 27.06 | 27.306 | 36.82 | 29.001 | 2.1 | 1.4 | 0.6 | 0.7 | 0.3
2055 | 30/07/2025 10:14:21.996 | 95.472 | 76 | 100 | 71 | 52 | 31.063 | 9.433 | 7.034 | 134.956 | 29.408 | 28.393 | 27.968 | 602.137 | 26.019 | 26.771 | 1318.044 | 27.035 | 27.296 | 36.867 | 29.001 | 2.1 | 1.4 | 0.6 | 0.7 | 0.3
2056 | 30/07/2025 10:14:23.629 | 95.544 | 76 | 100 | 70 | 52 | 29.114 | 9.36 | 7.033 | 134.597 | 29.399 | 28.382 | 27.98 | 601.982 | 26.02 | 26.778 | 1321.232 | 27.076 | 27.304 | 36.594 | 26.001 | 0.8 | 2.9 | 1.5 | 0.6 | 0.3
2057 | 30/07/2025 10:14:25.265 | 95.568 | 77 | 100 | 70 | 52 | 27.105 | 9.324 | 7.034 | 134.522 | 29.394 | 28.384 | 28.012 | 602.148 | 26.032 | 26.91 | 1306.787 | 27.067 | 27.287 | 36.455 | 25.001 | 0.8 | 2 | 1.5 | 0.6 | 0.3
2058 | 30/07/2025 10:14:26.902 | 95.16 | 75 | 100 | 70 | 52 | 30.482 | 9.433 | 7.033 | 134.683 | 29.396 | 28.408 | 28.012 | 602.238 | 26.032 | 26.955 | 1297.412 | 27.056 | 27.301 | 36.525 | 24.001 | 3.4 | 2.4 | 1.3 | 0.6 | 0.3
2059 | 30/07/2025 10:14:28.537 | 95.352 | 76 | 100 | 70 | 52 | 26.865 | 9.506 | 7.034 | 134.681 | 29.394 | 28.394 | 27.984 | 601.88 | 26.025 | 26.939 | 1301.415 | 27.03 | 27.294 | 36.793 | 26.001 | 3.4 | 1.7 | 1.3 | 0.6 | 0.3
2060 | 30/07/2025 10:14:30.172 | 95.568 | 76 | 100 | 70 | 52 | 29.696 | 9.432 | 7.033 | 134.782 | 29.391 | 28.4 | 27.996 | 602.242 | 26.019 | 26.947 | 1304.818 | 27.06 | 27.31 | 36.657 | 26.001 | 3.4 | 1.7 | 1.3 | 0.6 | 0.3
2061 | 30/07/2025 10:14:31.806 | 95.376 | 76 | 100 | 70 | 52 | 31.071 | 9.578 | 7.06 | 134.482 | 29.389 | 28.375 | 27.988 | 601.959 | 26.024 | 26.971 | 1306.927 | 27.091 | 27.301 | 36.726 | 28.001 | 2.3 | 1.8 | 0.9 | 0.2 | 0.4
2062 | 30/07/2025 10:14:33.440 | 95.304 | 76 | 99 | 70 | 52 | 28.357 | 9.435 | 7.068 | 134.504 | 29.393 | 28.398 | 28.005 | 602.165 | 26.032 | 26.941 | 1309.981 | 27.067 | 27.284 | 36.713 | 31.001 | 2.3 | 2.3 | 0.9 | 0.2 | 0.4
2063 | 30/07/2025 10:14:35.079 | 95.52 | 77 | 100 | 70 | 52 | 27.525 | 9.433 | 7.034 | 134.631 | 29.377 | 28.403 | 28.001 | 602.152 | 26.018 | 26.944 | 1308.911 | 27.046 | 27.326 | 36.825 | 25.001 | 3.3 | 1.1 | 0.9 | 0 | 0.4
2064 | 30/07/2025 10:14:36.715 | 95.352 | 75 | 100 | 71 | 53 | 29.62 | 9.285 | 7.033 | 134.902 | 29.394 | 28.392 | 27.984 | 602.144 | 26.038 | 26.929 | 1303.012 | 27.028 | 27.296 | 36.813 | 23.001 | 3.3 | 2 | 0.9 | 0 | 0.4
2065 | 30/07/2025 10:14:38.348 | 95.064 | 76 | 100 | 70 | 51 | 26.875 | 9.441 | 7.033 | 134.592 | 29.383 | 28.389 | 27.979 | 602.015 | 26.018 | 26.798 | 1295.344 | 27.077 | 27.311 | 36.607 | 24.001 | 3.2 | 1.1 | 0.6 | 0.8 | 0.4
2066 | 30/07/2025 10:14:39.994 | 94.176 | 74 | 100 | 71 | 52 | 30.076 | 9.549 | 7.034 | 134.565 | 29.408 | 28.373 | 27.994 | 601.843 | 26.013 | 26.955 | 1287.581 | 27.059 | 27.295 | 36.795 | 24.001 | 3.2 | 1.1 | 0.6 | 0.8 | 0.4
2067 | 30/07/2025 10:14:41.627 | 94.992 | 75 | 100 | 71 | 52 | 30.984 | 9.462 | 7.032 | 134.427 | 29.41 | 28.396 | 28.011 | 602.236 | 26.016 | 26.919 | 1275.042 | 27.058 | 27.272 | 38.203 | 24.001 | 3.2 | 1.3 | 0.6 | 0.8 | 0.4
2068 | 30/07/2025 10:14:43.261 | 94.392 | 76 | 100 | 70 | 52 | 27.906 | 9.436 | 7.033 | 134.72 | 29.42 | 28.402 | 27.986 | 601.811 | 26.02 | 26.803 | 1278.602 | 27.047 | 27.315 | 38.584 | 27.001 | 3.3 | 1.1 | 1.5 | 0 | 0.4
2069 | 30/07/2025 10:14:44.896 | 94.608 | 74 | 100 | 70 | 51 | 28.034 | 9.334 | 7.008 | 134.818 | 29.426 | 28.383 | 27.961 | 602.042 | 26.028 | 26.936 | 1268.284 | 27.063 | 27.303 | 36.815 | 24.001 | 3.3 | 2.4 | 1.5 | 0 | 0.4
2070 | 30/07/2025 10:14:46.544 | 94.512 | 76 | 100 | 70 | 52 | 29.16 | 9.44 | 7.005 | 134.551 | 29.419 | 28.386 | 27.973 | 601.841 | 26.016 | 26.945 | 1276.914 | 27.082 | 27.304 | 36.571 | 25.001 | 2.8 | 1.8 | 0.6 | 0.6 | 0.3
2071 | 30/07/2025 10:14:48.180 | 94.368 | 74 | 100 | 70 | 52 | 27.183 | 9.504 | 7.002 | 134.631 | 29.427 | 28.381 | 28.018 | 602.148 | 26.013 | 26.917 | 1287.477 | 27.059 | 27.29 | 36.466 | 25.001 | 2.8 | 1.8 | 0.6 | 0.6 | 0.3
2072 | 30/07/2025 10:14:49.815 | 94.92 | 75 | 100 | 70 | 52 | 30.593 | 9.431 | 7.006 | 134.465 | 29.406 | 28.402 | 28.004 | 602.221 | 25.992 | 26.809 | 1297.243 | 27.067 | 27.317 | 36.674 | 24.001 | 2.8 | 1.3 | 0.6 | 0.6 | 0.3
2073 | 30/07/2025 10:14:51.449 | 95.424 | 76 | 100 | 71 | 52 | 30.959 | 9.43 | 7.036 | 134.783 | 29.411 | 28.401 | 27.995 | 600.688 | 25.992 | 26.926 | 1307.331 | 27.031 | 27.318 | 36.878 | 25.001 | 3 | 2.4 | 0.9 | 0.7 | 0.3
2074 | 30/07/2025 10:14:53.086 | 95.88 | 77 | 100 | 71 | 52 | 27.461 | 9.295 | 7.033 | 134.779 | 29.409 | 28.394 | 27.988 | 602.094 | 26.008 | 26.903 | 1313.922 | 27.066 | 27.301 | 36.732 | 36.001 | 3 | 2.9 | 0.9 | 0.7 | 0.3
2075 | 30/07/2025 10:14:54.721 | 95.448 | 76 | 100 | 71 | 52 | 28.597 | 9.437 | 7.032 | 134.608 | 29.397 | 28.371 | 27.996 | 600.572 | 26.015 | 26.922 | 1301.575 | 27.083 | 27.297 | 36.617 | 28.001 | 3.4 | 3.3 | 0.9 | 1.1 | 0.2
2076 | 30/07/2025 10:14:56.357 | 95.616 | 77 | 100 | 70 | 52 | 28.602 | 9.491 | 7.034 | 134.493 | 29.404 | 28.398 | 28.005 | 600.693 | 26.028 | 26.915 | 1303.206 | 27.067 | 27.295 | 36.313 | 25.001 | 3.4 | 1.6 | 0.9 | 1.1 | 0.2
2077 | 30/07/2025 10:14:58.049 | 95.424 | 74 | 99 | 71 | 52 | 27.468 | 9.431 | 7.034 | 134.354 | 29.402 | 28.404 | 27.996 | 602.009 | 26.017 | 26.937 | 1311.851 | 27.08 | 27.307 | 36.774 | 25.001 | 3.4 | 1.6 | 0.9 | 1.1 | 0.2
2078 | 30/07/2025 10:14:59.683 | 95.448 | 76 | 100 | 70 | 51 | 30.758 | 9.437 | 7.032 | 134.87 | 29.416 | 28.399 | 27.994 | 602.057 | 26.039 | 26.929 | 1307.634 | 27.032 | 27.305 | 36.876 | 33.001 | 3.7 | 1.3 | 0.7 | 0 | 0.3
2079 | 30/07/2025 10:15:01.321 | 95.64 | 76 | 100 | 71 | 52 | 30.743 | 9.435 | 7.032 | 134.687 | 29.393 | 28.375 | 27.98 | 602.047 | 26.017 | 26.949 | 1311.951 | 27.083 | 27.319 | 36.734 | 27.001 | 3.7 | 0.7 | 0.7 | 0 | 0.3
2080 | 30/07/2025 10:15:02.954 | 95.448 | 76 | 100 | 71 | 52 | 27.123 | 9.433 | 7.032 | 134.6 | 29.389 | 28.378 | 28.006 | 602.034 | 26.022 | 26.945 | 1309.369 | 27.064 | 27.28 | 36.598 | 25.001 | 2 | 2.3 | 0.7 | 0 | 0.2
2081 | 30/07/2025 10:15:04.588 | 94.824 | 74 | 100 | 71 | 51 | 31.047 | 9.435 | 7.063 | 134.322 | 29.391 | 28.399 | 28.007 | 602.154 | 26.029 | 26.946 | 1307.032 | 27.08 | 27.291 | 36.35 | 25.001 | 2 | 2.2 | 0.7 | 0 | 0.2
2082 | 30/07/2025 10:15:06.222 | 94.992 | 75 | 100 | 70 | 53 | 28.027 | 9.425 | 7.069 | 134.651 | 29.389 | 28.391 | 27.986 | 602.024 | 26.034 | 26.941 | 1313.972 | 27.038 | 27.303 | 36.918 | 25.001 | 2 | 2.2 | 0.7 | 0 | 0.2
2083 | 30/07/2025 10:15:07.855 | 94.752 | 76 | 100 | 70 | 52 | 27.97 | 9.436 | 7.07 | 134.805 | 29.384 | 28.397 | 27.986 | 602.129 | 26.008 | 26.947 | 1305.711 | 27.054 | 27.31 | 36.599 | 26.001 | 5.4 | 3 | 1.3 | 0 | 0.1
2084 | 30/07/2025 10:15:09.491 | 95.328 | 74 | 100 | 70 | 52 | 30.849 | 9.429 | 7.072 | 134.604 | 29.369 | 28.374 | 27.972 | 601.989 | 26.021 | 26.94 | 1297.027 | 27.078 | 27.3 | 36.672 | 31.001 | 5.4 | 1.4 | 1.3 | 0 | 0.1
2085 | 30/07/2025 10:15:11.131 | 94.632 | 75 | 100 | 71 | 52 | 30.132 | 9.29 | 7.069 | 134.569 | 29.411 | 28.389 | 28.003 | 602.039 | 26.038 | 26.948 | 1295.805 | 27.054 | 27.289 | 36.349 | 29.001 | 1.9 | 1.4 | 1 | 0 | 0.2
2086 | 30/07/2025 10:15:12.850 | 94.608 | 74 | 100 | 71 | 52 | 26.803 | 9.289 | 7.122 | 134.514 | 29.405 | 28.411 | 28.001 | 601.993 | 26.024 | 26.953 | 1287.788 | 27.058 | 27.32 | 36.75 | 26.001 | 1.9 | 1.9 | 1 | 0 | 0.2
2087 | 30/07/2025 10:15:14.486 | 94.824 | 73 | 100 | 71 | 53 | 30.877 | 9.287 | 7.122 | 134.622 | 29.417 | 28.395 | 27.998 | 602.152 | 26.031 | 26.925 | 1287.521 | 27.032 | 27.3 | 36.684 | 32.001 | 2 | 2.4 | 0.4 | 0.1 | 0.2
2088 | 30/07/2025 10:15:16.124 | 95.376 | 76 | 100 | 71 | 52 | 27.374 | 9.431 | 7.071 | 134.435 | 29.418 | 28.398 | 27.972 | 601.894 | 26.013 | 26.933 | 1295.69 | 27.078 | 27.306 | 36.686 | 32.001 | 2 | 2.4 | 0.4 | 0.1 | 0.2
2089 | 30/07/2025 10:15:17.759 | 96.048 | 77 | 100 | 70 | 52 | 28.555 | 9.444 | 7.06 | 133.291 | 29.417 | 28.378 | 27.997 | 601.832 | 26.013 | 26.948 | 1303.736 | 27.069 | 27.296 | 36.76 | 24.001 | 2 | 1.5 | 0.4 | 0.1 | 0.2
2090 | 30/07/2025 10:15:19.393 | 96.504 | 77 | 100 | 70 | 52 | 30.978 | 9.288 | 7.033 | 132.905 | 29.41 | 28.388 | 27.993 | 602.305 | 26.012 | 26.93 | 1309.772 | 27.058 | 27.273 | 38.287 | 25.001 | 1.9 | 1.7 | 0.7 | 0 | 0.2
2091 | 30/07/2025 10:15:21.028 | 96.624 | 78 | 100 | 69 | 53 | 29.804 | 9.285 | 7.005 | 133.2 | 29.41 | 28.392 | 27.993 | 602.095 | 26.016 | 26.944 | 1311.908 | 27.059 | 27.314 | 36.857 | 30.001 | 1.9 | 1.9 | 0.7 | 0 | 0.2
2092 | 30/07/2025 10:15:22.667 | 97.224 | 77 | 100 | 70 | 52 | 27.004 | 9.472 | 7.015 | 133.279 | 29.41 | 28.397 | 27.984 | 602.045 | 26.005 | 26.924 | 1319.765 | 27.051 | 27.306 | 36.76 | 30.001 | 3.5 | 1.7 | 0.6 | 0 | 0.3
2093 | 30/07/2025 10:15:24.302 | 97.488 | 78 | 100 | 71 | 52 | 30.749 | 9.581 | 7.035 | 133.044 | 29.4 | 28.383 | 27.963 | 601.82 | 25.991 | 26.935 | 1318.599 | 27.081 | 27.311 | 36.824 | 30.001 | 3.5 | 1.7 | 0.6 | 0 | 0.3
2094 | 30/07/2025 10:15:25.949 | 97.992 | 78 | 99 | 70 | 52 | 27.152 | 9.502 | 7.03 | 133.268 | 29.42 | 28.381 | 28.013 | 603.415 | 26.006 | 26.917 | 1313.55 | 27.061 | 27.283 | 36.647 | 29.001 | 3.5 | 2.1 | 0.6 | 0 | 0.3
2095 | 30/07/2025 10:15:27.585 | 97.752 | 78 | 100 | 69 | 52 | 29.258 | 9.433 | 7.032 | 133.002 | 29.41 | 28.415 | 27.998 | 603.417 | 26.008 | 26.901 | 1299.99 | 27.079 | 27.298 | 36.726 | 27.001 | 2.1 | 2.7 | 0.9 | 0.5 | 0.2
2096 | 30/07/2025 10:15:29.230 | 98.544 | 78 | 100 | 72 | 51 | 31.039 | 9.432 | 7.032 | 133.329 | 29.409 | 28.397 | 27.986 | 603.232 | 26.014 | 26.931 | 1299.783 | 27.027 | 27.305 | 36.947 | 30.001 | 2.1 | 1.9 | 0.9 | 0.5 | 0.2
2097 | 30/07/2025 10:15:30.865 | 99.12 | 79 | 100 | 70 | 53 | 29.269 | 9.468 | 7.032 | 133.188 | 29.405 | 28.386 | 28.001 | 603.237 | 26.012 | 26.926 | 1294.958 | 27.077 | 27.302 | 36.716 | 26.001 | 4.5 | 2.6 | 0.8 | 0.8 | 0.2
2098 | 30/07/2025 10:15:32.502 | 98.832 | 79 | 100 | 70 | 52 | 30.888 | 9.519 | 7.033 | 133.191 | 29.41 | 28.377 | 27.993 | 603.197 | 26.049 | 26.938 | 1291.328 | 27.07 | 27.297 | 36.861 | 30.001 | 4.5 | 1.2 | 0.8 | 0.8 | 0.2
2099 | 30/07/2025 10:15:34.137 | 99.312 | 81 | 100 | 71 | 52 | 30.337 | 9.433 | 7.033 | 133.032 | 29.397 | 28.391 | 28.006 | 603.307 | 26.017 | 26.945 | 1286.961 | 27.06 | 27.298 | 36.353 | 30.001 | 4.5 | 1.2 | 0.8 | 0.8 | 0.2
2100 | 30/07/2025 10:15:35.772 | 99.168 | 80 | 100 | 70 | 53 | 26.928 | 9.288 | 7.035 | 132.938 | 29.39 | 28.392 | 27.996 | 603.255 | 26.018 | 26.96 | 1283.802 | 27.054 | 27.299 | 36.718 | 31.001 | 1.5 | 1.8 | 1 | 0.8 | 0.2
2101 | 30/07/2025 10:15:37.407 | 99.48 | 81 | 100 | 70 | 52 | 29.818 | 9.479 | 7.031 | 133.403 | 29.404 | 28.398 | 27.997 | 603.456 | 26.026 | 26.954 | 1277.584 | 27.037 | 27.313 | 36.756 | 25.001 | 1.5 | 1.3 | 1 | 0.8 | 0.2
2102 | 30/07/2025 10:15:39.043 | 99.264 | 80 | 100 | 69 | 52 | 31.096 | 9.477 | 7.034 | 133.088 | 29.377 | 28.389 | 27.974 | 603.196 | 26.022 | 26.959 | 1274.354 | 27.1 | 27.324 | 36.73 | 24.001 | 2.3 | 1.9 | 0.9 | 0.8 | 0.2
2103 | 30/07/2025 10:15:40.679 | 99.072 | 79 | 100 | 71 | 52 | 28.639 | 9.314 | 7.03 | 133.125 | 29.369 | 28.382 | 28.009 | 603.266 | 26.026 | 26.935 | 1273.098 | 27.067 | 27.295 | 36.723 | 26.001 | 2.3 | 1.3 | 0.9 | 0.8 | 0.2
2104 | 30/07/2025 10:15:42.312 | 98.808 | 78 | 100 | 70 | 54 | 30.979 | 9.288 | 7.032 | 132.969 | 29.379 | 28.417 | 27.992 | 603.315 | 26.009 | 26.943 | 1269.157 | 27.081 | 27.28 | 36.523 | 26.001 | 2.3 | 1.3 | 0.9 | 0.8 | 0.2
2105 | 30/07/2025 10:15:43.947 | 98.856 | 80 | 100 | 70 | 52 | 29.644 | 9.283 | 7.031 | 134.649 | 29.395 | 28.394 | 28.001 | 603.23 | 26.025 | 26.948 | 1270.413 | 27.047 | 27.304 | 36.723 | 26.001 | 3.9 | 1.1 | 0.9 | 0.2 | 0.2
2106 | 30/07/2025 10:15:45.581 | 97.92 | 79 | 100 | 71 | 51 | 26.862 | 9.577 | 7.069 | 134.718 | 29.4 | 28.392 | 27.984 | 603.245 | 26.007 | 26.93 | 1262.238 | 27.047 | 27.306 | 36.571 | 30.001 | 3.9 | 1.9 | 0.9 | 0.2 | 0.2
2107 | 30/07/2025 10:15:47.216 | 97.608 | 79 | 100 | 70 | 52 | 30.084 | 9.521 | 7.072 | 134.545 | 29.402 | 28.368 | 27.979 | 603.079 | 26.02 | 26.953 | 1267.058 | 27.082 | 27.309 | 36.532 | 24.001 | 1.4 | 3.2 | 0.9 | 0 | 0.1
2108 | 30/07/2025 10:15:48.852 | 97.152 | 77 | 100 | 71 | 52 | 31.023 | 9.435 | 7.071 | 134.667 | 29.416 | 28.387 | 28.013 | 603.291 | 26.032 | 26.943 | 1276.665 | 27.06 | 27.271 | 36.425 | 27.001 | 1.4 | 1.5 | 0.9 | 0 | 0.1
2109 | 30/07/2025 10:15:50.487 | 97.824 | 81 | 100 | 71 | 52 | 29.023 | 9.43 | 7.073 | 134.254 | 29.407 | 28.399 | 27.994 | 603.256 | 26.014 | 26.946 | 1275.628 | 27.061 | 27.291 | 36.485 | 28.001 | 3.6 | 2 | 0 | 0.5 | 0.2
2110 | 30/07/2025 10:15:52.125 | 97.728 | 77 | 100 | 70 | 52 | 31.039 | 9.495 | 7.033 | 134.692 | 29.414 | 28.401 | 28.007 | 603.36 | 26.012 | 26.927 | 1260.188 | 27.034 | 27.299 | 38.582 | 28.001 | 3.6 | 2 | 0 | 0.5 | 0.2
2111 | 30/07/2025 10:15:53.758 | 98.232 | 79 | 100 | 70 | 52 | 29.122 | 9.443 | 7.033 | 134.737 | 29.401 | 28.4 | 27.985 | 603.328 | 26.01 | 26.944 | 1269.245 | 27.077 | 27.313 | 38.198 | 27.001 | 3.6 | 1.2 | 0 | 0.5 | 0.2
2112 | 30/07/2025 10:15:55.393 | 98.04 | 79 | 100 | 71 | 52 | 27.164 | 9.285 | 7.031 | 134.764 | 29.412 | 28.364 | 27.988 | 603.098 | 26.016 | 26.936 | 1267.099 | 27.071 | 27.295 | 36.778 | 26.001 | 3.3 | 3.8 | 0.6 | 0.6 | 0.2
2113 | 30/07/2025 10:15:57.029 | 98.088 | 78 | 100 | 70 | 52 | 30.543 | 9.43 | 7.033 | 134.412 | 29.409 | 28.401 | 27.994 | 602.156 | 26.011 | 26.92 | 1265.401 | 27.057 | 27.285 | 36.389 | 31.001 | 3.3 | 3.1 | 0.6 | 0.6 | 0.2
2114 | 30/07/2025 10:15:58.668 | 97.608 | 78 | 100 | 70 | 52 | 26.92 | 9.478 | 7.035 | 134.564 | 29.42 | 28.396 | 27.993 | 602.115 | 26.005 | 26.918 | 1265.246 | 27.056 | 27.296 | 36.673 | 26.001 | 2.9 | 1.3 | 0.9 | 0.5 | 0.2
2115 | 30/07/2025 10:16:00.301 | 97.8 | 78 | 100 | 71 | 52 | 29.843 | 9.294 | 7.07 | 134.564 | 29.389 | 28.402 | 27.994 | 602.079 | 26.009 | 26.898 | 1262.746 | 27.036 | 27.315 | 36.704 | 26.001 | 2.9 | 1.3 | 0.9 | 0.5 | 0.2
2116 | 30/07/2025 10:16:01.935 | 97.728 | 80 | 100 | 70 | 54 | 31.068 | 9.474 | 7.115 | 134.58 | 29.405 | 28.389 | 27.96 | 601.948 | 26.014 | 26.918 | 1269.446 | 27.067 | 27.306 | 36.768 | 27.001 | 2.9 | 1.7 | 0.9 | 0.5 | 0.2
2117 | 30/07/2025 10:16:03.570 | 97.608 | 78 | 100 | 70 | 52 | 28.66 | 9.435 | 7.104 | 134.645 | 29.404 | 28.379 | 28.031 | 602.069 | 26.027 | 26.928 | 1276.458 | 27.056 | 27.301 | 36.463 | 26.001 | 4 | 1.3 | 1.8 | 1.6 | 0.1
2118 | 30/07/2025 10:16:05.205 | 97.296 | 76 | 100 | 70 | 52 | 27.555 | 9.29 | 7.089 | 134.337 | 29.391 | 28.411 | 27.989 | 602.057 | 26.029 | 26.933 | 1277.281 | 27.076 | 27.305 | 36.457 | 27.001 | 4 | 2.3 | 1.8 | 1.6 | 0.1
2119 | 30/07/2025 10:16:06.840 | 97.224 | 77 | 100 | 70 | 52 | 30.811 | 9.432 | 7.109 | 134.888 | 29.409 | 28.393 | 27.979 | 601.985 | 26.052 | 26.944 | 1282.02 | 27.026 | 27.309 | 36.792 | 23.001 | 3.1 | 2 | 0.3 | 1 | 0.1
2120 | 30/07/2025 10:16:08.475 | 96.696 | 78 | 100 | 70 | 52 | 26.998 | 9.518 | 7.124 | 134.563 | 29.397 | 28.394 | 27.974 | 601.972 | 26.019 | 26.95 | 1289.436 | 27.069 | 27.309 | 36.579 | 28.001 | 3.1 | 3 | 0.3 | 1 | 0.1
2121 | 30/07/2025 10:16:10.111 | 97.032 | 77 | 100 | 70 | 52 | 30.312 | 9.578 | 7.088 | 134.659 | 29.396 | 28.379 | 27.971 | 601.957 | 26.04 | 26.946 | 1294.881 | 27.071 | 27.287 | 36.795 | 28.001 | 3.1 | 3 | 0.3 | 1 | 0.1
2122 | 30/07/2025 10:16:11.747 | 96.48 | 77 | 100 | 71 | 54 | 31.089 | 9.442 | 7.087 | 134.62 | 29.381 | 28.382 | 28.01 | 601.858 | 26.023 | 26.953 | 1306.708 | 27.072 | 27.294 | 34.611 | 25.001 | 2.2 | 2.7 | 0.6 | 0.1 | 0.1
2123 | 30/07/2025 10:16:13.383 | 96.624 | 78 | 100 | 70 | 51 | 28.098 | 9.429 | 7.125 | 134.401 | 29.381 | 28.4 | 27.984 | 602.085 | 26.012 | 26.96 | 1307.361 | 27.051 | 27.293 | 36.591 | 24.001 | 2.2 | 1.2 | 0.6 | 0.1 | 0.1
2124 | 30/07/2025 10:16:15.027 | 97.368 | 78 | 100 | 70 | 52 | 28.018 | 9.428 | 7.07 | 134.967 | 29.38 | 28.393 | 28.007 | 601.928 | 26.017 | 26.928 | 1294.956 | 27.027 | 27.312 | 36.643 | 28.001 | 2.4 | 2.4 | 0.9 | 0.7 | 0.1
2125 | 30/07/2025 10:16:16.664 | 96.624 | 77 | 100 | 71 | 52 | 30.916 | 9.506 | 7.071 | 134.528 | 29.384 | 28.397 | 27.983 | 602.042 | 26.016 | 26.954 | 1301.786 | 27.091 | 27.326 | 36.65 | 26.001 | 2.4 | 2.1 | 0.9 | 0.7 | 0.1
2126 | 30/07/2025 10:16:18.299 | 96.672 | 76 | 100 | 70 | 52 | 27.141 | 9.431 | 7.068 | 134.687 | 29.395 | 28.375 | 27.999 | 602.055 | 26.005 | 26.943 | 1303.902 | 27.057 | 27.306 | 36.63 | 26.001 | 2.4 | 2.1 | 0.9 | 0.7 | 0.1
2127 | 30/07/2025 10:16:19.933 | 96.696 | 77 | 100 | 70 | 53 | 30.537 | 9.552 | 7.073 | 134.399 | 29.399 | 28.4 | 27.997 | 601.863 | 26.015 | 26.941 | 1306.648 | 27.088 | 27.291 | 36.364 | 28.001 | 2 | 1 | 1 | 0 | 0.1
2128 | 30/07/2025 10:16:21.568 | 97.248 | 78 | 100 | 71 | 52 | 30.942 | 9.435 | 7.072 | 134.614 | 29.428 | 28.407 | 27.998 | 602.179 | 26.032 | 26.942 | 1317.231 | 27.034 | 27.301 | 36.868 | 34.001 | 2 | 1.1 | 1 | 0 | 0.1
2129 | 30/07/2025 10:16:23.204 | 96.696 | 78 | 100 | 70 | 52 | 27.451 | 9.498 | 7.072 | 134.674 | 29.415 | 28.4 | 27.993 | 602.102 | 26.016 | 26.943 | 1312.187 | 27.044 | 27.313 | 36.586 | 33.001 | 1.9 | 1.3 | 0.6 | 0.6 | 0.1
2130 | 30/07/2025 10:16:24.839 | 97.056 | 80 | 100 | 70 | 50 | 28.519 | 9.58 | 7.072 | 134.613 | 29.405 | 28.382 | 27.98 | 601.904 | 26.008 | 26.945 | 1307.177 | 27.075 | 27.297 | 36.562 | 27.001 | 1.9 | 2.2 | 0.6 | 0.6 | 0.1
2131 | 30/07/2025 10:16:26.474 | 97.2 | 77 | 100 | 71 | 53 | 28.578 | 9.458 | 7.036 | 134.598 | 29.407 | 28.375 | 28.005 | 601.875 | 26.015 | 26.926 | 1312.062 | 27.071 | 27.307 | 36.486 | 25.001 | 2.4 | 2.1 | 0.6 | 0.5 | 0.1
2132 | 30/07/2025 10:16:28.109 | 96.96 | 78 | 100 | 70 | 53 | 27.58 | 9.483 | 7.032 | 134.418 | 29.418 | 28.397 | 27.999 | 602.02 | 26.014 | 26.936 | 1317.05 | 27.063 | 27.283 | 36.378 | 25.001 | 2.4 | 2.1 | 0.6 | 0.5 | 0.1
2133 | 30/07/2025 10:16:29.747 | 97.056 | 79 | 100 | 70 | 52 | 30.772 | 9.519 | 6.935 | 134.617 | 29.592 | 28.398 | 28.016 | 601.979 | 26.006 | 26.927 | 1315.149 | 27.034 | 27.304 | 36.652 | 31.001 | 2.4 | 1.9 | 0.6 | 0.5 | 0.1
2134 | 30/07/2025 10:16:31.383 | 97.176 | 78 | 100 | 71 | 52 | 30.702 | 9.563 | 6.981 | 134.647 | 29.403 | 28.396 | 27.989 | 600.598 | 26.001 | 26.939 | 1318.616 | 27.066 | 27.314 | 36.614 | 27.001 | 2.6 | 1.7 | 0.9 | 0 | 0.2
2135 | 30/07/2025 10:16:33.019 | 97.368 | 78 | 100 | 70 | 52 | 27.034 | 9.532 | 7.004 | 134.758 | 29.588 | 28.366 | 28.003 | 600.503 | 26.003 | 26.914 | 1312.61 | 27.059 | 27.294 | 36.627 | 32.001 | 2.6 | 1.3 | 0.9 | 0 | 0.2
2136 | 30/07/2025 10:16:34.653 | 97.392 | 78 | 100 | 71 | 52 | 29.165 | 9.589 | 7.033 | 134.401 | 29.46 | 28.397 | 27.998 | 600.524 | 25.993 | 26.911 | 1290.31 | 27.058 | 27.281 | 36.342 | 26.001 | 2.8 | 1.9 | 0.6 | 0 | 0.2
2137 | 30/07/2025 10:16:36.289 | 97.32 | 78 | 100 | 70 | 52 | 27.94 | 9.577 | 7.033 | 134.589 | 29.42 | 28.404 | 27.999 | 600.753 | 26.024 | 26.915 | 1291.839 | 27.058 | 27.287 | 36.576 | 26.001 | 2.8 | 1.9 | 0.6 | 0 | 0.2
2138 | 30/07/2025 10:16:37.930 | 97.224 | 80 | 100 | 70 | 52 | 28.014 | 9.505 | 7.032 | 134.696 | 29.401 | 28.409 | 27.993 | 600.668 | 26.017 | 26.914 | 1293.197 | 27.047 | 27.319 | 36.571 | 25.001 | 2.8 | 3.2 | 0.6 | 0 | 0.2
2139 | 30/07/2025 10:16:39.568 | 97.056 | 77 | 100 | 70 | 51 | 30.91 | 9.506 | 7.009 | 134.494 | 29.394 | 28.395 | 27.965 | 600.601 | 26.016 | 26.926 | 1293.662 | 27.069 | 27.305 | 36.686 | 27.001 | 1.4 | 2.3 | 0.7 | 0 | 0.3
2140 | 30/07/2025 10:16:41.204 | 97.224 | 78 | 100 | 71 | 51 | 30.425 | 9.285 | 7.002 | 134.71 | 29.403 | 28.373 | 28.023 | 600.677 | 26.021 | 26.94 | 1288.412 | 27.054 | 27.3 | 36.521 | 29.001 | 1.4 | 2.7 | 0.7 | 0 | 0.3
2141 | 30/07/2025 10:16:42.842 | 96.576 | 78 | 100 | 68 | 52 | 26.978 | 9.289 | 7.004 | 134.313 | 29.39 | 28.411 | 27.994 | 600.596 | 26.016 | 26.959 | 1295.881 | 27.082 | 27.295 | 36.415 | 27.001 | 1.5 | 1.6 | 1.7 | 0.5 | 0.2
2142 | 30/07/2025 10:16:44.479 | 96.456 | 76 | 100 | 70 | 52 | 31.02 | 9.317 | 7.004 | 134.642 | 29.548 | 28.414 | 28.008 | 600.718 | 26.02 | 26.956 | 1297.28 | 27.05 | 27.311 | 36.612 | 27.001 | 1.5 | 1.6 | 1.7 | 0.5 | 0.2
2143 | 30/07/2025 10:16:46.119 | 96.84 | 79 | 100 | 70 | 52 | 27.591 | 9.573 | 7.034 | 134.627 | 29.55 | 28.391 | 27.974 | 600.663 | 26.013 | 26.951 | 1292.271 | 27.054 | 27.305 | 36.648 | 27.001 | 1.5 | 1.6 | 1.7 | 0.5 | 0.2
2144 | 30/07/2025 10:16:47.754 | 96.216 | 77 | 100 | 71 | 52 | 28.721 | 9.578 | 7.033 | 134.699 | 29.383 | 28.385 | 27.975 | 600.596 | 26.036 | 26.951 | 1292.256 | 27.065 | 27.305 | 36.58 | 24.001 | 2.9 | 1.3 | 1.8 | 0.6 | 0.3
2145 | 30/07/2025 10:16:49.391 | 96.216 | 77 | 100 | 71 | 51 | 30.986 | 9.539 | 7.031 | 134.548 | 29.373 | 28.378 | 28.01 | 600.398 | 26.012 | 26.955 | 1280.367 | 27.068 | 27.314 | 36.455 | 27.001 | 2.9 | 2.5 | 1.8 | 0.6 | 0.3
2146 | 30/07/2025 10:16:51.027 | 96.84 | 78 | 100 | 70 | 52 | 29.82 | 9.433 | 7.034 | 134.36 | 29.558 | 28.398 | 27.99 | 600.642 | 26.017 | 26.947 | 1277.042 | 27.049 | 27.298 | 36.596 | 26.001 | 2.2 | 1.5 | 0.1 | 0.6 | 0.3
2147 | 30/07/2025 10:16:52.663 | 96.24 | 77 | 100 | 71 | 52 | 26.959 | 9.432 | 7.057 | 134.752 | 29.577 | 28.397 | 28.003 | 600.64 | 26.029 | 26.925 | 1277.308 | 27.027 | 27.301 | 36.764 | 28.001 | 2.2 | 1 | 0.1 | 0.6 | 0.3
2148 | 30/07/2025 10:16:54.297 | 96.672 | 78 | 100 | 70 | 52 | 30.725 | 9.54 | 7.07 | 134.737 | 29.581 | 28.398 | 27.977 | 600.598 | 26.022 | 26.945 | 1285.912 | 27.049 | 27.306 | 36.718 | 28.001 | 2.2 | 1 | 0.1 | 0.6 | 0.3
2149 | 30/07/2025 10:16:55.931 | 96.888 | 77 | 100 | 70 | 52 | 27.113 | 9.417 | 7.069 | 134.641 | 29.582 | 28.382 | 27.994 | 600.783 | 26.018 | 26.937 | 1299.275 | 27.062 | 27.307 | 36.669 | 23.001 | 1.1 | 1.6 | 1.5 | 0 | 0.3
2150 | 30/07/2025 10:16:57.567 | 96.936 | 78 | 100 | 70 | 52 | 29.078 | 9.409 | 7.07 | 134.445 | 29.576 | 28.389 | 28.009 | 601.995 | 26.011 | 26.946 | 1292.435 | 27.07 | 27.29 | 36.369 | 29.001 | 1.1 | 1 | 1.5 | 0 | 0.3
2151 | 30/07/2025 10:16:59.203 | 97.392 | 77 | 100 | 71 | 52 | 31.076 | 9.427 | 7.071 | 134.707 | 29.612 | 28.4 | 28.006 | 602.118 | 26.024 | 26.936 | 1299.17 | 27.047 | 27.307 | 36.717 | 30.001 | 2.9 | 2.7 | 0.9 | 0 | 0.3
2152 | 30/07/2025 10:17:00.839 | 97.704 | 80 | 100 | 71 | 52 | 29.274 | 9.431 | 7.07 | 134.67 | 29.578 | 28.405 | 27.981 | 602.21 | 25.984 | 26.939 | 1299.888 | 27.049 | 27.314 | 36.763 | 28.001 | 2.9 | 2.4 | 0.9 | 0 | 0.3
2153 | 30/07/2025 10:17:02.474 | 97.32 | 78 | 100 | 71 | 54 | 30.936 | 9.502 | 7.071 | 134.673 | 29.587 | 28.393 | 27.96 | 602.138 | 26.008 | 26.926 | 1310.892 | 27.059 | 27.303 | 36.668 | 28.001 | 3.8 | 1.8 | 0 | 0 | 0.3
2154 | 30/07/2025 10:17:04.109 | 97.104 | 78 | 100 | 72 | 52 | 30.347 | 9.584 | 7.07 | 134.597 | 29.577 | 28.374 | 27.989 | 603.254 | 26.004 | 26.928 | 1324.175 | 27.074 | 27.318 | 36.651 | 28.001 | 3.8 | 1.8 | 0 | 0 | 0.3
2155 | 30/07/2025 10:17:05.744 | 97.776 | 79 | 100 | 70 | 52 | 26.922 | 9.523 | 7.071 | 134.536 | 29.58 | 28.398 | 27.999 | 601.948 | 26.015 | 26.946 | 1328.687 | 27.066 | 27.293 | 36.463 | 31.001 | 3.8 | 2.8 | 0 | 0 | 0.3
2156 | 30/07/2025 10:17:07.379 | 97.608 | 78 | 99 | 70 | 52 | 29.669 | 9.432 | 7.07 | 134.681 | 29.58 | 28.398 | 28.018 | 602.222 | 26.003 | 26.903 | 1329.767 | 27.173 | 27.298 | 36.75 | 27.001 | 3.2 | 2 | 1.2 | 0.5 | 0.3
2157 | 30/07/2025 10:17:09.015 | 98.112 | 79 | 100 | 70 | 52 | 31.081 | 9.434 | 7.073 | 134.685 | 29.578 | 28.397 | 27.967 | 601.975 | 26.013 | 26.906 | 1311.795 | 27.213 | 27.303 | 36.642 | 25.001 | 3.2 | 3.3 | 1.2 | 0.5 | 0.3
2158 | 30/07/2025 10:17:10.652 | 97.896 | 78 | 100 | 71 | 52 | 28.586 | 9.35 | 7.069 | 134.816 | 29.59 | 28.378 | 27.986 | 601.9 | 26.027 | 26.911 | 1309.265 | 27.216 | 27.299 | 36.678 | 27.001 | 2.7 | 1.7 | 0 | 0 | 0.2
2159 | 30/07/2025 10:17:12.286 | 98.376 | 80 | 100 | 70 | 52 | 30.986 | 9.433 | 7.07 | 134.583 | 29.575 | 28.357 | 28.009 | 601.892 | 26.013 | 26.932 | 1309.952 | 27.067 | 27.298 | 36.566 | 27.001 | 2.7 | 1.7 | 0 | 0 | 0.2
2160 | 30/07/2025 10:17:13.921 | 98.76 | 81 | 100 | 72 | 52 | 29.797 | 9.578 | 7.072 | 134.646 | 29.581 | 28.398 | 28.008 | 602.357 | 26.039 | 26.924 | 1307.504 | 27.091 | 27.284 | 36.602 | 27.001 | 2.7 | 1.3 | 0 | 0 | 0.2
2161 | 30/07/2025 10:17:15.556 | 99.072 | 80 | 100 | 70 | 52 | 26.959 | 9.44 | 7.072 | 134.614 | 29.563 | 28.401 | 28.005 | 602.036 | 26.02 | 26.942 | 1306.767 | 27.052 | 27.322 | 36.701 | 32.001 | 4.9 | 1.1 | 0.9 | 0.5 | 0.3
2162 | 30/07/2025 10:17:17.191 | 98.616 | 79 | 100 | 70 | 53 | 30.229 | 9.372 | 7.073 | 134.654 | 29.561 | 28.388 | 27.956 | 602.024 | 26.009 | 26.943 | 1304.695 | 27.064 | 27.298 | 36.798 | 29.001 | 4.9 | 0.9 | 0.9 | 0.5 | 0.3
2163 | 30/07/2025 10:17:18.826 | 98.64 | 81 | 100 | 70 | 51 | 31.059 | 9.305 | 7.069 | 134.639 | 29.561 | 28.376 | 28 | 602.168 | 26.01 | 26.943 | 1306.836 | 27.062 | 27.3 | 36.641 | 28.001 | 2.3 | 2.6 | 0.6 | 0.5 | 0.3
2164 | 30/07/2025 10:17:20.464 | 98.664 | 80 | 100 | 71 | 53 | 29.247 | 9.409 | 7.069 | 134.71 | 29.576 | 28.383 | 28.008 | 601.846 | 26.031 | 26.955 | 1315.427 | 27.206 | 27.283 | 36.437 | 25.001 | 2.3 | 2.3 | 0.6 | 0.5 | 0.3
2165 | 30/07/2025 10:17:22.100 | 98.688 | 80 | 100 | 70 | 52 | 31.022 | 9.23 | 7.033 | 134.609 | 29.566 | 28.416 | 28.009 | 602.166 | 26.019 | 26.928 | 1317.688 | 27.209 | 27.31 | 36.497 | 25.001 | 2.3 | 2.3 | 0.6 | 0.5 | 0.3
2166 | 30/07/2025 10:17:23.739 | 98.28 | 77 | 100 | 68 | 51 | 29.224 | 9.342 | 7.033 | 134.565 | 29.56 | 28.394 | 27.978 | 603.256 | 26.023 | 26.956 | 1317.361 | 27.183 | 27.307 | 36.796 | 26.001 | 4 | 1.7 | 0.4 | 0 | 0.2
2167 | 30/07/2025 10:17:25.373 | 97.944 | 78 | 100 | 70 | 52 | 27.147 | 9.281 | 7.032 | 134.804 | 29.58 | 28.39 | 27.978 | 603.376 | 26.02 | 26.941 | 1304.26 | 27.067 | 27.305 | 36.722 | 24.001 | 4 | 1.1 | 0.4 | 0 | 0.2
2168 | 30/07/2025 10:17:27.013 | 97.848 | 78 | 100 | 70 | 52 | 30.587 | 9.506 | 7.032 | 134.531 | 29.557 | 28.373 | 28.013 | 603.337 | 26.012 | 26.939 | 1302.293 | 27.08 | 27.299 | 36.565 | 27.001 | 2.4 | 1.8 | 1.1 | 0.5 | 0.2
2169 | 30/07/2025 10:17:28.652 | 97.776 | 79 | 100 | 71 | 52 | 30.944 | 9.291 | 7.034 | 134.475 | 29.586 | 28.393 | 28.003 | 603.154 | 26.013 | 26.96 | 1291.923 | 27.166 | 27.296 | 36.456 | 23.001 | 2.4 | 1.2 | 1.1 | 0.5 | 0.2
2170 | 30/07/2025 10:17:30.292 | 97.44 | 78 | 100 | 71 | 52 | 29.705 | 9.286 | 7.034 | 134.55 | 29.569 | 28.408 | 27.982 | 603.371 | 26.018 | 26.95 | 1295.759 | 27.064 | 27.314 | 36.655 | 23.001 | 2.4 | 1.2 | 1.1 | 0.5 | 0.2
2171 | 30/07/2025 10:17:31.927 | 97.92 | 78 | 99 | 71 | 52 | 31.079 | 9.284 | 7.033 | 134.697 | 29.585 | 28.389 | 27.966 | 603.219 | 26.028 | 26.945 | 1296.712 | 27.039 | 27.303 | 36.736 | 26.001 | 2.7 | 0.9 | 1.2 | 0.5 | 0.2
2172 | 30/07/2025 10:17:33.563 | 97.872 | 79 | 100 | 70 | 52 | 28.662 | 9.286 | 7.022 | 134.665 | 29.58 | 28.374 | 27.994 | 602.579 | 26.007 | 26.926 | 1297.27 | 27.07 | 27.3 | 36.684 | 25.001 | 2.7 | 1.1 | 1.2 | 0.5 | 0.2
2173 | 30/07/2025 10:17:35.201 | 97.224 | 77 | 100 | 69 | 52 | 27.536 | 9.291 | 7.004 | 134.533 | 29.58 | 28.389 | 27.997 | 601.935 | 26.017 | 26.945 | 1297.254 | 27.067 | 27.284 | 36.886 | 26.001 | 3.8 | 0.3 | 1.2 | 0.4 | 0.2
2174 | 30/07/2025 10:17:36.835 | 97.248 | 77 | 100 | 71 | 52 | 30.836 | 9.463 | 6.865 | 134.529 | 29.604 | 28.408 | 27.995 | 600.76 | 26.016 | 26.931 | 1306.323 | 27.194 | 27.296 | 38.549 | 23.001 | 3.8 | 1.1 | 1.2 | 0.4 | 0.2
2175 | 30/07/2025 10:17:38.469 | 96.888 | 77 | 100 | 71 | 52 | 26.989 | 9.554 | 6.867 | 134.707 | 29.589 | 28.396 | 27.991 | 600.736 | 26.012 | 26.946 | 1304.549 | 27.189 | 27.308 | 36.84 | 26.001 | 2.8 | 1.8 | 0.4 | 0.5 | 0.2
2176 | 30/07/2025 10:17:40.104 | 96.792 | 77 | 99 | 70 | 52 | 30.233 | 9.431 | 6.992 | 134.753 | 29.6 | 28.395 | 27.981 | 600.71 | 25.995 | 26.928 | 1305.854 | 27.126 | 27.312 | 37.623 | 26.001 | 2.8 | 1.8 | 0.4 | 0.5 | 0.2
2177 | 30/07/2025 10:17:41.741 | 96.36 | 78 | 100 | 69 | 52 | 31.121 | 9.286 | 7.004 | 134.578 | 29.566 | 28.374 | 27.98 | 600.513 | 26.003 | 26.925 | 1314.969 | 27.094 | 27.298 | 36.782 | 28.001 | 2.8 | 0.7 | 0.4 | 0.5 | 0.2
2178 | 30/07/2025 10:17:43.382 | 96.168 | 77 | 100 | 72 | 52 | 28.048 | 9.508 | 7.004 | 134.642 | 29.583 | 28.387 | 27.985 | 600.49 | 26.008 | 26.924 | 1323.137 | 27.207 | 27.279 | 36.546 | 30.001 | 1.9 | 1.2 | 0.9 | 0.5 | 0.1
2179 | 30/07/2025 10:17:45.030 | 95.616 | 77 | 100 | 72 | 52 | 28.015 | 9.42 | 7.031 | 134.619 | 29.572 | 28.406 | 27.996 | 600.967 | 26.022 | 26.909 | 1324.722 | 27.192 | 27.304 | 38.319 | 34.001 | 1.9 | 1.1 | 0.9 | 0.5 | 0.1
2180 | 30/07/2025 10:17:46.665 | 95.304 | 76 | 100 | 70 | 52 | 30.907 | 9.286 | 7.035 | 134.65 | 29.574 | 28.393 | 27.975 | 600.476 | 26.023 | 26.94 | 1317.115 | 27.204 | 27.305 | 36.606 | 29.001 | 4.5 | 2.4 | 1 | 0.8 | 0.1
2181 | 30/07/2025 10:17:48.300 | 95.76 | 76 | 100 | 70 | 52 | 27.135 | 9.286 | 7.072 | 134.652 | 29.58 | 28.382 | 27.978 | 600.645 | 26.032 | 26.942 | 1311.099 | 27.225 | 27.315 | 36.592 | 29.001 | 4.5 | 2.4 | 1 | 0.8 | 0.1
2182 | 30/07/2025 10:17:49.935 | 95.904 | 77 | 100 | 71 | 52 | 30.557 | 9.504 | 7.088 | 134.652 | 29.566 | 28.386 | 27.995 | 600.565 | 26.015 | 26.952 | 1298.096 | 27.219 | 27.293 | 36.618 | 26.001 | 4.5 | 1.2 | 1 | 0.8 | 0.1
2183 | 30/07/2025 10:17:51.568 | 95.904 | 77 | 100 | 70 | 53 | 30.992 | 9.576 | 7.088 | 134.618 | 29.568 | 28.4 | 28.012 | 600.618 | 26.029 | 26.948 | 1297.472 | 27.058 | 27.283 | 36.47 | 25.001 | 1.2 | 2.5 | 0.7 | 0 | 0.2
2184 | 30/07/2025 10:17:53.202 | 95.808 | 78 | 100 | 71 | 52 | 27.481 | 9.43 | 7.122 | 134.664 | 29.554 | 28.41 | 27.993 | 600.673 | 26.029 | 26.957 | 1292.283 | 27.202 | 27.313 | 36.759 | 27.001 | 1.2 | 0.8 | 0.7 | 0 | 0.2
2185 | 30/07/2025 10:17:54.840 | 96.696 | 77 | 100 | 69 | 54 | 28.6 | 9.504 | 7.117 | 134.659 | 29.565 | 28.382 | 27.96 | 600.604 | 26.033 | 26.958 | 1290.103 | 27.06 | 27.298 | 36.814 | 26.001 | 1.2 | 2.2 | 1.4 | 0.5 | 0.1
2186 | 30/07/2025 10:17:56.475 | 96.36 | 77 | 100 | 71 | 52 | 28.576 | 9.507 | 7.009 | 134.739 | 29.559 | 28.385 | 27.971 | 600.564 | 26.017 | 26.959 | 1287.361 | 27.191 | 27.311 | 36.675 | 24.001 | 1.2 | 1.1 | 1.4 | 0.5 | 0.1
2187 | 30/07/2025 10:17:58.108 | 96.552 | 79 | 100 | 70 | 53 | 27.544 | 9.36 | 7.004 | 134.715 | 29.565 | 28.381 | 28.013 | 600.553 | 26.027 | 26.947 | 1301.68 | 27.061 | 27.428 | 36.652 | 24.001 | 1.2 | 1.1 | 1.4 | 0.5 | 0.1
2188 | 30/07/2025 10:17:59.744 | 97.08 | 78 | 100 | 70 | 52 | 30.786 | 9.286 | 7.033 | 134.475 | 29.552 | 28.42 | 27.994 | 601.747 | 26.013 | 26.947 | 1300.21 | 27.207 | 27.463 | 36.56 | 21.001 | 2.7 | 1 | 1.3 | 0.6 | 0.2
2189 | 30/07/2025 10:18:01.381 | 97.176 | 78 | 99 | 70 | 51 | 30.803 | 9.43 | 7.054 | 134.499 | 29.566 | 28.395 | 27.977 | 600.512 | 26.014 | 26.944 | 1297.07 | 27.19 | 27.441 | 36.973 | 25.001 | 2.7 | 1.4 | 1.3 | 0.6 | 0.2
2190 | 30/07/2025 10:18:03.015 | 96.768 | 77 | 100 | 70 | 52 | 27.181 | 9.515 | 7.035 | 134.447 | 29.579 | 28.394 | 27.966 | 602.189 | 26.019 | 26.93 | 1291.437 | 27.217 | 27.451 | 36.696 | 23.001 | 3.5 | 0.9 | 1.2 | 0 | 0.2
2191 | 30/07/2025 10:18:04.651 | 96.984 | 79 | 100 | 71 | 51 | 29.2 | 9.462 | 7.031 | 133.14 | 29.588 | 28.388 | 28.002 | 602 | 26.006 | 26.935 | 1299.128 | 27.232 | 27.445 | 36.621 | 23.001 | 3.5 | 2.3 | 1.2 | 0 | 0.2
2192 | 30/07/2025 10:18:06.286 | 96.624 | 79 | 100 | 70 | 52 | 28.168 | 9.492 | 7.032 | 133.104 | 29.589 | 28.395 | 28.01 | 602.153 | 26.014 | 26.923 | 1298.699 | 27.065 | 27.269 | 36.543 | 23.001 | 3.5 | 2.3 | 1.2 | 0 | 0.2
2193 | 30/07/2025 10:18:07.921 | 96.84 | 78 | 100 | 70 | 52 | 28.087 | 9.291 | 7.073 | 133.055 | 29.569 | 28.392 | 27.996 | 601.94 | 26.01 | 26.948 | 1304.983 | 27.211 | 27.305 | 36.754 | 29.001 | 4 | 1.4 | 1.4 | 0.7 | 0.1
2194 | 30/07/2025 10:18:09.556 | 96.792 | 79 | 100 | 70 | 52 | 30.953 | 9.387 | 7.07 | 133.434 | 29.602 | 28.393 | 27.987 | 601.885 | 26.019 | 26.931 | 1307.329 | 27.185 | 27.453 | 36.876 | 28.001 | 4 | 1.6 | 1.4 | 0.7 | 0.1
2195 | 30/07/2025 10:18:11.194 | 96.768 | 77 | 100 | 70 | 53 | 30.483 | 9.286 | 7.07 | 133.046 | 29.586 | 28.383 | 27.997 | 601.928 | 25.997 | 26.927 | 1302.88 | 27.213 | 27.333 | 36.54 | 28.001 | 4.5 | 2.8 | 0.6 | 0 | 0.1
2196 | 30/07/2025 10:18:12.831 | 97.464 | 79 | 100 | 70 | 52 | 26.948 | 9.287 | 7.033 | 132.93 | 29.577 | 28.384 | 28.006 | 601.813 | 25.989 | 26.939 | 1306.906 | 27.2 | 27.441 | 36.578 | 28.001 | 4.5 | 2 | 0.6 | 0 | 0.1
2197 | 30/07/2025 10:18:14.465 | 97.632 | 78 | 100 | 70 | 52 | 31.1 | 9.31 | 7.034 | 132.845 | 29.579 | 28.401 | 28.006 | 602.071 | 26 | 26.931 | 1304.912 | 27.217 | 27.294 | 36.634 | 30.001 | 1.6 | 1.4 | 0.2 | 0.6 | 0.2
2198 | 30/07/2025 10:18:16.103 | 98.328 | 79 | 100 | 71 | 52 | 27.656 | 9.492 | 7.034 | 133.095 | 29.58 | 28.394 | 27.978 | 602.091 | 26.007 | 26.908 | 1291.05 | 27.184 | 27.44 | 36.971 | 30.001 | 1.6 | 1.4 | 0.2 | 0.6 | 0.2
2199 | 30/07/2025 10:18:17.740 | 98.28 | 80 | 100 | 71 | 52 | 28.527 | 9.334 | 7.062 | 133.179 | 29.583 | 28.397 | 27.97 | 602.141 | 26.002 | 26.914 | 1277.477 | 27.201 | 27.311 | 36.696 | 26.001 | 1.6 | 2.7 | 0.2 | 0.6 | 0.2
2200 | 30/07/2025 10:18:19.374 | 98.784 | 79 | 100 | 70 | 52 | 31.027 | 9.524 | 7.07 | 132.973 | 29.576 | 28.369 | 27.982 | 602.079 | 26.015 | 26.927 | 1279.429 | 27.232 | 27.453 | 36.6 | 24.001 | 2.3 | 3 | 1.6 | 0.5 | 0.2
2201 | 30/07/2025 10:18:21.009 | 99.264 | 81 | 100 | 71 | 52 | 29.884 | 9.503 | 7.07 | 133.178 | 29.584 | 28.394 | 28.007 | 601.917 | 26.04 | 26.922 | 1280.603 | 27.209 | 27.287 | 36.512 | 27.001 | 2.3 | 1.9 | 1.6 | 0.5 | 0.2
2202 | 30/07/2025 10:18:22.642 | 99.6 | 81 | 100 | 70 | 53 | 26.963 | 9.507 | 7.071 | 133.043 | 29.566 | 28.408 | 28.001 | 602.057 | 26.022 | 26.934 | 1292.328 | 27.197 | 27.464 | 36.726 | 24.001 | 2 | 1.1 | 0.6 | 0.5 | 0.1
2203 | 30/07/2025 10:18:24.278 | 99.864 | 82 | 100 | 70 | 52 | 30.799 | 9.573 | 7.071 | 133.43 | 29.592 | 28.395 | 27.983 | 602.059 | 26.019 | 26.949 | 1295.496 | 27.19 | 27.459 | 36.816 | 24.001 | 2 | 1.1 | 0.6 | 0.5 | 0.1
2204 | 30/07/2025 10:18:25.916 | 99.84 | 81 | 100 | 70 | 53 | 27.15 | 9.437 | 7.072 | 133.304 | 29.562 | 28.39 | 27.974 | 602.047 | 26.016 | 26.947 | 1292.642 | 27.221 | 27.481 | 36.796 | 28.001 | 2 | 2.9 | 0.6 | 0.5 | 0.1
2205 | 30/07/2025 10:18:27.551 | 100.32 | 83 | 100 | 70 | 52 | 29.169 | 9.505 | 7.088 | 133.157 | 29.549 | 28.373 | 27.972 | 601.961 | 26.008 | 26.941 | 1297.062 | 27.213 | 27.292 | 36.716 | 29.001 | 3.4 | 2.7 | 0 | 0.5 | 0.1
2206 | 30/07/2025 10:18:29.186 | 100.128 | 81 | 100 | 70 | 52 | 31.084 | 9.584 | 7.089 | 133.1 | 29.555 | 28.401 | 27.995 | 603.226 | 26.017 | 26.942 | 1304.27 | 27.206 | 27.425 | 36.426 | 28.001 | 3.4 | 2.2 | 0 | 0.5 | 0.1
2207 | 30/07/2025 10:18:30.822 | 100.344 | 80 | 100 | 70 | 52 | 29.265 | 9.505 | 7.101 | 132.969 | 29.536 | 28.405 | 27.986 | 603.224 | 26.019 | 26.948 | 1302.347 | 27.197 | 27.46 | 37.014 | 27.001 | 3.2 | 3.4 | 0.6 | 0.1 | 0.1
2208 | 30/07/2025 10:18:32.460 | 100.224 | 80 | 100 | 70 | 52 | 30.95 | 9.711 | 7.123 | 133.09 | 29.554 | 28.402 | 27.994 | 603.337 | 26.012 | 26.945 | 1299.94 | 27.177 | 27.447 | 36.755 | 27.001 | 3.2 | 1.7 | 0.6 | 0.1 | 0.1
2209 | 30/07/2025 10:18:34.096 | 99.672 | 80 | 100 | 71 | 52 | 30.453 | 9.466 | 7.068 | 133.165 | 29.562 | 28.387 | 27.953 | 603.2 | 26.014 | 26.949 | 1304.11 | 27.231 | 27.447 | 36.686 | 27.001 | 3.2 | 1.7 | 0.6 | 0.1 | 0.1
2210 | 30/07/2025 10:18:35.733 | 100.104 | 80 | 100 | 70 | 53 | 26.964 | 9.579 | 7.034 | 133.131 | 29.587 | 28.384 | 28.005 | 603.144 | 26.032 | 26.939 | 1314.688 | 27.213 | 27.284 | 36.592 | 25.001 | 2.7 | 2.3 | 0.7 | 0.5 | 0.1
2211 | 30/07/2025 10:18:37.368 | 99.624 | 79 | 100 | 71 | 52 | 29.709 | 9.685 | 7.071 | 133.103 | 29.581 | 28.417 | 28.002 | 603.186 | 26.014 | 26.946 | 1313.031 | 27.211 | 27.311 | 36.69 | 26.001 | 2.7 | 1 | 0.7 | 0.5 | 0.1
2212 | 30/07/2025 10:18:39.003 | 99.288 | 81 | 100 | 70 | 52 | 31.109 | 9.276 | 7.07 | 134.533 | 29.595 | 28.402 | 27.987 | 603.216 | 26.013 | 26.953 | 1320.941 | 27.177 | 27.447 | 36.767 | 27.001 | 2.1 | 2.7 | 1.2 | 1.1 | 0.1
2213 | 30/07/2025 10:18:40.640 | 98.736 | 80 | 100 | 72 | 52 | 28.742 | 9.42 | 7.071 | 134.69 | 29.594 | 28.395 | 27.967 | 603.431 | 26.006 | 26.934 | 1325.914 | 27.215 | 27.453 | 36.7 | 22.001 | 2.1 | 2 | 1.2 | 1.1 | 0.1
2214 | 30/07/2025 10:18:42.277 | 99.024 | 80 | 100 | 70 | 52 | 30.989 | 9.442 | 7.07 | 134.654 | 29.611 | 28.378 | 27.99 | 603.16 | 26.013 | 26.949 | 1317.118 | 27.222 | 27.453 | 36.712 | 22.001 | 2.1 | 2 | 1.2 | 1.1 | 0.1
2215 | 30/07/2025 10:18:43.911 | 99.24 | 80 | 100 | 71 | 52 | 29.943 | 9.433 | 7.069 | 134.57 | 29.584 | 28.394 | 28.004 | 603.373 | 26.002 | 26.918 | 1320.133 | 27.211 | 27.277 | 36.353 | 26.001 | 1.9 | 2.4 | 0.9 | 0.5 | 0.1
2216 | 30/07/2025 10:18:45.549 | 98.688 | 80 | 100 | 71 | 52 | 27.072 | 9.452 | 7.072 | 134.483 | 29.584 | 28.393 | 27.974 | 603.012 | 25.99 | 26.943 | 1322.108 | 27.209 | 27.444 | 36.784 | 30.001 | 1.9 | 2.7 | 0.9 | 0.5 | 0.1
2217 | 30/07/2025 10:18:47.185 | 98.64 | 79 | 100 | 70 | 51 | 30.327 | 9.432 | 7.09 | 134.602 | 29.588 | 28.398 | 27.972 | 603.266 | 26.011 | 26.908 | 1325.465 | 27.176 | 27.446 | 36.861 | 28.001 | 2 | 1.3 | 1.2 | 0 | 0.1
2218 | 30/07/2025 10:18:48.820 | 97.872 | 79 | 100 | 70 | 52 | 31.161 | 9.507 | 7.122 | 134.588 | 29.576 | 28.386 | 27.983 | 603.323 | 26.001 | 26.919 | 1309.796 | 27.221 | 27.41 | 36.587 | 26.001 | 2 | 2.9 | 1.2 | 0 | 0.1
2219 | 30/07/2025 10:18:50.453 | 98.736 | 79 | 100 | 71 | 52 | 29.238 | 9.576 | 7.122 | 134.721 | 29.601 | 28.378 | 28.019 | 603.32 | 26.004 | 26.908 | 1300.439 | 27.206 | 27.417 | 36.643 | 27.001 | 1.4 | 1.6 | 0 | 0.6 | 0.1
2220 | 30/07/2025 10:18:52.088 | 98.976 | 79 | 100 | 70 | 52 | 31.127 | 9.585 | 7.135 | 134.492 | 29.583 | 28.407 | 28.141 | 603.1 | 26.007 | 26.921 | 1296.647 | 27.227 | 27.324 | 36.407 | 27.001 | 1.4 | 1.6 | 0 | 0.6 | 0.1
2221 | 30/07/2025 10:18:53.723 | 99.288 | 81 | 99 | 70 | 52 | 29.363 | 9.508 | 7.089 | 134.815 | 29.57 | 28.393 | 28.138 | 603.083 | 26.011 | 26.928 | 1289.885 | 27.185 | 27.453 | 36.869 | 27.001 | 1.4 | 1.3 | 0 | 0.6 | 0.1
2222 | 30/07/2025 10:18:55.357 | 99.216 | 80 | 100 | 70 | 52 | 27.205 | 9.471 | 7.089 | 134.694 | 29.588 | 28.406 | 28.129 | 603.113 | 26.012 | 26.94 | 1312.874 | 27.192 | 27.46 | 36.556 | 30.001 | 3.7 | 1.1 | 1.2 | 1.1 | 0.1
2223 | 30/07/2025 10:18:56.990 | 99.024 | 81 | 100 | 71 | 51 | 30.638 | 9.288 | 7.089 | 134.603 | 29.558 | 28.372 | 28.119 | 603.099 | 26.012 | 26.951 | 1309.157 | 27.219 | 27.459 | 36.712 | 26.001 | 3.7 | 1.2 | 1.2 | 1.1 | 0.1
2224 | 30/07/2025 10:18:58.624 | 99.288 | 82 | 100 | 70 | 52 | 31.086 | 9.398 | 7.086 | 134.569 | 29.591 | 28.387 | 28.039 | 603.256 | 26.038 | 26.945 | 1311.65 | 27.208 | 27.442 | 36.51 | 27.001 | 2.1 | 2.1 | 1.2 | 0.9 | 0.1
2225 | 30/07/2025 10:19:00.262 | 99.552 | 81 | 100 | 72 | 52 | 29.716 | 9.284 | 7.091 | 134.502 | 29.561 | 28.4 | 28.03 | 603.1 | 26.024 | 26.968 | 1311.511 | 27.209 | 27.435 | 36.482 | 27.001 | 2.1 | 2.1 | 1.2 | 0.9 | 0.1
2226 | 30/07/2025 10:19:01.896 | 99 | 79 | 100 | 71 | 52 | 31.125 | 9.573 | 7.122 | 134.634 | 29.564 | 28.404 | 28.15 | 603.231 | 26.028 | 26.941 | 1307.182 | 27.184 | 27.312 | 36.717 | 28.001 | 2.1 | 2.7 | 1.2 | 0.9 | 0.1
2227 | 30/07/2025 10:19:03.530 | 98.664 | 78 | 100 | 70 | 52 | 28.681 | 9.581 | 7.092 | 134.654 | 29.541 | 28.402 | 28.117 | 603.2 | 26.009 | 26.933 | 1307.546 | 27.225 | 27.418 | 36.825 | 24.001 | 1.8 | 3.7 | 1.5 | 0.5 | 0.1
2228 | 30/07/2025 10:19:05.166 | 98.448 | 79 | 100 | 70 | 53 | 27.494 | 9.5 | 7.086 | 134.563 | 29.56 | 28.376 | 28.121 | 603.259 | 26.02 | 26.929 | 1306.731 | 27.211 | 27.298 | 36.636 | 24.001 | 1.8 | 2.4 | 1.5 | 0.5 | 0.1
2229 | 30/07/2025 10:19:06.802 | 98.976 | 81 | 100 | 70 | 51 | 30.815 | 9.725 | 7.086 | 134.545 | 29.555 | 28.4 | 28.144 | 603.252 | 26.009 | 26.946 | 1296.981 | 27.209 | 27.319 | 36.328 | 28.001 | 4.4 | 2.8 | 0.9 | 0 | 0.2
2230 | 30/07/2025 10:19:08.436 | 98.712 | 81 | 100 | 70 | 52 | 26.965 | 9.577 | 7.088 | 134.364 | 29.554 | 28.394 | 28.147 | 603.168 | 26.03 | 26.95 | 1299.441 | 27.197 | 27.287 | 36.663 | 32.001 | 4.4 | 2.2 | 0.9 | 0 | 0.2
2231 | 30/07/2025 10:19:10.070 | 98.208 | 79 | 100 | 71 | 51 | 30.129 | 9.288 | 7.07 | 134.862 | 29.562 | 28.398 | 28.141 | 603.299 | 25.998 | 26.936 | 1292.287 | 27.19 | 27.314 | 36.614 | 32.001 | 4.4 | 2.2 | 0.9 | 0 | 0.2
2232 | 30/07/2025 10:19:11.707 | 98.16 | 79 | 100 | 71 | 52 | 31.09 | 9.505 | 7.073 | 134.592 | 29.585 | 28.379 | 28.108 | 602.849 | 26.009 | 26.952 | 1277.689 | 27.228 | 27.344 | 36.841 | 27.001 | 2.3 | 2.2 | 0.6 | 0.5 | 0.2
2233 | 30/07/2025 10:19:13.341 | 97.992 | 80 | 100 | 71 | 54 | 28.072 | 9.493 | 7.069 | 134.647 | 29.582 | 28.376 | 28.155 | 603.373 | 26.019 | 26.938 | 1276.537 | 27.206 | 27.437 | 36.406 | 25.001 | 2.3 | 1.8 | 0.6 | 0.5 | 0.2
2234 | 30/07/2025 10:19:14.979 | 97.824 | 78 | 100 | 71 | 52 | 28.159 | 9.299 | 7.069 | 134.278 | 29.562 | 28.412 | 28.136 | 603.157 | 26.016 | 26.94 | 1287.792 | 27.223 | 27.444 | 36.511 | 26.001 | 2 | 1.1 | 0.9 | 0.9 | 0.2
2235 | 30/07/2025 10:19:16.614 | 97.992 | 78 | 100 | 70 | 52 | 29.316 | 9.164 | 7.069 | 134.598 | 29.598 | 28.406 | 28.161 | 603.17 | 26.012 | 26.931 | 1290.016 | 27.186 | 27.45 | 36.662 | 28.001 | 2 | 2.1 | 0.9 | 0.9 | 0.2
2236 | 30/07/2025 10:19:18.248 | 98.544 | 79 | 100 | 71 | 52 | 27.242 | 9.432 | 7.071 | 134.542 | 29.586 | 28.411 | 28.124 | 603.147 | 25.992 | 26.936 | 1282.659 | 27.211 | 27.331 | 36.705 | 28.001 | 2 | 2.1 | 0.9 | 0.9 | 0.2
2237 | 30/07/2025 10:19:19.885 | 97.968 | 78 | 100 | 70 | 53 | 30.594 | 9.507 | 7.072 | 134.676 | 29.596 | 28.385 | 28.132 | 603.1 | 26.018 | 26.94 | 1289.265 | 27.228 | 27.454 | 36.762 | 29.001 | 3.3 | 1.7 | 0.6 | 0.7 | 0.3
2238 | 30/07/2025 10:19:21.521 | 98.16 | 78 | 100 | 70 | 52 | 31.077 | 9.582 | 7.071 | 134.643 | 29.576 | 28.389 | 28.149 | 603.362 | 26.003 | 26.917 | 1294.516 | 27.21 | 27.441 | 36.4 | 25.001 | 3.3 | 2 | 0.6 | 0.7 | 0.3
2239 | 30/07/2025 10:19:23.155 | 98.736 | 78 | 100 | 70 | 51 | 27.685 | 9.43 | 7.073 | 134.461 | 29.569 | 28.401 | 28.119 | 603.097 | 25.991 | 26.915 | 1297.113 | 27.206 | 27.447 | 36.581 | 26.001 | 2.1 | 4.5 | 0.6 | 0.5 | 0.3
2240 | 30/07/2025 10:19:24.789 | 98.232 | 80 | 100 | 70 | 52 | 31.125 | 9.433 | 7.07 | 134.532 | 29.566 | 28.4 | 28.131 | 603.226 | 26.004 | 26.915 | 1291.899 | 27.186 | 27.466 | 36.646 | 20.001 | 2.1 | 3.2 | 0.6 | 0.5 | 0.3
2241 | 30/07/2025 10:19:26.424 | 98.208 | 78 | 100 | 71 | 52 | 28.872 | 9.285 | 7.072 | 134.647 | 29.575 | 28.391 | 28.121 | 603.046 | 26.02 | 26.924 | 1291.807 | 27.207 | 27.449 | 36.828 | 26.001 | 3 | 1.7 | 1.2 | 0.8 | 0.3
2242 | 30/07/2025 10:19:28.061 | 97.872 | 78 | 100 | 70 | 52 | 27.515 | 9.466 | 7.068 | 134.711 | 29.579 | 28.374 | 28.147 | 603.327 | 26.011 | 26.924 | 1299.608 | 27.217 | 27.441 | 36.636 | 26.001 | 3 | 1.7 | 1.2 | 0.8 | 0.3
2243 | 30/07/2025 10:19:29.696 | 98.448 | 80 | 99 | 70 | 52 | 30.907 | 9.287 | 7.088 | 134.363 | 29.561 | 28.404 | 28.128 | 603.331 | 26.019 | 26.941 | 1294.459 | 27.228 | 27.414 | 36.472 | 21.001 | 3 | 1.3 | 1.2 | 0.8 | 0.3
2244 | 30/07/2025 10:19:31.331 | 98.376 | 78 | 100 | 70 | 52 | 30.935 | 9.283 | 7.088 | 134.774 | 29.577 | 28.399 | 28.138 | 603.137 | 26.037 | 26.936 | 1290.191 | 27.189 | 27.458 | 36.587 | 27.001 | 2.2 | 2.2 | 1.1 | 0.5 | 0.2
2245 | 30/07/2025 10:19:32.965 | 98.664 | 79 | 100 | 71 | 52 | 27.347 | 9.217 | 7.071 | 134.669 | 29.563 | 28.397 | 28.129 | 603.248 | 26.173 | 26.947 | 1288.775 | 27.196 | 27.453 | 36.586 | 26.001 | 2.2 | 1.6 | 1.1 | 0.5 | 0.2
2246 | 30/07/2025 10:19:34.603 | 98.688 | 81 | 100 | 70 | 52 | 31.167 | 9.423 | 7.07 | 134.878 | 29.576 | 28.386 | 28.11 | 603.105 | 26.175 | 26.944 | 1296.564 | 27.212 | 27.448 | 36.7 | 25.001 | 2 | 2.2 | 0.6 | 0 | 0.1
2247 | 30/07/2025 10:19:36.239 | 99.264 | 81 | 100 | 71 | 52 | 28.182 | 9.435 | 7.062 | 134.514 | 29.55 | 28.375 | 28.142 | 603.196 | 26.155 | 26.938 | 1296.877 | 27.217 | 27.457 | 36.613 | 25.001 | 2 | 2.2 | 0.6 | 0 | 0.1
2248 | 30/07/2025 10:19:37.875 | 98.856 | 81 | 100 | 71 | 52 | 28.017 | 9.435 | 7.035 | 134.398 | 29.546 | 28.402 | 28.142 | 603.181 | 26.158 | 26.958 | 1299.511 | 27.204 | 27.437 | 36.492 | 25.001 | 2 | 1.2 | 0.6 | 0 | 0.1
2249 | 30/07/2025 10:19:39.509 | 98.64 | 82 | 100 | 70 | 52 | 30.963 | 9.284 | 7.036 | 134.72 | 29.563 | 28.395 | 28.16 | 603.247 | 26.165 | 26.942 | 1297.25 | 27.179 | 27.452 | 36.642 | 30.001 | 2.2 | 1.5 | 1.3 | 0.5 | 0.2
2250 | 30/07/2025 10:19:41.144 | 97.896 | 79 | 100 | 70 | 52 | 30.476 | 9.579 | 7.034 | 134.61 | 29.562 | 28.408 | 28.117 | 603.32 | 26.162 | 26.937 | 1297.083 | 27.219 | 27.456 | 36.814 | 30.001 | 2.2 | 1.1 | 1.3 | 0.5 | 0.2
2251 | 30/07/2025 10:19:42.781 | 97.368 | 78 | 100 | 71 | 52 | 27.012 | 9.431 | 7.069 | 134.657 | 29.575 | 28.379 | 28.135 | 603.039 | 26.17 | 26.954 | 1303.912 | 27.21 | 27.44 | 36.776 | 27.001 | 2.1 | 2.1 | 0.9 | 0 | 0.1
2252 | 30/07/2025 10:19:44.416 | 97.512 | 79 | 100 | 70 | 52 | 31.017 | 9.555 | 7.065 | 134.457 | 29.567 | 28.381 | 28.145 | 603.131 | 26.163 | 26.945 | 1300.809 | 27.229 | 27.438 | 36.325 | 28.001 | 2.1 | 2.6 | 0.9 | 0 | 0.1
2253 | 30/07/2025 10:19:46.049 | 97.08 | 76 | 100 | 71 | 53 | 27.597 | 9.701 | 7.041 | 134.364 | 29.596 | 28.397 | 28.138 | 603.214 | 26.183 | 26.949 | 1292.432 | 27.197 | 27.428 | 36.63 | 28.001 | 2.1 | 2.6 | 0.9 | 0 | 0.1
2254 | 30/07/2025 10:19:47.686 | 97.416 | 78 | 100 | 70 | 51 | 28.582 | 9.636 | 7.069 | 134.747 | 29.587 | 28.404 | 28.134 | 603.389 | 26.163 | 26.94 | 1292.378 | 27.187 | 27.466 | 36.816 | 23.001 | 2.1 | 1.8 | 1.8 | 0.5 | 0.1
2255 | 30/07/2025 10:19:49.320 | 97.248 | 79 | 100 | 70 | 52 | 31.055 | 9.506 | 7.072 | 134.694 | 29.587 | 28.387 | 28.104 | 603.087 | 26.156 | 26.935 | 1304.188 | 27.218 | 27.456 | 36.532 | 23.001 | 2.1 | 1.5 | 1.8 | 0.5 | 0.1
2256 | 30/07/2025 10:19:50.956 | 96.96 | 78 | 100 | 70 | 52 | 29.997 | 9.285 | 7.07 | 134.552 | 29.582 | 28.378 | 28.15 | 603.317 | 26.149 | 26.923 | 1292.507 | 27.208 | 27.439 | 36.572 | 29.001 | 4.8 | 3 | 1.2 | 0.7 | 0.2
2257 | 30/07/2025 10:19:52.593 | 96.864 | 79 | 100 | 70 | 53 | 30.894 | 9.29 | 7.07 | 134.398 | 29.578 | 28.389 | 28.138 | 603.1 | 26.137 | 26.924 | 1288.164 | 27.203 | 27.426 | 36.439 | 26.001 | 4.8 | 1.1 | 1.2 | 0.7 | 0.2
2258 | 30/07/2025 10:19:54.227 | 97.344 | 78 | 100 | 70 | 52 | 30.847 | 9.136 | 7.123 | 134.514 | 29.584 | 28.396 | 28.151 | 602.063 | 26.156 | 26.922 | 1295.38 | 27.189 | 27.455 | 36.616 | 26.001 | 4.8 | 1.1 | 1.2 | 0.7 | 0.2
2259 | 30/07/2025 10:19:55.864 | 97.416 | 79 | 100 | 71 | 52 | 27.176 | 9.581 | 7.07 | 134.561 | 29.569 | 28.403 | 28.114 | 601.854 | 26.15 | 26.933 | 1294.878 | 27.204 | 27.455 | 36.679 | 26.001 | 3 | 1.9 | 0.8 | 0.5 | 0.2
2260 | 30/07/2025 10:19:57.498 | 96.768 | 77 | 100 | 70 | 52 | 29.198 | 9.513 | 7.071 | 134.857 | 29.59 | 28.384 | 28.134 | 602.061 | 26.17 | 26.917 | 1296.937 | 27.215 | 27.453 | 36.696 | 23.001 | 3 | 2.3 | 0.8 | 0.5 | 0.2
2261 | 30/07/2025 10:19:59.131 | 96.96 | 78 | 100 | 70 | 52 | 31.124 | 9.438 | 7.069 | 134.561 | 29.566 | 28.387 | 28.16 | 602.17 | 26.143 | 26.916 | 1306.794 | 27.214 | 27.446 | 36.569 | 27.001 | 2.8 | 2 | 0.8 | 1 | 0.2
2262 | 30/07/2025 10:20:00.767 | 97.296 | 78 | 100 | 70 | 52 | 29.473 | 9.502 | 7.073 | 134.261 | 29.569 | 28.397 | 28.13 | 602.064 | 26.152 | 26.911 | 1312.459 | 27.203 | 27.442 | 36.863 | 29.001 | 2.5 | 0.8 | 1.8 | 0.8 | 0.2
2263 | 30/07/2025 10:20:02.403 | 97.344 | 77 | 100 | 71 | 52 | 31.026 | 9.301 | 7.071 | 134.625 | 29.563 | 28.411 | 28.142 | 602.114 | 26.162 | 26.922 | 1314.952 | 27.196 | 27.459 | 36.82 | 32.001 | 3.6 | 0.8 | 1.6 | 0.9 | 0.1
2264 | 30/07/2025 10:20:04.037 | 97.248 | 78 | 100 | 70 | 51 | 30.552 | 9.21 | 7.074 | 134.675 | 29.575 | 28.391 | 28.103 | 603.147 | 26.172 | 26.915 | 1314.603 | 27.196 | 27.452 | 36.779 | 32.001 | 3.6 | 0.8 | 1.6 | 0.9 | 0.1
2265 | 30/07/2025 10:20:05.676 | 97.2 | 77 | 100 | 70 | 51 | 27.038 | 9.284 | 7.069 | 134.641 | 29.578 | 28.373 | 28.139 | 603.362 | 26.169 | 26.938 | 1316.067 | 27.211 | 27.457 | 36.427 | 29.001 | 3.6 | 1.9 | 1.6 | 0.9 | 0.1
2266 | 30/07/2025 10:20:07.317 | 97.152 | 78 | 100 | 71 | 52 | 29.798 | 9.433 | 7.033 | 134.245 | 29.563 | 28.403 | 28.124 | 603.192 | 26.155 | 26.955 | 1306.827 | 27.23 | 27.444 | 36.352 | 30.001 | 2.3 | 2.1 | 0.9 | 0 | 0.1
2267 | 30/07/2025 10:20:08.954 | 96.264 | 77 | 100 | 70 | 52 | 31.16 | 9.43 | 7.071 | 134.7 | 29.569 | 28.399 | 28.13 | 603.121 | 26.164 | 26.942 | 1306.693 | 27.191 | 27.446 | 36.691 | 29.001 | 2.3 | 1.6 | 0.9 | 0 | 0.1
2268 | 30/07/2025 10:20:10.588 | 96.288 | 79 | 100 | 70 | 52 | 28.571 | 9.429 | 7.072 | 134.626 | 29.545 | 28.394 | 28.111 | 603.016 | 26.173 | 26.951 | 1306.796 | 27.195 | 27.451 | 36.754 | 27.001 | 1.3 | 2.7 | 1.2 | 0 | 0.2
2269 | 30/07/2025 10:20:12.223 | 96.48 | 77 | 100 | 71 | 52 | 31.092 | 9.429 | 7.07 | 134.63 | 29.572 | 28.395 | 28.112 | 603.176 | 26.164 | 26.954 | 1300.725 | 27.208 | 27.45 | 36.532 | 27.001 | 1.3 | 2.7 | 1.2 | 0 | 0.2
2270 | 30/07/2025 10:20:13.858 | 96.696 | 77 | 100 | 71 | 52 | 29.971 | 9.437 | 7.069 | 134.532 | 29.554 | 28.376 | 28.137 | 603.227 | 26.166 | 26.931 | 1301.741 | 27.223 | 27.453 | 36.58 | 26.001 | 1.3 | 1.9 | 1.2 | 0 | 0.2
2271 | 30/07/2025 10:20:15.493 | 97.056 | 79 | 100 | 70 | 52 | 27 | 9.379 | 7.073 | 134.471 | 29.559 | 28.402 | 28.143 | 603.164 | 26.165 | 26.934 | 1299.738 | 27.208 | 27.427 | 36.618 | 26.001 | 3.1 | 1.1 | 1.7 | 0.6 | 0.1
2272 | 30/07/2025 10:20:17.129 | 97.656 | 77 | 100 | 70 | 53 | 30.128 | 9.501 | 7.069 | 134.733 | 29.583 | 28.395 | 28.145 | 603.426 | 26.157 | 26.938 | 1300.166 | 27.184 | 27.455 | 36.766 | 22.001 | 3.1 | 1.4 | 1.7 | 0.6 | 0.1
2273 | 30/07/2025 10:20:18.764 | 97.992 | 80 | 100 | 71 | 52 | 31.174 | 9.43 | 7.071 | 134.565 | 29.57 | 28.39 | 28.112 | 602.972 | 26.156 | 26.938 | 1287.413 | 27.232 | 27.46 | 36.517 | 33.001 | 2.3 | 1.9 | 0.6 | 1 | 0.1
2274 | 30/07/2025 10:20:20.398 | 97.944 | 79 | 100 | 71 | 51 | 29.138 | 9.572 | 7.061 | 134.631 | 29.576 | 28.394 | 28.117 | 603.171 | 26.156 | 26.941 | 1288.55 | 27.212 | 27.456 | 36.586 | 29.001 | 2.3 | 2.2 | 0.6 | 1 | 0.1
2275 | 30/07/2025 10:20:22.033 | 98.376 | 80 | 100 | 70 | 52 | 31.135 | 9.569 | 7.037 | 134.553 | 29.575 | 28.376 | 28.141 | 603.158 | 26.154 | 26.949 | 1286.699 | 27.208 | 27.451 | 36.479 | 29.001 | 2.3 | 2.2 | 0.6 | 1 | 0.1
2276 | 30/07/2025 10:20:23.669 | 98.424 | 81 | 100 | 70 | 52 | 29.319 | 9.734 | 7.059 | 134.411 | 29.594 | 28.403 | 28.147 | 603.136 | 26.166 | 26.92 | 1285.225 | 27.203 | 27.438 | 36.655 | 22.001 | 5.4 | 1.2 | 1 | 0.8 | 0.1
2277 | 30/07/2025 10:20:25.303 | 98.208 | 81 | 100 | 70 | 52 | 27.216 | 9.498 | 7.04 | 134.682 | 29.564 | 28.392 | 28.135 | 603.182 | 26.152 | 26.931 | 1284.84 | 27.182 | 27.468 | 36.8 | 22.001 | 5.4 | 2 | 1 | 0.8 | 0.1
2278 | 30/07/2025 10:20:26.940 | 97.872 | 79 | 100 | 71 | 52 | 30.55 | 9.58 | 7.06 | 134.707 | 29.577 | 28.389 | 28.102 | 601.875 | 26.159 | 26.928 | 1285.957 | 27.206 | 27.442 | 36.672 | 23.001 | 2.1 | 2.4 | 0.6 | 1.1 | 0.1
2279 | 30/07/2025 10:20:28.576 | 97.44 | 80 | 100 | 70 | 52 | 27.049 | 9.579 | 7.06 | 134.54 | 29.578 | 28.391 | 28.133 | 601.915 | 26.142 | 26.927 | 1282.828 | 27.224 | 27.458 | 36.595 | 24.001 | 2.1 | 3.1 | 0.6 | 1.1 | 0.1
2280 | 30/07/2025 10:20:30.210 | 97.44 | 77 | 100 | 70 | 53 | 29.662 | 9.437 | 7.07 | 134.662 | 29.577 | 28.384 | 28.145 | 601.969 | 26.151 | 26.922 | 1297.018 | 27.208 | 27.426 | 36.382 | 24.001 | 2.1 | 3.1 | 0.6 | 1.1 | 0.1
2281 | 30/07/2025 10:20:31.847 | 97.08 | 79 | 100 | 70 | 52 | 31.136 | 9.432 | 7.033 | 134.463 | 29.57 | 28.404 | 28.143 | 602.081 | 26.138 | 26.912 | 1294.92 | 27.189 | 27.453 | 36.617 | 29.001 | 3.1 | 2.8 | 1 | 1 | 0.2
2282 | 30/07/2025 10:20:33.482 | 97.584 | 80 | 100 | 70 | 51 | 28.853 | 9.292 | 7.037 | 134.875 | 29.573 | 28.399 | 28.121 | 601.948 | 26.158 | 26.931 | 1296.072 | 27.191 | 27.46 | 36.724 | 26.001 | 3.1 | 2 | 1 | 1 | 0.2
2283 | 30/07/2025 10:20:35.119 | 97.488 | 78 | 100 | 71 | 52 | 27.59 | 9.127 | 7.033 | 134.822 | 29.582 | 28.386 | 28.122 | 602.548 | 26.173 | 26.927 | 1297.166 | 27.209 | 27.454 | 36.534 | 23.001 | 3.4 | 2.2 | 0.6 | 0.6 | 0.2
2284 | 30/07/2025 10:20:36.755 | 98.04 | 78 | 100 | 70 | 53 | 30.867 | 9.29 | 7.032 | 134.584 | 29.563 | 28.382 | 28.145 | 603.255 | 26.162 | 26.94 | 1300.91 | 27.222 | 27.449 | 36.551 | 27.001 | 1.9 | 1.9 | 1.2 | 0.5 | 0.2
2285 | 30/07/2025 10:20:38.389 | 98.544 | 81 | 100 | 70 | 52 | 27.084 | 9.395 | 7.057 | 134.505 | 29.585 | 28.397 | 28.145 | 603.439 | 26.175 | 26.927 | 1297.345 | 27.2 | 27.431 | 36.515 | 27.001 | 2.6 | 1.9 | 0.3 | 0.6 | 0.2
2286 | 30/07/2025 10:20:40.024 | 98.184 | 79 | 100 | 71 | 52 | 30.321 | 9.579 | 7.074 | 134.569 | 29.554 | 28.408 | 28.124 | 602.008 | 26.155 | 26.949 | 1301.814 | 27.205 | 27.458 | 36.765 | 27.001 | 2.6 | 1.9 | 0.3 | 0.6 | 0.2
2287 | 30/07/2025 10:20:41.660 | 98.184 | 81 | 100 | 71 | 52 | 31.177 | 9.286 | 7.072 | 134.68 | 29.566 | 28.394 | 28.121 | 601.932 | 26.175 | 26.947 | 1309.229 | 27.194 | 27.442 | 36.71 | 29.001 | 2.6 | 1.7 | 0.3 | 0.6 | 0.2
2288 | 30/07/2025 10:20:43.295 | 98.712 | 80 | 100 | 70 | 52 | 28.238 | 9.435 | 7.069 | 134.683 | 29.557 | 28.386 | 28.144 | 602.012 | 26.163 | 26.946 | 1311.998 | 27.212 | 27.448 | 36.612 | 32.001 | 2.7 | 1 | 2.2 | 0.8 | 0.2
2289 | 30/07/2025 10:20:44.931 | 98.424 | 79 | 100 | 70 | 52 | 28.073 | 9.511 | 7.072 | 134.492 | 29.555 | 28.389 | 28.135 | 602.07 | 26.161 | 26.952 | 1309.346 | 27.23 | 27.43 | 36.413 | 32.001 | 2.7 | 1.7 | 2.2 | 0.8 | 0.2
2290 | 30/07/2025 10:20:46.565 | 97.896 | 79 | 100 | 71 | 54 | 29.492 | 9.433 | 7.07 | 134.561 | 29.553 | 28.405 | 28.151 | 602.122 | 26.156 | 26.943 | 1307.127 | 27.214 | 27.439 | 36.347 | 31.001 | 2.2 | 1.4 | 1.2 | 1.4 | 0.3
2291 | 30/07/2025 10:20:48.206 | 98.616 | 78 | 100 | 71 | 52 | 27.197 | 9.431 | 7.074 | 134.627 | 29.541 | 28.397 | 28.114 | 602.005 | 26.149 | 26.947 | 1309.112 | 27.188 | 27.444 | 36.782 | 31.001 | 2.2 | 1.4 | 1.2 | 1.4 | 0.3
2292 | 30/07/2025 10:20:49.842 | 98.592 | 80 | 100 | 71 | 52 | 30.656 | 9.55 | 7.07 | 134.662 | 29.579 | 28.387 | 28.117 | 602 | 26.146 | 26.935 | 1307.052 | 27.199 | 27.461 | 36.565 | 28.001 | 2.2 | 1.7 | 1.2 | 1.4 | 0.3
2293 | 30/07/2025 10:20:51.477 | 98.304 | 80 | 99 | 71 | 52 | 31.186 | 9.442 | 7.07 | 134.469 | 29.564 | 28.38 | 28.141 | 602.075 | 26.158 | 26.943 | 1313.434 | 27.231 | 27.464 | 36.694 | 26.001 | 2.4 | 2.1 | 0.6 | 0.5 | 0.3
2294 | 30/07/2025 10:20:53.112 | 98.256 | 80 | 100 | 71 | 52 | 27.691 | 9.567 | 7.073 | 134.374 | 29.59 | 28.394 | 28.114 | 602.026 | 26.157 | 26.938 | 1294.851 | 27.207 | 27.419 | 36.433 | 30.001 | 2.4 | 2.3 | 0.6 | 0.5 | 0.3
2295 | 30/07/2025 10:20:54.748 | 97.248 | 78 | 100 | 71 | 51 | 31.149 | 9.355 | 7.073 | 134.36 | 29.58 | 28.421 | 28.135 | 602.193 | 26.143 | 26.937 | 1292.826 | 27.22 | 27.45 | 36.661 | 24.001 | 3.8 | 1.8 | 1.3 | 1.3 | 0.2
2296 | 30/07/2025 10:20:56.384 | 97.512 | 78 | 100 | 70 | 52 | 28.848 | 9.496 | 7.072 | 134.761 | 29.593 | 28.395 | 28.12 | 602.04 | 26.168 | 26.94 | 1290.492 | 27.182 | 27.465 | 36.814 | 26.001 | 3.8 | 1 | 1.3 | 1.3 | 0.2
2297 | 30/07/2025 10:20:58.018 | 97.224 | 78 | 100 | 71 | 52 | 27.5 | 9.298 | 7.058 | 134.62 | 29.567 | 28.395 | 28.107 | 601.965 | 26.144 | 26.932 | 1292.495 | 27.214 | 27.445 | 36.648 | 26.001 | 3.8 | 1 | 1.3 | 1.3 | 0.2
2298 | 30/07/2025 10:20:59.656 | 97.248 | 77 | 100 | 70 | 51 | 30.802 | 9.289 | 7.037 | 134.69 | 29.574 | 28.367 | 28.148 | 601.981 | 26.154 | 26.944 | 1301.414 | 27.219 | 27.448 | 36.633 | 30.001 | 2.3 | 1.1 | 1.1 | 1.1 | 0.3
2299 | 30/07/2025 10:21:01.296 | 97.872 | 79 | 100 | 71 | 52 | 30.87 | 9.293 | 7.071 | 134.324 | 29.572 | 28.401 | 28.147 | 602.078 | 26.134 | 26.915 | 1306.347 | 27.2 | 27.418 | 36.577 | 29.001 | 2.3 | 2 | 1.1 | 1.1 | 0.3
2300 | 30/07/2025 10:21:02.933 | 98.352 | 81 | 100 | 70 | 52 | 27.258 | 9.423 | 7.071 | 134.756 | 29.57 | 28.406 | 28.136 | 602.07 | 26.147 | 26.916 | 1314.47 | 27.191 | 27.47 | 36.878 | 29.001 | 3.4 | 1.6 | 0 | 0.6 | 0.3
2301 | 30/07/2025 10:21:04.572 | 98.352 | 79 | 100 | 70 | 52 | 31.179 | 9.305 | 7.07 | 134.647 | 29.58 | 28.393 | 28.14 | 602.131 | 26.142 | 26.907 | 1317.366 | 27.185 | 27.46 | 36.801 | 26.001 | 4.8 | 0.7 | 0.6 | 0 | 0.3
2302 | 30/07/2025 10:21:06.213 | 98.088 | 80 | 100 | 70 | 52 | 28.154 | 9.429 | 7.06 | 134.537 | 29.566 | 28.396 | 28.129 | 601.974 | 26.161 | 26.933 | 1301.36 | 27.238 | 27.457 | 36.793 | 26.001 | 4.8 | 0.7 | 0.6 | 0 | 0.3
2303 | 30/07/2025 10:21:07.847 | 97.92 | 80 | 100 | 71 | 52 | 28.085 | 9.435 | 7.033 | 134.656 | 29.576 | 28.384 | 28.135 | 601.954 | 26.178 | 26.92 | 1295.189 | 27.205 | 27.425 | 36.52 | 27.001 | 3.3 | 0.7 | 0.6 | 0 | 0.3
2304 | 30/07/2025 10:21:09.485 | 97.92 | 79 | 100 | 70 | 52 | 31.036 | 9.319 | 7.053 | 134.302 | 29.577 | 28.404 | 28.136 | 602.5 | 26.149 | 26.917 | 1321.076 | 27.201 | 27.459 | 36.665 | 26.001 | 3.3 | 1.4 | 0.6 | 0 | 0.3
2305 | 30/07/2025 10:21:11.122 | 98.376 | 81 | 100 | 71 | 52 | 30.579 | 9.29 | 7.061 | 134.788 | 29.574 | 28.398 | 28.105 | 601.991 | 26.164 | 26.946 | 1322.335 | 27.196 | 27.457 | 36.807 | 25.001 | 1.1 | 1.5 | 1.1 | 0.6 | 0.3
2306 | 30/07/2025 10:21:12.763 | 98.136 | 78 | 100 | 70 | 52 | 27.067 | 9.43 | 7.07 | 134.68 | 29.581 | 28.389 | 28.134 | 601.946 | 26.179 | 26.929 | 1326.874 | 27.214 | 27.455 | 36.772 | 28.001 | 1.1 | 2.3 | 1.1 | 0.6 | 0.3
2307 | 30/07/2025 10:21:14.397 | 97.92 | 80 | 100 | 70 | 53 | 31.145 | 9.432 | 7.07 | 134.529 | 29.565 | 28.368 | 28.124 | 602.051 | 26.173 | 26.94 | 1325.679 | 27.217 | 27.435 | 36.827 | 24.001 | 2.1 | 2.4 | 1.5 | 0.7 | 0.2
2308 | 30/07/2025 10:21:16.034 | 98.76 | 80 | 100 | 71 | 53 | 27.648 | 9.506 | 7.07 | 134.445 | 29.571 | 28.392 | 28.165 | 602.316 | 26.158 | 26.935 | 1317.622 | 27.198 | 27.431 | 36.424 | 24.001 | 2.1 | 2.4 | 1.5 | 0.7 | 0.2
2309 | 30/07/2025 10:21:17.672 | 98.328 | 79 | 100 | 70 | 52 | 28.697 | 9.292 | 7.119 | 134.493 | 29.55 | 28.412 | 28.149 | 601.955 | 26.163 | 26.962 | 1309.707 | 27.21 | 27.464 | 36.766 | 26.001 | 2.1 | 1.4 | 1.5 | 0.7 | 0.2
2310 | 30/07/2025 10:21:19.309 | 98.4 | 80 | 100 | 70 | 52 | 31.089 | 9.291 | 7.097 | 134.714 | 29.553 | 28.396 | 28.125 | 601.94 | 26.166 | 26.937 | 1302.203 | 27.187 | 27.445 | 36.853 | 30.001 | 2.3 | 2.2 | 0.7 | 0.5 | 0.3
2311 | 30/07/2025 10:21:20.945 | 98.4 | 80 | 100 | 69 | 52 | 30.065 | 9.523 | 7.07 | 134.494 | 29.56 | 28.383 | 28.127 | 601.942 | 26.155 | 26.944 | 1293.408 | 27.215 | 27.461 | 36.678 | 27.001 | 2.3 | 2.8 | 0.7 | 0.5 | 0.3
2312 | 30/07/2025 10:21:22.580 | 98.64 | 81 | 100 | 71 | 52 | 30.885 | 9.313 | 7.069 | 134.675 | 29.655 | 28.377 | 28.146 | 601.974 | 26.175 | 26.936 | 1296.995 | 27.204 | 27.44 | 36.722 | 28.001 | 2.2 | 1.9 | 0.6 | 0.6 | 0.3
2313 | 30/07/2025 10:21:24.216 | 98.112 | 79 | 100 | 71 | 52 | 30.986 | 9.288 | 7.072 | 134.472 | 29.563 | 28.409 | 28.152 | 601.931 | 26.157 | 26.936 | 1291.955 | 27.214 | 27.44 | 36.354 | 28.001 | 2.2 | 1.9 | 0.6 | 0.6 | 0.3
2314 | 30/07/2025 10:21:25.851 | 98.088 | 79 | 100 | 69 | 52 | 27.336 | 9.283 | 7.074 | 134.702 | 29.567 | 28.398 | 28.123 | 602.066 | 26.158 | 26.951 | 1289.458 | 27.189 | 27.456 | 36.706 | 27.001 | 2.2 | 1 | 0.6 | 0.6 | 0.3
2315 | 30/07/2025 10:21:27.487 | 98.616 | 79 | 100 | 70 | 52 | 29.239 | 9.569 | 7.07 | 134.764 | 29.592 | 28.394 | 28.124 | 602.108 | 26.162 | 26.929 | 1287.691 | 27.204 | 27.454 | 36.632 | 30.001 | 2.7 | 2.1 | 0.6 | 0.5 | 0.2
2316 | 30/07/2025 10:21:29.125 | 98.592 | 80 | 100 | 70 | 52 | 31.128 | 9.433 | 7.07 | 134.536 | 29.668 | 28.376 | 28.144 | 601.807 | 26.157 | 26.937 | 1289.653 | 27.231 | 27.457 | 36.598 | 26.001 | 2.7 | 2.1 | 0.6 | 0.5 | 0.2
2317 | 30/07/2025 10:21:30.760 | 98.424 | 78 | 100 | 70 | 52 | 29.467 | 9.287 | 7.071 | 134.55 | 29.727 | 28.386 | 28.132 | 602.096 | 26.161 | 26.941 | 1289.627 | 27.208 | 27.422 | 36.399 | 29.001 | 2.1 | 2.1 | 1.3 | 0.6 | 0.2
2318 | 30/07/2025 10:21:32.395 | 98.64 | 80 | 100 | 70 | 53 | 31.071 | 9.4 | 7.072 | 134.427 | 29.707 | 28.405 | 28.127 | 602.008 | 26.15 | 26.946 | 1292.392 | 27.23 | 27.443 | 36.695 | 28.001 | 2.1 | 1.6 | 1.3 | 0.6 | 0.2
2319 | 30/07/2025 10:21:34.029 | 98.688 | 80 | 100 | 72 | 52 | 30.556 | 9.287 | 7.072 | 134.784 | 29.739 | 28.398 | 28.134 | 602.008 | 26.151 | 26.926 | 1294.596 | 27.178 | 27.453 | 36.807 | 28.001 | 2.1 | 1.6 | 1.3 | 0.6 | 0.2
2320 | 30/07/2025 10:21:35.667 | 98.928 | 80 | 100 | 70 | 52 | 27.116 | 9.359 | 7.071 | 134.505 | 29.73 | 28.391 | 28.118 | 601.984 | 26.148 | 26.931 | 1294.254 | 27.223 | 27.463 | 36.417 | 32.001 | 4.3 | 1.6 | 0.9 | 0.8 | 0.2
2321 | 30/07/2025 10:21:37.302 | 98.424 | 81 | 100 | 69 | 52 | 29.667 | 9.509 | 7.07 | 134.465 | 29.732 | 28.376 | 28.115 | 601.69 | 26.149 | 26.917 | 1281.809 | 27.214 | 27.431 | 36.599 | 32.001 | 4.3 | 2.2 | 0.9 | 0.8 | 0.2
2322 | 30/07/2025 10:21:38.938 | 98.976 | 81 | 100 | 70 | 52 | 31.259 | 9.504 | 7.069 | 134.579 | 29.734 | 28.407 | 28.146 | 602.244 | 26.151 | 26.915 | 1292.557 | 27.208 | 27.424 | 36.439 | 31.001 | 3.3 | 1.2 | 0.1 | 0.5 | 0.2
2323 | 30/07/2025 10:21:40.572 | 98.832 | 80 | 100 | 70 | 52 | 28.558 | 9.428 | 7.071 | 134.442 | 29.716 | 28.4 | 28.125 | 601.866 | 26.144 | 26.929 | 1287.921 | 27.189 | 27.447 | 36.736 | 30.001 | 3.3 | 1.4 | 0.1 | 0.5 | 0.2
2324 | 30/07/2025 10:21:42.210 | 98.592 | 79 | 100 | 71 | 52 | 31.134 | 9.58 | 7.071 | 134.522 | 29.731 | 28.399 | 28.134 | 602.053 | 26.145 | 26.904 | 1281.173 | 27.175 | 27.456 | 36.715 | 30.001 | 3.3 | 1.4 | 0.1 | 0.5 | 0.2
2325 | 30/07/2025 10:21:43.849 | 98.736 | 78 | 100 | 70 | 52 | 30.084 | 9.285 | 7.071 | 134.562 | 29.705 | 28.382 | 28.109 | 601.966 | 26.156 | 26.925 | 1283.525 | 27.238 | 27.453 | 36.598 | 30.001 | 2.8 | 1.9 | 0.1 | 0 | 0.2
2326 | 30/07/2025 10:21:45.482 | 98.088 | 80 | 100 | 70 | 53 | 27.08 | 9.504 | 7.032 | 134.793 | 29.735 | 28.377 | 28.154 | 601.944 | 26.19 | 26.935 | 1287.154 | 27.207 | 27.434 | 36.473 | 28.001 | 2.8 | 1.8 | 0.1 | 0 | 0.2
2327 | 30/07/2025 10:21:47.117 | 97.944 | 78 | 100 | 70 | 52 | 30.247 | 9.577 | 7.035 | 134.299 | 29.701 | 28.411 | 28.147 | 602.074 | 26.16 | 26.944 | 1294.783 | 27.206 | 27.447 | 36.478 | 25.001 | 3.2 | 2.2 | 0.6 | 0.5 | 0.2
2328 | 30/07/2025 10:21:48.751 | 98.4 | 79 | 100 | 70 | 52 | 27.243 | 9.481 | 7.037 | 134.588 | 29.728 | 28.397 | 28.146 | 602.111 | 26.177 | 26.948 | 1296.902 | 27.176 | 27.467 | 36.563 | 28.001 | 3.2 | 1.7 | 0.6 | 0.5 | 0.2
2329 | 30/07/2025 10:21:50.386 | 99 | 79 | 100 | 70 | 52 | 29.252 | 9.441 | 7.067 | 134.535 | 29.702 | 28.394 | 28.113 | 602.05 | 26.162 | 26.944 | 1284.932 | 27.199 | 27.457 | 36.692 | 26.001 | 3.1 | 1.9 | 0.5 | 0.2 | 0.1
2330 | 30/07/2025 10:21:52.022 | 99.168 | 81 | 100 | 71 | 52 | 31.139 | 9.429 | 7.071 | 134.654 | 29.702 | 28.373 | 28.114 | 601.881 | 26.177 | 26.953 | 1282.307 | 27.217 | 27.445 | 36.864 | 26.001 | 3.1 | 1.9 | 0.5 | 0.2 | 0.1
2331 | 30/07/2025 10:21:53.659 | 98.832 | 80 | 100 | 70 | 52 | 29.495 | 9.32 | 7.086 | 134.576 | 29.714 | 28.397 | 28.156 | 602.098 | 26.164 | 26.942 | 1277.334 | 27.21 | 27.435 | 36.331 | 29.001 | 3.1 | 1.3 | 0.5 | 0.2 | 0.1
2332 | 30/07/2025 10:21:55.296 | 98.832 | 80 | 100 | 71 | 51 | 27.237 | 9.287 | 7.07 | 134.47 | 29.69 | 28.41 | 28.134 | 602.106 | 26.157 | 26.949 | 1286.924 | 27.217 | 27.452 | 36.76 | 29.001 | 2.2 | 1.1 | 1.5 | 0.6 | 0.1
2333 | 30/07/2025 10:21:56.931 | 98.28 | 80 | 100 | 70 | 52 | 30.652 | 9.286 | 7.071 | 134.809 | 29.732 | 28.398 | 28.123 | 602.09 | 26.171 | 26.945 | 1289.754 | 27.19 | 27.454 | 36.563 | 26.001 | 2.2 | 1.5 | 1.5 | 0.6 | 0.1
2334 | 30/07/2025 10:21:58.565 | 99 | 80 | 100 | 70 | 52 | 27.108 | 9.487 | 7.071 | 134.508 | 29.717 | 28.391 | 28.122 | 601.846 | 26.164 | 26.955 | 1286.933 | 27.218 | 27.46 | 36.672 | 26.001 | 3.4 | 1.2 | 0.6 | 0.5 | 0.1
2335 | 30/07/2025 10:22:00.202 | 99.168 | 80 | 100 | 72 | 52 | 29.821 | 9.29 | 7.066 | 134.616 | 29.747 | 28.373 | 28.139 | 601.87 | 26.167 | 26.932 | 1287.845 | 27.209 | 27.449 | 36.773 | 26.001 | 3.4 | 1.2 | 0.6 | 0.5 | 0.1
2336 | 30/07/2025 10:22:01.837 | 99 | 80 | 100 | 70 | 52 | 31.223 | 9.291 | 7.034 | 134.593 | 29.717 | 28.408 | 28.159 | 602.216 | 26.155 | 26.931 | 1297.486 | 27.21 | 27.444 | 36.57 | 34.001 | 3.4 | 1 | 0.6 | 0.5 | 0.1
2337 | 30/07/2025 10:22:03.474 | 98.856 | 81 | 99 | 70 | 53 | 28.929 | 9.429 | 7.035 | 134.654 | 29.728 | 28.401 | 28.117 | 600.58 | 26.158 | 26.941 | 1286.965 | 27.175 | 27.455 | 36.688 | 30.001 | 3.3 | 1.3 | 0.6 | 0.9 | 0.1
2338 | 30/07/2025 10:22:05.111 | 98.952 | 80 | 100 | 71 | 53 | 27.644 | 9.45 | 7.045 | 134.598 | 29.731 | 28.397 | 28.116 | 600.622 | 26.156 | 26.925 | 1287.275 | 27.196 | 27.45 | 36.686 | 22.001 | 3.3 | 2.8 | 0.6 | 0.9 | 0.1
2339 | 30/07/2025 10:22:06.746 | 99.36 | 83 | 100 | 70 | 53 | 30.091 | 9.505 | 7.071 | 134.693 | 29.732 | 28.389 | 28.111 | 600.559 | 26.161 | 26.931 | 1287.097 | 27.204 | 27.451 | 36.714 | 27.001 | 2.4 | 1.9 | 0.6 | 1 | 0.1
2340 | 30/07/2025 10:22:08.381 | 98.76 | 81 | 100 | 70 | 52 | 27.105 | 9.331 | 7.076 | 134.618 | 29.736 | 28.381 | 28.14 | 600.457 | 26.142 | 26.937 | 1294.278 | 27.207 | 27.438 | 36.382 | 25.001 | 2.4 | 1.6 | 0.6 | 1 | 0.1
2341 | 30/07/2025 10:22:10.017 | 98.712 | 80 | 100 | 70 | 51 | 30.19 | 9.433 | 7.073 | 134.324 | 29.715 | 28.391 | 28.144 | 600.601 | 26.145 | 26.939 | 1292.459 | 27.209 | 27.434 | 36.57 | 25.001 | 2.4 | 1.6 | 0.6 | 1 | 0.1
2342 | 30/07/2025 10:22:11.654 | 98.64 | 80 | 100 | 70 | 52 | 31.294 | 9.445 | 7.07 | 134.83 | 29.741 | 28.397 | 28.129 | 600.753 | 26.15 | 26.919 | 1287.373 | 27.172 | 27.465 | 36.583 | 31.001 | 2.3 | 2.4 | 1.3 | 0 | 0.2
2343 | 30/07/2025 10:22:13.292 | 98.736 | 78 | 100 | 70 | 52 | 28.396 | 9.43 | 7.07 | 134.616 | 29.716 | 28.387 | 28.112 | 599.316 | 26.143 | 26.913 | 1284.591 | 27.219 | 27.466 | 36.704 | 30.001 | 2.3 | 1.5 | 1.3 | 0 | 0.2
2344 | 30/07/2025 10:22:14.928 | 98.112 | 79 | 100 | 71 | 50 | 28.044 | 9.432 | 7.125 | 134.46 | 29.714 | 28.372 | 28.139 | 598.001 | 26.158 | 26.924 | 1279.435 | 27.213 | 27.445 | 36.64 | 26.001 | 1.6 | 1.8 | 1.3 | 0.5 | 0.2
2345 | 30/07/2025 10:22:16.561 | 98.952 | 80 | 100 | 70 | 52 | 29.564 | 9.435 | 7.122 | 134.512 | 29.702 | 28.389 | 28.143 | 597.832 | 26.158 | 26.916 | 1288.359 | 27.216 | 27.426 | 36.432 | 28.001 | 2.2 | 1.2 | 0.6 | 0 | 0.2
2346 | 30/07/2025 10:22:18.197 | 98.88 | 80 | 100 | 70 | 53 | 27.273 | 9.29 | 7.089 | 134.564 | 29.713 | 28.392 | 28.131 | 598.143 | 26.175 | 26.927 | 1288.084 | 27.203 | 27.449 | 36.74 | 28.001 | 2.2 | 1.2 | 0.6 | 0 | 0.2
2347 | 30/07/2025 10:22:19.831 | 98.832 | 80 | 100 | 70 | 52 | 30.634 | 9.506 | 7.072 | 134.649 | 29.715 | 28.401 | 28.151 | 598.073 | 26.157 | 26.939 | 1300.415 | 27.178 | 27.461 | 36.637 | 25.001 | 2 | 1.2 | 0.9 | 0.5 | 0.2
2348 | 30/07/2025 10:22:21.466 | 99.216 | 80 | 100 | 70 | 52 | 31.198 | 9.581 | 7.07 | 134.55 | 29.704 | 28.387 | 28.125 | 598.177 | 26.168 | 26.944 | 1314.159 | 27.221 | 27.459 | 36.691 | 29.001 | 2 | 2 | 0.9 | 0.5 | 0.2
2349 | 30/07/2025 10:22:23.105 | 98.592 | 79 | 100 | 69 | 52 | 27.659 | 9.434 | 7.045 | 134.594 | 29.732 | 28.384 | 28.164 | 598.026 | 26.165 | 26.957 | 1311.923 | 27.205 | 27.443 | 36.52 | 25.001 | 2.2 | 1.3 | 1.8 | 0.6 | 0.2
2350 | 30/07/2025 10:22:24.740 | 97.584 | 77 | 100 | 71 | 52 | 28.624 | 9.582 | 7.034 | 134.171 | 29.7 | 28.414 | 28.146 | 598.179 | 26.16 | 26.944 | 1307.158 | 27.211 | 27.461 | 36.528 | 25.001 | 3.3 | 0.8 | 1.6 | 0.1 | 0.2
2351 | 30/07/2025 10:22:26.375 | 97.776 | 79 | 100 | 71 | 52 | 28.749 | 9.668 | 7.032 | 134.715 | 29.703 | 28.4 | 28.139 | 599.48 | 26.163 | 26.928 | 1309.286 | 27.185 | 27.446 | 36.788 | 24.001 | 3.6 | 0.8 | 0.2 | 0.9 | 0.2
2352 | 30/07/2025 10:22:28.012 | 97.416 | 78 | 100 | 71 | 52 | 27.564 | 9.445 | 7.034 | 134.641 | 29.694 | 28.408 | 28.114 | 599.72 | 26.157 | 26.94 | 1314.772 | 27.211 | 27.453 | 36.692 | 24.001 | 3.6 | 0.8 | 0.2 | 0.9 | 0.2
2353 | 30/07/2025 10:22:29.646 | 96.984 | 77 | 100 | 70 | 52 | 30.856 | 9.433 | 7.033 | 134.881 | 29.702 | 28.374 | 28.123 | 600.564 | 26.163 | 26.944 | 1316.669 | 27.221 | 27.451 | 36.557 | 25.001 | 2.8 | 1.1 | 1.8 | 0.7 | 0.3
2354 | 30/07/2025 10:22:31.281 | 96.96 | 78 | 100 | 70 | 52 | 30.936 | 9.509 | 7.054 | 134.576 | 29.7 | 28.389 | 28.148 | 600.5 | 26.155 | 26.939 | 1317.359 | 27.208 | 27.445 | 36.407 | 22.001 | 1.4 | 1.1 | 0.5 | 0.1 | 0.3
2355 | 30/07/2025 10:22:32.918 | 96.72 | 78 | 100 | 71 | 52 | 27.417 | 9.282 | 7.062 | 134.367 | 29.722 | 28.397 | 28.134 | 599.529 | 26.156 | 26.955 | 1306.81 | 27.216 | 27.449 | 36.613 | 24.001 | 2.4 | 0.6 | 0.6 | 0.8 | 0.3
2356 | 30/07/2025 10:22:34.555 | 96.24 | 77 | 100 | 70 | 52 | 31.209 | 9.289 | 7.07 | 134.579 | 29.709 | 28.397 | 28.128 | 599.364 | 26.149 | 26.925 | 1309.493 | 27.186 | 27.454 | 36.642 | 29.001 | 1.9 | 0.6 | 0 | 0.9 | 0.2
2357 | 30/07/2025 10:22:36.189 | 96.264 | 77 | 100 | 70 | 52 | 28.357 | 9.504 | 7.058 | 134.675 | 29.729 | 28.396 | 28.104 | 598.002 | 26.159 | 26.943 | 1311.726 | 27.211 | 27.447 | 36.66 | 29.001 | 1.9 | 0.6 | 0 | 0.9 | 0.2
2358 | 30/07/2025 10:22:37.825 | 96.552 | 78 | 100 | 70 | 52 | 28.143 | 9.434 | 7.032 | 134.626 | 29.743 | 28.375 | 28.135 | 599.303 | 26.161 | 26.928 | 1311.812 | 27.211 | 27.443 | 36.541 | 31.001 | 3.3 | 1.6 | 1.3 | 0.5 | 0.2
2359 | 30/07/2025 10:22:39.460 | 96.168 | 77 | 100 | 70 | 52 | 31.081 | 9.443 | 7.054 | 134.517 | 29.719 | 28.404 | 28.141 | 599.253 | 26.147 | 26.927 | 1317.205 | 27.218 | 27.439 | 36.317 | 31.001 | 3.2 | 1.6 | 1.2 | 0.1 | 0.2
2360 | 30/07/2025 10:22:41.095 | 96.768 | 77 | 100 | 71 | 52 | 30.61 | 9.499 | 7.033 | 134.565 | 29.728 | 28.39 | 28.131 | 600.584 | 26.155 | 26.935 | 1309.552 | 27.187 | 27.457 | 36.709 | 31.001 | 2.6 | 2.4 | 1 | 0 | 0.2
2361 | 30/07/2025 10:22:42.730 | 96.456 | 79 | 100 | 69 | 51 | 27.136 | 9.449 | 7.032 | 134.679 | 29.715 | 28.405 | 28.138 | 600.522 | 26.141 | 26.926 | 1316.284 | 27.185 | 27.462 | 36.617 | 26.001 | 3 | 2.4 | 1.8 | 0.5 | 0.1
2362 | 30/07/2025 10:22:44.366 | 97.272 | 78 | 100 | 70 | 51 | 31.234 | 9.433 | 7.06 | 134.823 | 29.728 | 28.385 | 28.116 | 600.579 | 26.156 | 26.923 | 1314.856 | 27.213 | 27.45 | 36.766 | 26.001 | 3 | 1.7 | 1.8 | 0.5 | 0.1
2363 | 30/07/2025 10:22:46.003 | 97.608 | 78 | 100 | 71 | 53 | 27.807 | 9.51 | 7.068 | 134.657 | 29.722 | 28.377 | 28.14 | 600.45 | 26.128 | 26.911 | 1309.163 | 27.215 | 27.457 | 36.424 | 26.001 | 3 | 1.7 | 1.8 | 0.5 | 0.1
2364 | 30/07/2025 10:22:47.637 | 97.752 | 78 | 100 | 70 | 53 | 28.615 | 9.433 | 7.073 | 134.298 | 29.721 | 28.403 | 28.119 | 600.496 | 26.152 | 26.92 | 1306.779 | 27.208 | 27.438 | 36.616 | 28.001 | 3.1 | 1.6 | 0.6 | 0.1 | 0.2
2365 | 30/07/2025 10:22:49.274 | 97.512 | 78 | 100 | 70 | 52 | 31.113 | 9.304 | 7.069 | 134.775 | 29.731 | 28.399 | 28.134 | 600.718 | 26.16 | 26.907 | 1300.231 | 27.17 | 27.459 | 36.706 | 25.001 | 3.1 | 2.3 | 0.6 | 0.1 | 0.2
2366 | 30/07/2025 10:22:50.912 | 97.848 | 80 | 100 | 69 | 52 | 30.143 | 9.43 | 7.071 | 134.739 | 29.697 | 28.397 | 28.103 | 599.396 | 26.154 | 26.919 | 1299.363 | 27.224 | 27.458 | 36.643 | 25.001 | 1.9 | 3.1 | 0.6 | 0 | 0.2
2367 | 30/07/2025 10:22:52.548 | 98.136 | 80 | 100 | 70 | 52 | 30.929 | 9.429 | 7.078 | 134.844 | 29.723 | 28.387 | 28.119 | 599.444 | 26.164 | 26.923 | 1297.271 | 27.218 | 27.443 | 36.611 | 27.001 | 1.9 | 3.3 | 0.6 | 0 | 0.2
2368 | 30/07/2025 10:22:54.182 | 97.992 | 80 | 100 | 71 | 52 | 31.008 | 9.287 | 7.123 | 134.416 | 29.713 | 28.374 | 28.147 | 599.266 | 26.166 | 26.948 | 1293.672 | 27.223 | 27.444 | 36.296 | 27.001 | 1.9 | 3.3 | 0.6 | 0 | 0.2
2369 | 30/07/2025 10:22:55.818 | 97.8 | 78 | 100 | 71 | 51 | 27.307 | 9.568 | 7.085 | 134.449 | 29.709 | 28.396 | 28.139 | 599.435 | 26.163 | 26.931 | 1306.013 | 27.203 | 27.445 | 36.779 | 29.001 | 3.4 | 2.3 | 0.7 | 0.1 | 0.2
2370 | 30/07/2025 10:22:57.452 | 97.44 | 78 | 100 | 70 | 52 | 29.187 | 9.431 | 7.07 | 134.792 | 29.706 | 28.399 | 28.138 | 600.649 | 26.153 | 26.944 | 1304.572 | 27.186 | 27.48 | 36.631 | 28.001 | 3.4 | 2 | 0.7 | 0.1 | 0.2
2371 | 30/07/2025 10:22:59.131 | 97.464 | 79 | 100 | 70 | 53 | 31.17 | 9.486 | 7.072 | 134.508 | 29.696 | 28.386 | 28.111 | 600.318 | 26.166 | 26.971 | 1305.446 | 27.217 | 27.461 | 36.715 | 31.001 | 2.1 | 1.2 | 0.6 | 0 | 0.2
2372 | 30/07/2025 10:23:00.766 | 97.896 | 78 | 100 | 70 | 52 | 29.384 | 9.434 | 7.069 | 134.56 | 29.697 | 28.375 | 28.153 | 599.374 | 26.179 | 26.939 | 1305.069 | 27.205 | 27.44 | 36.61 | 26.001 | 3.5 | 2.2 | 1.3 | 0.5 | 0.2
2373 | 30/07/2025 10:23:02.402 | 97.632 | 78 | 100 | 70 | 53 | 31.063 | 9.494 | 7.073 | 134.649 | 29.699 | 28.393 | 28.131 | 599.23 | 26.165 | 26.94 | 1309.299 | 27.202 | 27.432 | 36.323 | 26.001 | 3 | 2.2 | 0.9 | 0.6 | 0.2
2374 | 30/07/2025 10:23:04.271 | 97.608 | 77 | 100 | 70 | 51 | 30.594 | 9.436 | 7.087 | 134.584 | 29.721 | 28.402 | 28.152 | 600.602 | 26.159 | 26.935 | 1312.841 | 27.195 | 27.453 | 36.732 | 26.001 | 3 | 2.2 | 0.9 | 0.6 | 0.2
2375 | 30/07/2025 10:23:05.906 | 97.728 | 78 | 100 | 71 | 52 | 27.105 | 9.51 | 7.088 | 134.622 | 29.708 | 28.414 | 28.116 | 600.535 | 26.156 | 26.95 | 1305.127 | 27.21 | 27.469 | 36.652 | 28.001 | 3 | 1.2 | 0.9 | 0.6 | 0.2
2376 | 30/07/2025 10:23:07.541 | 98.016 | 78 | 100 | 70 | 52 | 29.703 | 9.432 | 7.088 | 134.744 | 29.733 | 28.376 | 28.114 | 600.545 | 26.17 | 26.947 | 1306.709 | 27.218 | 27.446 | 36.655 | 27.001 | 2.4 | 2.5 | 0 | 0.5 | 0.3
2377 | 30/07/2025 10:23:09.177 | 98.016 | 80 | 100 | 70 | 53 | 31.182 | 9.418 | 7.12 | 134.553 | 29.722 | 28.391 | 28.157 | 600.523 | 26.157 | 26.938 | 1304.204 | 27.205 | 27.44 | 36.445 | 30.001 | 2.2 | 2.6 | 0.7 | 0.5 | 0.3
2378 | 30/07/2025 10:23:10.814 | 98.256 | 79 | 100 | 71 | 52 | 28.974 | 9.14 | 7.125 | 134.607 | 29.723 | 28.396 | 28.129 | 600.411 | 26.152 | 26.942 | 1306.81 | 27.209 | 27.447 | 36.585 | 26.001 | 3.3 | 2.6 | 2.5 | 0 | 0.3
2379 | 30/07/2025 10:23:12.450 | 97.8 | 79 | 100 | 70 | 53 | 27.618 | 9.496 | 7.122 | 134.775 | 29.736 | 28.398 | 28.124 | 600.803 | 26.154 | 26.935 | 1299.914 | 27.174 | 27.458 | 36.558 | 26.001 | 3.3 | 1.9 | 2.5 | 0 | 0.3
2380 | 30/07/2025 10:23:14.086 | 97.464 | 79 | 100 | 71 | 52 | 30.126 | 9.476 | 7.079 | 134.69 | 29.72 | 28.398 | 28.099 | 600.668 | 26.156 | 26.944 | 1296.867 | 27.206 | 27.45 | 36.531 | 26.001 | 3.3 | 1.9 | 2.5 | 0 | 0.3
2381 | 30/07/2025 10:23:15.723 | 97.512 | 79 | 100 | 70 | 53 | 27.089 | 9.428 | 7.004 | 134.545 | 29.735 | 28.381 | 28.16 | 600.542 | 26.15 | 26.916 | 1306.848 | 27.212 | 27.447 | 36.525 | 28.001 | 3.6 | 2.3 | 0.6 | 0 | 0.2
2382 | 30/07/2025 10:23:17.359 | 97.008 | 78 | 100 | 70 | 52 | 30.3 | 9.292 | 7.004 | 134.404 | 29.712 | 28.403 | 28.137 | 600.533 | 26.152 | 26.929 | 1304.787 | 27.234 | 27.442 | 36.484 | 23.001 | 3.6 | 2.4 | 0.6 | 0 | 0.2
2383 | 30/07/2025 10:23:18.996 | 97.704 | 78 | 100 | 70 | 51 | 31.298 | 9.425 | 7.005 | 134.649 | 29.735 | 28.404 | 28.136 | 600.532 | 26.152 | 26.935 | 1304.802 | 27.196 | 27.453 | 36.739 | 26.001 | 2.8 | 1 | 0.9 | 0.1 | 0.3
2384 | 30/07/2025 10:23:20.636 | 97.248 | 79 | 100 | 71 | 52 | 28.434 | 9.59 | 7.047 | 134.59 | 29.714 | 28.399 | 28.112 | 600.601 | 26.144 | 26.898 | 1306.977 | 27.195 | 27.454 | 36.73 | 22.001 | 2.8 | 0.7 | 0.9 | 0.1 | 0.3
2385 | 30/07/2025 10:23:22.276 | 97.488 | 78 | 100 | 70 | 53 | 31.185 | 9.579 | 7.049 | 134.835 | 29.743 | 28.391 | 28.117 | 600.697 | 26.171 | 26.913 | 1303.384 | 27.214 | 27.44 | 37.093 | 22.001 | 2.8 | 0.7 | 0.9 | 0.1 | 0.3
2386 | 30/07/2025 10:23:23.911 | 97.776 | 79 | 100 | 70 | 52 | 29.685 | 9.141 | 7.069 | 134.63 | 29.723 | 28.37 | 28.135 | 600.568 | 26.148 | 26.92 | 1296.851 | 27.227 | 27.451 | 36.462 | 28.001 | 1.2 | 2.9 | 1.2 | 0.4 | 0.2
2387 | 30/07/2025 10:23:25.548 | 98.328 | 79 | 100 | 70 | 52 | 27.291 | 9.286 | 7.072 | 134.419 | 29.713 | 28.396 | 28.12 | 600.498 | 26.166 | 26.917 | 1298.402 | 27.199 | 27.429 | 36.461 | 27.001 | 1.2 | 1.6 | 1.2 | 0.4 | 0.2
2388 | 30/07/2025 10:23:27.184 | 98.352 | 81 | 100 | 70 | 52 | 30.695 | 9.21 | 7.071 | 134.751 | 29.711 | 28.398 | 28.152 | 600.65 | 26.175 | 26.928 | 1294.87 | 27.178 | 27.469 | 36.695 | 25.001 | 3.9 | 2.9 | 1 | 0.8 | 0.2
2389 | 30/07/2025 10:23:28.819 | 98.592 | 78 | 100 | 70 | 52 | 31.255 | 9.556 | 7.123 | 134.611 | 29.709 | 28.41 | 28.106 | 600.582 | 26.166 | 26.947 | 1299.702 | 27.231 | 27.451 | 36.857 | 28.001 | 3.9 | 1.6 | 1 | 0.8 | 0.2
2390 | 30/07/2025 10:23:30.456 | 98.424 | 78 | 100 | 70 | 52 | 27.775 | 9.579 | 7.121 | 134.504 | 29.726 | 28.377 | 28.138 | 600.636 | 26.183 | 26.951 | 1311.398 | 27.219 | 27.452 | 36.613 | 24.001 | 2.9 | 2.1 | 0.7 | 0 | 0.1
2391 | 30/07/2025 10:23:32.090 | 97.68 | 80 | 100 | 70 | 52 | 31.263 | 9.509 | 7.124 | 134.527 | 29.689 | 28.382 | 28.147 | 600.514 | 26.168 | 26.965 | 1316.83 | 27.23 | 27.453 | 36.444 | 24.001 | 2.9 | 2.1 | 0.7 | 0 | 0.1
2392 | 30/07/2025 10:23:33.727 | 98.16 | 79 | 100 | 70 | 52 | 28.889 | 9.348 | 7.123 | 134.571 | 29.707 | 28.397 | 28.132 | 602.044 | 26.176 | 26.944 | 1317.972 | 27.203 | 27.428 | 36.5 | 30.001 | 2.9 | 2.3 | 0.7 | 0 | 0.1
2393 | 30/07/2025 10:23:35.362 | 98.376 | 78 | 100 | 70 | 52 | 27.513 | 9.432 | 7.098 | 134.703 | 29.704 | 28.396 | 28.126 | 600.442 | 26.155 | 26.937 | 1304.784 | 27.186 | 27.471 | 36.54 | 29.001 | 1.4 | 2.1 | 1.3 | 0.5 | 0.2
2394 | 30/07/2025 10:23:36.999 | 98.256 | 80 | 100 | 70 | 53 | 30.864 | 9.334 | 7.062 | 134.457 | 29.685 | 28.387 | 28.096 | 600.767 | 26.153 | 26.95 | 1305.369 | 27.214 | 27.45 | 36.604 | 31.001 | 1.4 | 2.6 | 1.3 | 0.5 | 0.2
2395 | 30/07/2025 10:23:38.634 | 98.256 | 79 | 100 | 71 | 52 | 31.031 | 9.536 | 7.002 | 134.652 | 29.725 | 28.373 | 28.169 | 600.673 | 26.149 | 26.934 | 1297.017 | 27.208 | 27.447 | 36.567 | 25.001 | 4.6 | 2.4 | 0.9 | 0.9 | 0.2
2396 | 30/07/2025 10:23:40.270 | 98.376 | 79 | 100 | 69 | 52 | 30.195 | 9.437 | 7.005 | 134.499 | 29.711 | 28.39 | 28.126 | 600.575 | 26.156 | 26.951 | 1306.516 | 27.205 | 27.434 | 36.479 | 25.001 | 4.6 | 2.4 | 0.9 | 0.9 | 0.2
2397 | 30/07/2025 10:23:41.907 | 97.896 | 80 | 100 | 71 | 52 | 31.269 | 9.21 | 6.918 | 134.592 | 29.725 | 28.398 | 28.15 | 602.175 | 26.155 | 26.936 | 1307.897 | 27.191 | 27.447 | 36.501 | 26.001 | 4.6 | 1.2 | 0.9 | 0.9 | 0.2
2398 | 30/07/2025 10:23:43.542 | 98.184 | 80 | 100 | 70 | 52 | 28.343 | 9.576 | 6.905 | 134.608 | 29.725 | 28.395 | 28.107 | 601.901 | 26.163 | 26.945 | 1295.667 | 27.198 | 27.46 | 36.684 | 26.001 | 3.7 | 1.6 | 1 | 0.5 | 0.1
2399 | 30/07/2025 10:23:45.174 | 98.28 | 80 | 100 | 70 | 53 | 28.069 | 9.468 | 6.864 | 134.834 | 29.747 | 28.383 | 28.1 | 601.975 | 26.172 | 26.944 | 1290.083 | 27.203 | 27.451 | 36.737 | 27.001 | 3.7 | 1.4 | 1 | 0.5 | 0.1
2400 | 30/07/2025 10:23:46.808 | 98.016 | 81 | 100 | 70 | 52 | 31.087 | 9.283 | 6.931 | 134.724 | 29.721 | 28.394 | 28.159 | 602.066 | 26.147 | 26.93 | 1287.594 | 27.217 | 27.442 | 36.397 | 28.001 | 4 | 1.9 | 0.9 | 0 | 0.1
2401 | 30/07/2025 10:23:48.444 | 98.4 | 79 | 100 | 72 | 53 | 30.707 | 9.542 | 6.937 | 134.508 | 29.721 | 28.404 | 28.124 | 601.956 | 26.158 | 26.931 | 1282.694 | 27.202 | 27.451 | 36.574 | 30.001 | 4 | 2 | 0.9 | 0 | 0.1
2402 | 30/07/2025 10:23:50.080 | 98.424 | 80 | 100 | 70 | 52 | 30.679 | 9.505 | 6.945 | 134.81 | 29.727 | 28.402 | 28.145 | 602.085 | 26.158 | 26.925 | 1284.595 | 27.189 | 27.47 | 36.705 | 30.001 | 4 | 2 | 0.9 | 0 | 0.1
2403 | 30/07/2025 10:23:51.715 | 98.736 | 80 | 100 | 70 | 51 | 31.258 | 9.433 | 6.951 | 134.779 | 29.73 | 28.396 | 28.118 | 601.946 | 26.139 | 26.924 | 1288.997 | 27.199 | 27.456 | 36.596 | 30.001 | 3.1 | 1.9 | 0.6 | 0 | 0.1
2404 | 30/07/2025 10:23:53.348 | 99.024 | 79 | 100 | 70 | 52 | 27.91 | 9.397 | 7.003 | 134.736 | 29.719 | 28.381 | 28.134 | 602.195 | 26.139 | 26.905 | 1289.679 | 27.213 | 27.448 | 36.535 | 26.001 | 2.4 | 2.2 | 0.6 | 0.6 | 0.1
2405 | 30/07/2025 10:23:54.983 | 99.576 | 80 | 100 | 70 | 52 | 28.74 | 9.512 | 7.063 | 134.506 | 29.711 | 28.398 | 28.138 | 602.09 | 26.135 | 26.9 | 1289.369 | 27.224 | 27.433 | 36.326 | 23.001 | 2 | 2.2 | 0 | 0.6 | 0.1
2406 | 30/07/2025 10:23:56.617 | 99.72 | 80 | 100 | 70 | 51 | 31.133 | 9.443 | 7.071 | 134.788 | 29.728 | 28.401 | 28.133 | 601.995 | 26.174 | 26.928 | 1290.571 | 27.194 | 27.454 | 36.771 | 31.001 | 2 | 1.8 | 0 | 0.6 | 0.1
2407 | 30/07/2025 10:23:58.249 | 99.816 | 81 | 100 | 70 | 52 | 27.714 | 9.579 | 7.151 | 133.313 | 29.722 | 28.394 | 28.116 | 600.598 | 26.164 | 26.933 | 1296.4 | 27.183 | 27.461 | 36.742 | 31.001 | 2 | 1.8 | 0 | 0.6 | 0.1
2408 | 30/07/2025 10:23:59.881 | 100.032 | 81 | 100 | 71 | 52 | 30.998 | 9.304 | 7.167 | 133.292 | 29.733 | 28.395 | 28.117 | 600.569 | 26.181 | 26.931 | 1306.679 | 27.205 | 27.457 | 36.584 | 31.001 | 3.1 | 1 | 0.7 | 0 | 0.1
2409 | 30/07/2025 10:24:01.514 | 99.912 | 82 | 100 | 71 | 52 | 31.052 | 9.284 | 7.121 | 133.297 | 29.712 | 28.381 | 28.149 | 602.211 | 26.166 | 26.94 | 1304.492 | 27.22 | 27.453 | 36.451 | 31.001 | 3.1 | 2.7 | 0.7 | 0 | 0.1
2410 | 30/07/2025 10:24:03.148 | 100.104 | 81 | 100 | 69 | 52 | 27.424 | 9.435 | 7.124 | 132.927 | 29.7 | 28.4 | 28.125 | 600.48 | 26.151 | 26.948 | 1300.901 | 27.206 | 27.424 | 36.443 | 30.001 | 2 | 3 | 0.5 | 0.8 | 0.1
2411 | 30/07/2025 10:24:04.786 | 100.392 | 82 | 100 | 70 | 52 | 29.21 | 9.285 | 7.121 | 133.266 | 29.713 | 28.403 | 28.146 | 600.721 | 26.152 | 26.934 | 1293.99 | 27.174 | 27.453 | 36.672 | 26.001 | 4.2 | 0.7 | 0.9 | 0.3 | 0.1
2412 | 30/07/2025 10:24:06.423 | 100.776 | 82 | 100 | 70 | 51 | 31.202 | 9.275 | 7.088 | 133.089 | 29.7 | 28.405 | 28.099 | 600.58 | 26.158 | 26.959 | 1306.822 | 27.219 | 27.452 | 36.517 | 21.001 | 3.5 | 0.7 | 1 | 0 | 0.1
2413 | 30/07/2025 10:24:08.057 | 100.68 | 82 | 100 | 71 | 52 | 28.025 | 9.443 | 7.086 | 133.292 | 29.7 | 28.389 | 28.129 | 600.566 | 26.145 | 26.931 | 1311.771 | 27.217 | 27.452 | 36.502 | 21.001 | 3.5 | 0.7 | 1 | 0 | 0.1
2414 | 30/07/2025 10:24:09.691 | 100.728 | 82 | 100 | 70 | 52 | 31.046 | 9.285 | 7.135 | 134.471 | 29.687 | 28.368 | 28.123 | 600.699 | 26.156 | 26.962 | 1306.691 | 27.227 | 27.447 | 36.423 | 28.001 | 3.5 | 1 | 1 | 0 | 0.1
2415 | 30/07/2025 10:24:11.327 | 100.536 | 82 | 100 | 70 | 52 | 30.67 | 9.503 | 7.123 | 134.606 | 29.708 | 28.401 | 28.143 | 600.639 | 26.163 | 26.941 | 1302.214 | 27.196 | 27.434 | 36.475 | 38.001 | 5.6 | 2.2 | 0.7 | 0.6 | 0.3
2416 | 30/07/2025 10:24:12.962 | 100.32 | 82 | 99 | 71 | 52 | 27.169 | 9.437 | 7.124 | 134.759 | 29.718 | 28.403 | 28.135 | 600.56 | 26.159 | 26.942 | 1307.765 | 27.195 | 27.481 | 36.695 | 26.001 | 5.6 | 1.8 | 0.7 | 0.6 | 0.3
2417 | 30/07/2025 10:24:14.597 | 100.344 | 82 | 100 | 70 | 52 | 29.715 | 9.486 | 7.124 | 134.689 | 29.721 | 28.393 | 28.108 | 600.489 | 26.159 | 26.942 | 1304.539 | 27.21 | 27.452 | 36.88 | 32.001 | 3.9 | 1.5 | 0.7 | 0.6 | 0.3
2418 | 30/07/2025 10:24:16.233 | 100.008 | 82 | 100 | 70 | 52 | 27.872 | 9.549 | 7.121 | 134.553 | 29.731 | 28.395 | 28.132 | 600.506 | 26.167 | 26.945 | 1299.707 | 27.232 | 27.458 | 36.661 | 32.001 | 3.9 | 1.5 | 0.7 | 0.6 | 0.3
2419 | 30/07/2025 10:24:17.868 | 99.984 | 82 | 100 | 71 | 52 | 28.542 | 9.291 | 7.135 | 134.591 | 29.743 | 28.385 | 28.134 | 599.319 | 26.162 | 26.939 | 1307.223 | 27.214 | 27.423 | 36.589 | 24.001 | 3.9 | 2.3 | 0.7 | 0.6 | 0.3
2420 | 30/07/2025 10:24:19.502 | 99.72 | 81 | 100 | 70 | 52 | 31.142 | 9.447 | 7.092 | 134.617 | 29.736 | 28.403 | 28.15 | 598.3 | 26.149 | 26.925 | 1305.444 | 27.198 | 27.448 | 36.554 | 27.001 | 3.2 | 2.9 | 0.6 | 1 | 0.3
2421 | 30/07/2025 10:24:21.138 | 99.816 | 81 | 100 | 71 | 51 | 30.109 | 9.39 | 7.089 | 134.603 | 29.723 | 28.396 | 28.117 | 599.229 | 26.142 | 26.945 | 1291.894 | 27.195 | 27.464 | 36.513 | 27.001 | 3.2 | 2.5 | 0.6 | 1 | 0.3
2422 | 30/07/2025 10:24:22.774 | 99.792 | 81 | 100 | 71 | 51 | 27.05 | 9.229 | 7.087 | 134.891 | 29.743 | 28.383 | 28.12 | 600.645 | 26.155 | 26.939 | 1309.467 | 27.212 | 27.456 | 36.498 | 26.001 | 2.2 | 1.9 | 1.2 | 1.1 | 0.3
2423 | 30/07/2025 10:24:24.412 | 99.696 | 82 | 100 | 70 | 52 | 31.006 | 9.173 | 7.088 | 134.523 | 29.726 | 28.366 | 28.129 | 600.452 | 26.145 | 26.94 | 1306.833 | 27.211 | 27.449 | 36.573 | 25.001 | 4.1 | 2.6 | 0.6 | 1.4 | 0.3
2424 | 30/07/2025 10:24:26.048 | 99.384 | 80 | 100 | 70 | 53 | 27.375 | 9.492 | 7.087 | 134.429 | 29.736 | 28.395 | 28.155 | 600.564 | 26.161 | 26.929 | 1309.753 | 27.196 | 27.432 | 36.451 | 25.001 | 4.1 | 2.6 | 0.6 | 1.4 | 0.3
2425 | 30/07/2025 10:24:27.683 | 99.36 | 80 | 100 | 71 | 52 | 29.221 | 9.562 | 7.07 | 134.655 | 29.713 | 28.411 | 28.133 | 600.709 | 26.15 | 26.912 | 1307.009 | 27.205 | 27.451 | 36.699 | 29.001 | 2 | 2.6 | 0.7 | 0.7 | 0.3
2426 | 30/07/2025 10:24:29.317 | 99.192 | 81 | 100 | 71 | 52 | 31.161 | 9.286 | 7.071 | 134.84 | 29.72 | 28.393 | 28.111 | 600.613 | 26.165 | 26.923 | 1306.787 | 27.194 | 27.447 | 36.647 | 35.001 | 2 | 0.6 | 0.7 | 0.7 | 0.3
2427 | 30/07/2025 10:24:30.954 | 98.688 | 80 | 100 | 70 | 52 | 29.624 | 9.388 | 7.086 | 134.731 | 29.718 | 28.379 | 28.138 | 600.644 | 26.139 | 26.911 | 1314.669 | 27.209 | 27.443 | 36.564 | 30.001 | 3.4 | 1.4 | 0.6 | 0.6 | 0.2
2428 | 30/07/2025 10:24:32.590 | 99.888 | 80 | 100 | 70 | 52 | 27.315 | 9.437 | 7.104 | 134.466 | 29.717 | 28.394 | 28.136 | 600.529 | 26.159 | 26.932 | 1311.023 | 27.219 | 27.432 | 36.431 | 26.001 | 4.4 | 0.5 | 0.3 | 0.7 | 0.2
2429 | 30/07/2025 10:24:34.229 | 99.792 | 80 | 100 | 71 | 52 | 30.697 | 9.496 | 7.134 | 134.506 | 29.715 | 28.411 | 28.126 | 600.582 | 26.16 | 26.933 | 1317.308 | 27.214 | 27.436 | 36.283 | 26.001 | 4.4 | 0.5 | 0.3 | 0.7 | 0.2
2430 | 30/07/2025 10:24:35.863 | 99.576 | 79 | 100 | 71 | 52 | 27.207 | 9.641 | 7.125 | 134.601 | 29.707 | 28.389 | 28.119 | 600.601 | 26.169 | 26.951 | 1312.369 | 27.186 | 27.455 | 36.853 | 28.001 | 3.9 | 0.5 | 0.6 | 0.5 | 0.1
2431 | 30/07/2025 10:24:37.500 | 99.528 | 83 | 100 | 70 | 52 | 29.884 | 9.575 | 7.122 | 134.728 | 29.722 | 28.389 | 28.282 | 600.781 | 26.157 | 26.933 | 1316.509 | 27.205 | 27.451 | 36.527 | 27.001 | 1.6 | 2.3 | 0.1 | 0.5 | 0.1
2432 | 30/07/2025 10:24:39.135 | 99.096 | 81 | 100 | 70 | 52 | 31.26 | 9.32 | 7.133 | 134.481 | 29.694 | 28.367 | 28.249 | 600.686 | 26.163 | 26.953 | 1316.795 | 27.23 | 27.461 | 36.605 | 30.001 | 1.3 | 2.3 | 0 | 0.1 | 0.2
2433 | 30/07/2025 10:24:40.769 | 99.192 | 81 | 100 | 70 | 52 | 29.038 | 9.288 | 7.1 | 134.381 | 29.697 | 28.393 | 28.29 | 600.564 | 26.173 | 26.956 | 1322.794 | 27.206 | 27.435 | 36.559 | 29.001 | 2.5 | 3.2 | 0.9 | 0.6 | 0.3
2434 | 30/07/2025 10:24:42.404 | 99.096 | 80 | 100 | 70 | 52 | 31.145 | 9.289 | 7.09 | 134.381 | 29.685 | 28.416 | 28.185 | 600.476 | 26.161 | 26.958 | 1317.613 | 27.224 | 27.453 | 36.592 | 29.001 | 2.1 | 3.2 | 0.8 | 0.3 | 0.3
2435 | 30/07/2025 10:24:44.039 | 98.376 | 79 | 100 | 70 | 52 | 30.187 | 9.429 | 7.097 | 134.88 | 29.719 | 28.399 | 28.224 | 600.509 | 26.175 | 26.944 | 1318.572 | 27.166 | 27.458 | 36.788 | 29.001 | 2.1 | 3.2 | 0.8 | 0.3 | 0.3
2436 | 30/07/2025 10:24:45.675 | 97.968 | 79 | 100 | 70 | 51 | 27.117 | 9.49 | 7.135 | 134.72 | 29.712 | 28.39 | 28.119 | 600.727 | 26.164 | 26.952 | 1296.507 | 27.214 | 27.458 | 36.812 | 30.001 | 2.1 | 2.6 | 0.8 | 0.3 | 0.3
2437 | 30/07/2025 10:24:47.310 | 97.944 | 79 | 100 | 71 | 53 | 30.262 | 9.473 | 7.088 | 134.562 | 29.711 | 28.373 | 28.284 | 600.541 | 26.154 | 26.948 | 1297.058 | 27.211 | 27.443 | 36.557 | 24.001 | 3.6 | 2 | 1.3 | 0 | 0.2
2438 | 30/07/2025 10:24:48.944 | 97.968 | 79 | 100 | 70 | 52 | 31.304 | 9.49 | 7.058 | 134.526 | 29.732 | 28.411 | 28.295 | 600.716 | 26.174 | 26.942 | 1297.355 | 27.211 | 27.434 | 36.394 | 29.001 | 3.3 | 0.7 | 0.9 | 0.5 | 0.2
2439 | 30/07/2025 10:24:50.578 | 98.832 | 78 | 100 | 70 | 52 | 28.441 | 9.465 | 7.004 | 134.742 | 29.725 | 28.407 | 28.296 | 600.448 | 26.158 | 26.953 | 1292.168 | 27.2 | 27.482 | 36.677 | 31.001 | 1.7 | 0.7 | 1.1 | 0.6 | 0.2
2440 | 30/07/2025 10:24:52.214 | 98.784 | 79 | 100 | 71 | 52 | 31.172 | 9.503 | 6.938 | 134.771 | 29.741 | 28.392 | 28.292 | 600.704 | 26.159 | 26.934 | 1300.616 | 27.187 | 27.451 | 36.535 | 31.001 | 1.7 | 0.7 | 1.1 | 0.6 | 0.2
2441 | 30/07/2025 10:24:53.848 | 98.712 | 79 | 100 | 71 | 52 | 29.562 | 9.432 | 6.847 | 134.591 | 29.715 | 28.381 | 28.258 | 600.63 | 26.141 | 26.951 | 1304.736 | 27.24 | 27.464 | 36.726 | 31.001 | 1.6 | 2.5 | 0.4 | 1.1 | 0.3
2442 | 30/07/2025 10:24:55.484 | 99.024 | 81 | 100 | 70 | 52 | 27.194 | 9.488 | 6.933 | 134.655 | 29.737 | 28.384 | 28.296 | 600.653 | 26.173 | 26.94 | 1296.083 | 27.21 | 27.428 | 36.609 | 29.001 | 1.4 | 2.5 | 0.6 | 0.5 | 0.3
2443 | 30/07/2025 10:24:57.120 | 98.856 | 79 | 100 | 70 | 52 | 30.579 | 9.506 | 6.953 | 134.473 | 29.725 | 28.399 | 28.286 | 600.582 | 26.147 | 26.929 | 1301.995 | 27.206 | 27.456 | 36.549 | 33.001 | 1.4 | 2.1 | 0.6 | 0.5 | 0.3
2444 | 30/07/2025 10:24:58.757 | 98.808 | 81 | 100 | 72 | 52 | 31.239 | 9.579 | 7.005 | 134.602 | 29.718 | 28.402 | 28.274 | 601.94 | 26.151 | 26.933 | 1306.736 | 27.187 | 27.462 | 36.859 | 33.001 | 4.1 | 2.9 | 1.2 | 0.2 | 0.3
2445 | 30/07/2025 10:25:00.392 | 98.856 | 81 | 100 | 70 | 52 | 29.738 | 9.583 | 7.01 | 134.61 | 29.719 | 28.401 | 28.274 | 600.68 | 26.155 | 26.919 | 1310.767 | 27.209 | 27.455 | 36.9 | 26.001 | 4.1 | 1.3 | 1.2 | 0.2 | 0.3
2446 | 30/07/2025 10:25:02.028 | 98.808 | 80 | 100 | 71 | 53 | 31.237 | 9.579 | 7.035 | 134.779 | 29.725 | 28.378 | 28.277 | 600.733 | 26.149 | 26.926 | 1315.207 | 27.215 | 27.446 | 36.826 | 26.001 | 4.1 | 1.3 | 1.2 | 0.2 | 0.3
2447 | 30/07/2025 10:25:03.665 | 98.616 | 81 | 100 | 70 | 52 | 29.027 | 9.449 | 7.058 | 134.322 | 29.737 | 28.394 | 28.306 | 602.244 | 26.159 | 26.918 | 1319.173 | 27.208 | 27.436 | 36.441 | 30.001 | 2.9 | 3.3 | 0.8 | 0.5 | 0.2
2448 | 30/07/2025 10:25:05.299 | 98.784 | 80 | 100 | 70 | 52 | 27.679 | 9.432 | 7.061 | 134.621 | 29.71 | 28.4 | 28.285 | 600.469 | 26.155 | 26.92 | 1319.78 | 27.204 | 27.459 | 36.706 | 28.001 | 2.1 | 1.2 | 0.9 | 0.5 | 0.2
2449 | 30/07/2025 10:25:06.935 | 98.136 | 81 | 99 | 70 | 52 | 30.976 | 9.429 | 7.034 | 134.869 | 29.728 | 28.394 | 28.278 | 601.662 | 26.165 | 26.927 | 1317.091 | 27.178 | 27.456 | 36.635 | 29.001 | 1.5 | 1.2 | 0.8 | 0.8 | 0.2
2450 | 30/07/2025 10:25:08.798 | 97.728 | 79 | 100 | 70 | 52 | 31.042 | 9.289 | 7.058 | 134.651 | 29.713 | 28.382 | 28.264 | 602.112 | 26.168 | 26.938 | 1317.28 | 27.217 | 27.449 | 36.671 | 30.001 | 1.5 | 2.2 | 0.8 | 0.8 | 0.2
2451 | 30/07/2025 10:25:10.433 | 97.368 | 78 | 100 | 71 | 52 | 27.386 | 9.437 | 7.06 | 134.445 | 29.693 | 28.39 | 28.273 | 601.934 | 26.171 | 26.959 | 1307.197 | 27.222 | 27.434 | 36.715 | 30.001 | 2.2 | 2.3 | 0.9 | 0.8 | 0.2
2452 | 30/07/2025 10:25:12.070 | 97.512 | 78 | 100 | 71 | 53 | 31.331 | 9.436 | 7.069 | 134.507 | 29.706 | 28.407 | 28.283 | 602.137 | 26.16 | 26.948 | 1304.94 | 27.213 | 27.432 | 36.336 | 30.001 | 2.2 | 2.3 | 0.9 | 0.8 | 0.2
2453 | 30/07/2025 10:25:13.703 | 97.704 | 78 | 100 | 71 | 52 | 28.421 | 9.289 | 7.071 | 134.706 | 29.69 | 28.394 | 28.266 | 602.027 | 26.174 | 26.95 | 1295.033 | 27.176 | 27.447 | 36.781 | 27.001 | 2.2 | 3.6 | 0.9 | 0.8 | 0.2
2454 | 30/07/2025 10:25:15.420 | 97.92 | 78 | 100 | 70 | 52 | 28.116 | 9.428 | 7.072 | 134.748 | 29.699 | 28.4 | 28.273 | 602.062 | 26.167 | 26.947 | 1289.847 | 27.207 | 27.454 | 36.449 | 25.001 | 3.8 | 2.9 | 0.1 | 0 | 0.2
2455 | 30/07/2025 10:25:17.058 | 98.376 | 79 | 100 | 70 | 52 | 31.12 | 9.505 | 7.116 | 134.59 | 29.687 | 28.382 | 28.279 | 602.022 | 26.144 | 26.936 | 1298.415 | 27.237 | 27.445 | 36.742 | 23.001 | 3.8 | 1.5 | 0.1 | 0 | 0.2
2456 | 30/07/2025 10:25:18.693 | 98.328 | 81 | 100 | 70 | 52 | 30.753 | 9.467 | 7.103 | 134.505 | 29.714 | 28.396 | 28.294 | 602.046 | 26.165 | 26.935 | 1306.966 | 27.209 | 27.427 | 36.557 | 27.001 | 3 | 1.9 | 1.5 | 0.3 | 0.1
2457 | 30/07/2025 10:25:20.329 | 97.992 | 79 | 100 | 70 | 53 | 27.27 | 9.291 | 7.085 | 134.799 | 29.703 | 28.406 | 28.285 | 602.155 | 26.147 | 26.93 | 1299.915 | 27.2 | 27.453 | 36.821 | 27.001 | 3 | 1.9 | 1.5 | 0.3 | 0.1
2458 | 30/07/2025 10:25:21.969 | 98.688 | 81 | 100 | 70 | 52 | 31.335 | 9.336 | 7.089 | 134.864 | 29.732 | 28.397 | 28.286 | 601.978 | 26.179 | 26.932 | 1307.117 | 27.173 | 27.458 | 36.662 | 23.001 | 3.2 | 3.4 | 1.1 | 0 | 0.1
2459 | 30/07/2025 10:25:23.604 | 98.328 | 80 | 100 | 71 | 52 | 27.96 | 9.396 | 7.088 | 134.68 | 29.714 | 28.397 | 28.279 | 602.093 | 26.16 | 26.936 | 1306.487 | 27.214 | 27.463 | 36.545 | 25.001 | 2.9 | 3.4 | 1.5 | 1 | 0.2
2460 | 30/07/2025 10:25:25.240 | 98.28 | 79 | 100 | 70 | 52 | 28.608 | 9.508 | 7.123 | 134.43 | 29.721 | 28.382 | 28.273 | 601.84 | 26.153 | 26.953 | 1304.214 | 27.213 | 27.452 | 36.608 | 29.001 | 3.1 | 3.5 | 1.5 | 0.1 | 0.1
2461 | 30/07/2025 10:25:26.876 | 97.824 | 80 | 100 | 71 | 52 | 31.122 | 9.434 | 7.121 | 134.403 | 29.748 | 28.412 | 28.308 | 602.192 | 26.158 | 26.935 | 1305.135 | 27.201 | 27.416 | 36.516 | 26.001 | 1.9 | 3.5 | 0.9 | 0.5 | 0.2
2462 | 30/07/2025 10:25:28.514 | 98.136 | 82 | 100 | 71 | 53 | 30.208 | 9.407 | 7.074 | 134.739 | 29.72 | 28.411 | 28.279 | 602.201 | 26.156 | 26.926 | 1295.213 | 27.208 | 27.457 | 36.959 | 25.001 | 3.2 | 1.8 | 0.7 | 0.9 | 0.2
2463 | 30/07/2025 10:25:30.149 | 97.872 | 79 | 100 | 70 | 52 | 30.919 | 9.434 | 7.07 | 134.939 | 29.728 | 28.406 | 28.27 | 602.23 | 26.142 | 26.925 | 1295.28 | 27.182 | 27.45 | 36.63 | 25.001 | 3.2 | 1.8 | 0.7 | 0.9 | 0.2
2464 | 30/07/2025 10:25:31.784 | 97.944 | 79 | 100 | 69 | 52 | 31.082 | 9.497 | 7.071 | 134.565 | 29.717 | 28.387 | 28.274 | 602.088 | 26.136 | 26.932 | 1300.243 | 27.237 | 27.451 | 36.563 | 25.001 | 2.2 | 1.8 | 0.9 | 0.5 | 0.2
2465 | 30/07/2025 10:25:33.423 | 98.544 | 80 | 100 | 71 | 52 | 27.536 | 9.29 | 7.074 | 134.737 | 29.738 | 28.379 | 28.301 | 601.923 | 26.16 | 26.92 | 1307.264 | 27.205 | 27.428 | 36.711 | 25.001 | 2.2 | 2.2 | 0.9 | 0.5 | 0.2
2466 | 30/07/2025 10:25:35.058 | 97.896 | 82 | 100 | 70 | 52 | 29.181 | 9.429 | 7.088 | 134.478 | 29.713 | 28.406 | 28.294 | 602.123 | 26.141 | 26.92 | 1307.127 | 27.203 | 27.442 | 36.457 | 24.001 | 2.7 | 3 | 1.5 | 0.5 | 0.2
2467 | 30/07/2025 10:25:36.708 | 97.848 | 78 | 100 | 70 | 53 | 31.229 | 9.578 | 7.091 | 134.748 | 29.717 | 28.395 | 28.267 | 602.045 | 26.143 | 26.912 | 1302.192 | 27.184 | 27.446 | 36.83 | 23.001 | 2.7 | 1.3 | 1.5 | 0.5 | 0.2
2468 | 30/07/2025 10:25:38.346 | 98.256 | 82 | 100 | 70 | 52 | 29.715 | 9.58 | 7.07 | 134.619 | 29.73 | 28.393 | 28.28 | 602.195 | 26.145 | 26.904 | 1307.086 | 27.22 | 27.449 | 36.729 | 23.001 | 2.7 | 1.3 | 1.5 | 0.5 | 0.2
2469 | 30/07/2025 10:25:39.983 | 98.328 | 82 | 100 | 70 | 52 | 27.3 | 9.436 | 7.069 | 134.543 | 29.721 | 28.385 | 28.294 | 602.086 | 26.163 | 26.933 | 1309.364 | 27.22 | 27.447 | 36.718 | 25.001 | 2.2 | 1.1 | 1.3 | 0.5 | 0.2
2470 | 30/07/2025 10:25:41.619 | 98.376 | 81 | 100 | 71 | 52 | 30.648 | 9.437 | 7.067 | 134.471 | 29.723 | 28.392 | 28.316 | 602.11 | 26.169 | 26.936 | 1309.662 | 27.204 | 27.436 | 36.561 | 28.001 | 0.8 | 2.2 | 0.4 | 0.5 | 0.2
2471 | 30/07/2025 10:25:43.256 | 98.232 | 81 | 100 | 70 | 52 | 27.126 | 9.284 | 7.072 | 134.335 | 29.707 | 28.405 | 28.257 | 602.098 | 26.161 | 26.945 | 1317.283 | 27.216 | 27.452 | 38.62 | 24.001 | 1.8 | 2.2 | 0.6 | 1.1 | 0.1
2472 | 30/07/2025 10:25:44.892 | 98.256 | 81 | 100 | 71 | 52 | 29.791 | 9.282 | 7.072 | 134.894 | 29.722 | 28.397 | 28.268 | 603.398 | 26.185 | 26.949 | 1312.181 | 27.177 | 27.44 | 36.776 | 24.001 | 1.8 | 1.8 | 0.6 | 1.1 | 0.1
2473 | 30/07/2025 10:25:46.525 | 98.112 | 79 | 100 | 69 | 52 | 31.291 | 9.432 | 7.073 | 134.714 | 29.695 | 28.388 | 28.274 | 602.217 | 26.144 | 26.941 | 1306.419 | 27.226 | 27.463 | 36.6 | 26.001 | 1.4 | 1.4 | 1 | 0 | 0.2
2474 | 30/07/2025 10:25:48.161 | 98.568 | 81 | 100 | 71 | 51 | 28.655 | 9.429 | 7.084 | 134.826 | 29.711 | 28.38 | 28.305 | 602.041 | 26.165 | 26.944 | 1306.219 | 27.216 | 27.453 | 36.513 | 26.001 | 1.4 | 1.4 | 1 | 0 | 0.2
2475 | 30/07/2025 10:25:49.797 | 98.04 | 81 | 100 | 69 | 52 | 31.15 | 9.452 | 7.103 | 134.464 | 29.686 | 28.399 | 28.291 | 602.007 | 26.155 | 26.937 | 1291.975 | 27.211 | 27.443 | 36.376 | 22.001 | 1.4 | 2.9 | 1 | 0 | 0.2
2476 | 30/07/2025 10:25:51.433 | 98.16 | 82 | 100 | 71 | 52 | 30.317 | 9.48 | 7.123 | 134.582 | 29.689 | 28.395 | 28.259 | 601.867 | 26.16 | 26.937 | 1292.182 | 27.182 | 27.449 | 36.823 | 30.001 | 2.7 | 1.3 | 1.3 | 0 | 0.1
2477 | 30/07/2025 10:25:53.069 | 98.352 | 79 | 100 | 72 | 52 | 27.191 | 9.437 | 7.124 | 134.819 | 29.704 | 28.406 | 28.272 | 602.221 | 26.159 | 26.93 | 1298.877 | 27.198 | 27.448 | 36.794 | 25.001 | 2.7 | 1.1 | 1.3 | 0 | 0.1
2478 | 30/07/2025 10:25:54.704 | 98.088 | 80 | 100 | 71 | 53 | 30.349 | 9.58 | 7.075 | 134.583 | 29.709 | 28.382 | 28.286 | 602.045 | 26.165 | 26.966 | 1295.179 | 27.236 | 27.464 | 36.778 | 23.001 | 1.6 | 1.7 | 0.6 | 0 | 0.2
2479 | 30/07/2025 10:25:56.341 | 97.632 | 79 | 100 | 70 | 51 | 31.351 | 9.412 | 7.069 | 134.469 | 29.723 | 28.397 | 28.3 | 602.026 | 26.179 | 26.955 | 1288.009 | 27.209 | 27.423 | 36.538 | 23.001 | 1.6 | 1.7 | 0.6 | 0 | 0.2
2480 | 30/07/2025 10:25:57.978 | 97.224 | 80 | 100 | 70 | 52 | 29.303 | 9.293 | 7.073 | 134.21 | 29.729 | 28.398 | 28.28 | 601.975 | 26.159 | 26.952 | 1287.595 | 27.217 | 27.442 | 36.643 | 26.001 | 1.6 | 2 | 0.6 | 0 | 0.2
2481 | 30/07/2025 10:25:59.616 | 96.816 | 81 | 100 | 70 | 52 | 31.188 | 9.226 | 7.069 | 134.803 | 29.751 | 28.4 | 28.294 | 600.694 | 26.168 | 26.931 | 1296.776 | 27.175 | 27.446 | 36.794 | 32.001 | 2.8 | 1.1 | 0.3 | 0.5 | 0.2
2482 | 30/07/2025 10:26:01.256 | 97.416 | 79 | 100 | 69 | 52 | 29.696 | 9.216 | 7.087 | 134.642 | 29.713 | 28.401 | 28.27 | 600.368 | 26.158 | 26.94 | 1297.032 | 27.219 | 27.468 | 36.591 | 23.001 | 2.3 | 1.8 | 0 | 0.8 | 0.2
2483 | 30/07/2025 10:26:02.894 | 97.104 | 79 | 100 | 70 | 51 | 27.283 | 9.518 | 7.061 | 134.583 | 29.722 | 28.377 | 28.287 | 600.59 | 26.143 | 26.936 | 1297.14 | 27.206 | 27.447 | 36.548 | 20.001 | 2.4 | 1.8 | 0.6 | 0 | 0.2
2484 | 30/07/2025 10:26:04.530 | 96.984 | 80 | 100 | 70 | 52 | 30.724 | 9.288 | 7.06 | 134.525 | 29.734 | 28.404 | 28.304 | 600.758 | 26.158 | 26.924 | 1306.756 | 27.215 | 27.419 | 36.316 | 23.001 | 3.2 | 0.8 | 0.7 | 0.5 | 0.2
2485 | 30/07/2025 10:26:06.167 | 97.488 | 81 | 100 | 70 | 52 | 27.262 | 9.288 | 7.061 | 134.744 | 29.737 | 28.401 | 28.283 | 600.615 | 26.146 | 26.93 | 1307.068 | 27.195 | 27.443 | 36.635 | 23.001 | 3.2 | 0.8 | 0.7 | 0.5 | 0.2
2486 | 30/07/2025 10:26:07.804 | 97.92 | 79 | 100 | 71 | 53 | 29.76 | 9.287 | 7.06 | 134.706 | 29.716 | 28.399 | 28.272 | 600.554 | 26.13 | 26.923 | 1301.219 | 27.176 | 27.451 | 36.724 | 27.001 | 3.4 | 0.8 | 0.6 | 0.2 | 0.2
2487 | 30/07/2025 10:26:09.446 | 98.016 | 79 | 100 | 70 | 52 | 31.368 | 9.293 | 7.072 | 134.501 | 29.702 | 28.386 | 28.252 | 600.366 | 26.149 | 26.914 | 1308.55 | 27.23 | 27.443 | 36.771 | 24.001 | 4.2 | 1.7 | 0.6 | 0.8 | 0.2
2488 | 30/07/2025 10:26:11.082 | 98.376 | 82 | 99 | 70 | 52 | 29.162 | 9.578 | 7.067 | 134.697 | 29.734 | 28.391 | 28.297 | 600.631 | 26.156 | 26.921 | 1316.721 | 27.206 | 27.436 | 36.643 | 26.001 | 2.8 | 1.7 | 0.3 | 0.1 | 0.2
2489 | 30/07/2025 10:26:12.719 | 98.76 | 81 | 100 | 71 | 51 | 27.711 | 9.506 | 7.088 | 134.374 | 29.715 | 28.407 | 28.286 | 600.636 | 26.165 | 26.912 | 1307.342 | 27.214 | 27.446 | 36.676 | 28.001 | 2.8 | 1.1 | 0 | 0 | 0.2
2490 | 30/07/2025 10:26:14.352 | 99.096 | 82 | 100 | 70 | 51 | 30.956 | 9.433 | 7.089 | 134.811 | 29.719 | 28.405 | 28.291 | 600.588 | 26.159 | 26.928 | 1312.135 | 27.195 | 27.461 | 36.887 | 28.001 | 2.8 | 1.1 | 0 | 0 | 0.2
2491 | 30/07/2025 10:26:15.987 | 98.52 | 81 | 100 | 70 | 53 | 27.13 | 9.498 | 7.088 | 134.597 | 29.705 | 28.406 | 28.261 | 600.743 | 26.166 | 26.931 | 1307.09 | 27.2 | 27.458 | 36.806 | 25.001 | 4 | 1.1 | 1 | 0.5 | 0.2
2492 | 30/07/2025 10:26:17.622 | 98.232 | 82 | 100 | 70 | 52 | 30.238 | 9.467 | 7.136 | 134.733 | 29.708 | 28.368 | 28.289 | 600.566 | 26.17 | 26.947 | 1306.912 | 27.222 | 27.455 | 36.601 | 29.001 | 3.1 | 2.7 | 0.7 | 0 | 0.3
2493 | 30/07/2025 10:26:19.256 | 98.04 | 79 | 100 | 70 | 52 | 31.329 | 9.294 | 7.135 | 134.42 | 29.709 | 28.395 | 28.309 | 600.576 | 26.165 | 26.946 | 1299.753 | 27.206 | 27.44 | 36.556 | 30.001 | 1.1 | 2.7 | 0.9 | 0.5 | 0.2
2494 | 30/07/2025 10:26:20.892 | 97.728 | 81 | 100 | 70 | 52 | 28.365 | 9.505 | 7.137 | 134.38 | 29.694 | 28.41 | 28.272 | 600.539 | 26.168 | 26.963 | 1296.97 | 27.2 | 27.451 | 36.811 | 27.001 | 1.1 | 1.2 | 0.9 | 0.5 | 0.2
2495 | 30/07/2025 10:26:22.529 | 97.512 | 78 | 100 | 71 | 52 | 28.048 | 9.429 | 7.071 | 134.987 | 29.718 | 28.404 | 28.273 | 600.689 | 26.18 | 26.964 | 1295.139 | 27.179 | 27.447 | 36.864 | 27.001 | 2.3 | 1.2 | 1.3 | 0 | 0.2
2496 | 30/07/2025 10:26:24.163 | 98.04 | 79 | 100 | 71 | 52 | 31.117 | 9.521 | 7.069 | 134.638 | 29.826 | 28.385 | 28.271 | 600.477 | 26.158 | 26.942 | 1293.868 | 27.232 | 27.461 | 36.747 | 27.001 | 2.3 | 1.2 | 1.3 | 0 | 0.2
2497 | 30/07/2025 10:26:25.801 | 98.472 | 82 | 100 | 71 | 52 | 27.291 | 9.492 | 7.07 | 134.68 | 29.861 | 28.378 | 28.297 | 601.459 | 26.158 | 26.945 | 1288.02 | 27.204 | 27.443 | 36.739 | 28.001 | 2.3 | 0.8 | 1.3 | 0 | 0.2
2498 | 30/07/2025 10:26:27.447 | 98.016 | 80 | 100 | 70 | 51 | 30.726 | 9.434 | 7.06 | 134.334 | 29.854 | 28.41 | 28.289 | 601.993 | 26.159 | 26.939 | 1287.248 | 27.22 | 27.437 | 36.447 | 24.001 | 1.8 | 1.8 | 0.7 | 0.5 | 0.2
2499 | 30/07/2025 10:26:29.083 | 98.256 | 78 | 100 | 70 | 52 | 31.305 | 9.579 | 7.061 | 134.721 | 29.865 | 28.391 | 28.276 | 600.836 | 26.164 | 26.935 | 1295.266 | 27.187 | 27.448 | 36.882 | 27.001 | 1.5 | 1 | 1.2 | 0.2 | 0.2
2500 | 30/07/2025 10:26:30.721 | 98.4 | 81 | 100 | 70 | 53 | 27.869 | 9.524 | 7.059 | 134.831 | 29.723 | 28.403 | 28.285 | 600.598 | 26.151 | 26.944 | 1297.211 | 27.19 | 27.466 | 36.759 | 28.001 | 2.6 | 1 | 1.5 | 1.1 | 0.2
2501 | 30/07/2025 10:26:32.359 | 98.52 | 82 | 100 | 70 | 52 | 28.684 | 9.476 | 7.06 | 134.553 | 29.725 | 28.376 | 28.278 | 600.458 | 26.155 | 26.956 | 1306.6 | 27.224 | 27.457 | 36.565 | 28.001 | 2.6 | 1 | 1.5 | 1.1 | 0.2
2502 | 30/07/2025 10:26:33.998 | 98.76 | 81 | 100 | 70 | 52 | 29.015 | 9.451 | 7.057 | 134.674 | 29.87 | 28.373 | 28.31 | 600.481 | 26.149 | 26.937 | 1306.676 | 27.214 | 27.449 | 36.31 | 27.001 | 2.4 | 2.4 | 0.9 | 0 | 0.2
2503 | 30/07/2025 10:26:35.633 | 99.072 | 81 | 100 | 71 | 52 | 27.618 | 9.434 | 7.07 | 134.212 | 29.87 | 28.398 | 28.271 | 600.424 | 26.143 | 26.941 | 1308.647 | 27.202 | 27.434 | 36.541 | 29.001 | 4.8 | 2.4 | 1.1 | 0.5 | 0.2
2504 | 30/07/2025 10:26:37.269 | 98.88 | 79 | 100 | 70 | 52 | 30.964 | 9.503 | 7.07 | 134.883 | 29.878 | 28.402 | 28.29 | 600.509 | 26.164 | 26.934 | 1307.185 | 27.167 | 27.459 | 36.738 | 26.001 | 4.8 | 1.2 | 1.1 | 0.5 | 0.2
2505 | 30/07/2025 10:26:38.908 | 99.072 | 81 | 100 | 71 | 52 | 31.094 | 9.433 | 7.071 | 134.693 | 29.877 | 28.407 | 28.268 | 600.528 | 26.138 | 26.924 | 1299.599 | 27.214 | 27.454 | 36.715 | 25.001 | 1.2 | 2.8 | 0.6 | 0.5 | 0.2
2506 | 30/07/2025 10:26:40.542 | 98.832 | 81 | 100 | 70 | 52 | 27.602 | 9.508 | 7.073 | 134.532 | 29.884 | 28.375 | 28.273 | 600.575 | 26.153 | 26.915 | 1299.167 | 27.215 | 27.438 | 36.616 | 25.001 | 3.8 | 3 | 0.6 | 0.5 | 0.2
2507 | 30/07/2025 10:26:42.181 | 98.856 | 81 | 100 | 71 | 52 | 29.243 | 9.508 | 7.087 | 134.306 | 29.866 | 28.403 | 28.298 | 602.024 | 26.136 | 26.903 | 1289.895 | 27.209 | 27.415 | 36.293 | 25.001 | 3.8 | 3 | 0.6 | 0.5 | 0.2
2508 | 30/07/2025 10:26:43.822 | 98.232 | 81 | 100 | 71 | 53 | 28.67 | 9.434 | 7.092 | 134.448 | 29.872 | 28.401 | 28.29 | 602.038 | 26.154 | 26.917 | 1285.394 | 27.204 | 27.437 | 36.633 | 20.001 | 2.9 | 3 | 0.9 | 0.2 | 0.2
2509 | 30/07/2025 10:26:45.457 | 98.376 | 79 | 100 | 70 | 51 | 28.089 | 9.582 | 7.121 | 134.623 | 29.873 | 28.399 | 28.284 | 601.994 | 26.134 | 26.909 | 1277.063 | 27.184 | 27.462 | 36.67 | 27.001 | 2.9 | 2.6 | 0.9 | 0.2 | 0.2
2510 | 30/07/2025 10:26:47.092 | 97.896 | 80 | 99 | 71 | 53 | 31.109 | 9.288 | 7.088 | 134.616 | 29.862 | 28.386 | 28.247 | 601.924 | 26.156 | 26.92 | 1276.852 | 27.212 | 27.448 | 36.673 | 26.001 | 2.9 | 2.6 | 0.1 | 1.2 | 0.2
2511 | 30/07/2025 10:26:48.728 | 97.488 | 78 | 100 | 71 | 52 | 30.796 | 9.426 | 7.087 | 134.552 | 29.881 | 28.383 | 28.299 | 602.104 | 26.16 | 26.917 | 1284.242 | 27.202 | 27.442 | 36.509 | 31.001 | 2.9 | 2.4 | 0.1 | 1.2 | 0.2
2512 | 30/07/2025 10:26:50.365 | 96.72 | 77 | 100 | 70 | 53 | 27.225 | 9.436 | 7.125 | 134.429 | 29.852 | 28.412 | 28.286 | 602.132 | 26.166 | 26.93 | 1282.304 | 27.213 | 27.448 | 36.498 | 28.001 | 2.3 | 2.6 | 0.6 | 0.5 | 0.3
2513 | 30/07/2025 10:26:52.022 | 96.72 | 78 | 100 | 69 | 53 | 31.262 | 9.428 | 7.122 | 134.557 | 29.868 | 28.397 | 28.288 | 602.057 | 26.148 | 26.935 | 1284.938 | 27.188 | 27.448 | 36.627 | 28.001 | 2.3 | 2.6 | 0.6 | 0.5 | 0.3
2514 | 30/07/2025 10:26:53.657 | 96.888 | 78 | 100 | 70 | 52 | 27.92 | 9.439 | 7.124 | 134.663 | 29.866 | 28.416 | 28.262 | 602.046 | 26.17 | 26.958 | 1293.09 | 27.203 | 27.462 | 36.567 | 29.001 | 2.1 | 3.9 | 0.3 | 0.1 | 0.3
2515 | 30/07/2025 10:26:55.291 | 97.32 | 81 | 100 | 70 | 53 | 28.534 | 9.504 | 7.122 | 134.742 | 29.853 | 28.383 | 28.279 | 601.872 | 26.169 | 26.941 | 1284.744 | 27.216 | 27.445 | 36.673 | 26.001 | 2.6 | 3.9 | 0.6 | 0 | 0.2
2516 | 30/07/2025 10:26:56.927 | 97.632 | 79 | 100 | 70 | 52 | 31.179 | 9.582 | 7.123 | 134.508 | 29.852 | 28.392 | 28.298 | 602.054 | 26.161 | 26.95 | 1277.455 | 27.211 | 27.441 | 36.357 | 26.001 | 5 | 3.9 | 0.1 | 1 | 0.2
2517 | 30/07/2025 10:26:58.567 | 97.416 | 79 | 100 | 70 | 52 | 30.288 | 9.3 | 7.136 | 134.476 | 29.84 | 28.397 | 28.28 | 601.842 | 26.158 | 26.949 | 1284.417 | 27.201 | 27.443 | 36.627 | 26.001 | 2.4 | 3.9 | 0.6 | 0.9 | 0.2
2518 | 30/07/2025 10:27:00.202 | 97.584 | 81 | 100 | 70 | 51 | 27.114 | 9.42 | 7.135 | 134.913 | 29.862 | 28.402 | 28.295 | 600.688 | 26.18 | 26.936 | 1289.161 | 27.177 | 27.458 | 36.646 | 26.001 | 2.4 | 3.9 | 0.6 | 0.9 | 0.2
2519 | 30/07/2025 10:27:01.843 | 97.728 | 79 | 100 | 70 | 54 | 31.162 | 9.286 | 7.138 | 134.781 | 29.851 | 28.399 | 28.265 | 600.496 | 26.159 | 26.946 | 1288.978 | 27.184 | 27.453 | 36.707 | 27.001 | 3.6 | 0.9 | 0.6 | 0.2 | 0.2
2520 | 30/07/2025 10:27:03.479 | 97.272 | 79 | 100 | 70 | 53 | 27.387 | 9.443 | 7.121 | 134.647 | 29.874 | 28.386 | 28.294 | 600.564 | 26.163 | 26.94 | 1290.242 | 27.209 | 27.451 | 36.591 | 28.001 | 3.5 | 0.9 | 0.1 | 0 | 0.2
2521 | 30/07/2025 10:27:05.114 | 97.944 | 79 | 100 | 70 | 52 | 29.179 | 9.583 | 7.122 | 134.335 | 29.869 | 28.412 | 28.282 | 600.529 | 26.167 | 26.943 | 1294.028 | 27.224 | 27.439 | 36.405 | 28.001 | 4.8 | 4.4 | 0.9 | 0 | 0.1
2522 | 30/07/2025 10:27:06.750 | 97.704 | 80 | 100 | 71 | 52 | 31.164 | 9.427 | 7.123 | 134.776 | 29.883 | 28.402 | 28.286 | 600.535 | 26.161 | 26.943 | 1279.244 | 27.197 | 27.444 | 36.716 | 29.001 | 2.3 | 4.4 | 0.4 | 0.6 | 0.1
2523 | 30/07/2025 10:27:08.388 | 98.448 | 79 | 100 | 70 | 54 | 29.681 | 9.511 | 7.149 | 134.724 | 29.876 | 28.408 | 28.276 | 600.436 | 26.144 | 26.939 | 1276.93 | 27.189 | 27.458 | 36.639 | 28.001 | 4.5 | 1.2 | 2.1 | 1.1 | 0.1
2524 | 30/07/2025 10:27:10.026 | 98.064 | 78 | 100 | 71 | 52 | 31.065 | 9.697 | 7.152 | 134.746 | 29.898 | 28.395 | 28.258 | 599.629 | 26.162 | 26.935 | 1281.574 | 27.205 | 27.445 | 36.658 | 28.001 | 4.5 | 1.2 | 2.1 | 1.1 | 0.1
2525 | 30/07/2025 10:27:11.665 | 98.184 | 78 | 100 | 70 | 52 | 30.796 | 9.594 | 7.123 | 134.658 | 29.861 | 28.369 | 28.293 | 599.335 | 26.149 | 26.921 | 1292.89 | 27.22 | 27.453 | 36.678 | 21.001 | 3.5 | 1.2 | 1.1 | 0.2 | 0.1
2526 | 30/07/2025 10:27:13.300 | 98.352 | 81 | 100 | 70 | 52 | 27.258 | 9.317 | 7.125 | 134.364 | 29.871 | 28.4 | 28.268 | 597.994 | 26.144 | 26.933 | 1287.847 | 27.205 | 27.433 | 36.519 | 23.001 | 3.5 | 1.8 | 1.1 | 0.2 | 0.1
2527 | 30/07/2025 10:27:14.933 | 98.232 | 79 | 100 | 70 | 53 | 29.851 | 9.427 | 7.123 | 134.741 | 29.862 | 28.399 | 28.285 | 598.1 | 26.149 | 26.904 | 1286.659 | 27.172 | 27.447 | 36.792 | 28.001 | 2.9 | 2.3 | 1.1 | 1.7 | 0.1
2528 | 30/07/2025 10:27:16.570 | 98.208 | 81 | 100 | 70 | 52 | 31.392 | 9.292 | 7.123 | 134.621 | 29.853 | 28.413 | 28.273 | 597.999 | 26.146 | 26.925 | 1291.778 | 27.212 | 27.456 | 36.804 | 28.001 | 3.3 | 2.2 | 0 | 0.4 | 0
2529 | 30/07/2025 10:27:18.206 | 98.88 | 80 | 100 | 72 | 52 | 29.278 | 9.6 | 7.122 | 134.697 | 29.879 | 28.371 | 28.284 | 597.911 | 26.166 | 26.929 | 1297.231 | 27.212 | 27.454 | 36.695 | 28.001 | 3.3 | 2.2 | 0 | 0.4 | 0
2530 | 30/07/2025 10:27:19.845 | 98.64 | 80 | 100 | 70 | 52 | 31.178 | 9.592 | 7.122 | 134.455 | 29.868 | 28.373 | 28.308 | 598.042 | 26.156 | 26.925 | 1297.171 | 27.22 | 27.448 | 36.51 | 24.001 | 2 | 2.2 | 0.7 | 0 | 0.1
2531 | 30/07/2025 10:27:21.479 | 99.288 | 81 | 100 | 70 | 52 | 30.394 | 9.498 | 7.107 | 134.577 | 29.882 | 28.402 | 28.298 | 597.991 | 26.169 | 26.923 | 1298.801 | 27.206 | 27.453 | 36.588 | 29.001 | 3.4 | 0.8 | 0.3 | 0.5 | 0.1
2532 | 30/07/2025 10:27:23.115 | 99.336 | 81 | 100 | 71 | 51 | 27.157 | 9.578 | 7.071 | 134.785 | 29.849 | 28.411 | 28.281 | 598.051 | 26.16 | 26.927 | 1296.935 | 27.189 | 27.459 | 36.714 | 29.001 | 4.3 | 0.8 | 0.9 | 0.1 | 0.1
2533 | 30/07/2025 10:27:24.751 | 99.72 | 82 | 100 | 70 | 52 | 30.215 | 9.322 | 7.073 | 134.604 | 29.869 | 28.39 | 28.266 | 597.961 | 26.161 | 26.932 | 1296.737 | 27.212 | 27.45 | 36.712 | 27.001 | 4.3 | 2.1 | 0.9 | 0.1 | 0.1
2534 | 30/07/2025 10:27:26.385 | 99.768 | 83 | 100 | 70 | 51 | 31.443 | 9.499 | 7.067 | 134.585 | 29.864 | 28.378 | 28.302 | 597.996 | 26.168 | 26.931 | 1296.544 | 27.209 | 27.445 | 36.521 | 33.001 | 3.1 | 2.1 | 0.1 | 0 | 0.1
2535 | 30/07/2025 10:27:28.030 | 99.816 | 82 | 100 | 70 | 52 | 29.122 | 9.293 | 7.069 | 134.473 | 29.863 | 28.385 | 28.293 | 597.996 | 26.163 | 26.953 | 1301.728 | 27.206 | 27.431 | 36.443 | 33.001 | 3.1 | 2.1 | 0.1 | 0 | 0.1
2536 | 30/07/2025 10:27:29.664 | 100.104 | 82 | 100 | 70 | 52 | 31.265 | 9.289 | 7.071 | 134.596 | 29.866 | 28.401 | 28.304 | 598.23 | 26.146 | 26.942 | 1288.409 | 27.193 | 27.457 | 36.562 | 28.001 | 2 | 1.8 | 0.9 | 0 | 0.1
2537 | 30/07/2025 10:27:31.300 | 100.032 | 83 | 100 | 70 | 52 | 29.76 | 9.286 | 7.071 | 134.55 | 29.84 | 28.392 | 28.265 | 598.116 | 26.155 | 26.953 | 1284.733 | 27.204 | 27.466 | 34.874 | 23.001 | 1.9 | 1.8 | 1.9 | 0.5 | 0.2
2538 | 30/07/2025 10:27:32.934 | 100.248 | 82 | 100 | 70 | 53 | 27.251 | 9.285 | 7.069 | 134.758 | 29.866 | 28.382 | 28.282 | 598.048 | 26.18 | 26.951 | 1276.962 | 27.214 | 27.458 | 35.037 | 29.001 | 2.4 | 1.9 | 1.3 | 0 | 0.1
2539 | 30/07/2025 10:27:34.569 | 99.648 | 83 | 100 | 70 | 52 | 30.633 | 9.289 | 7.069 | 134.569 | 29.858 | 28.4 | 28.299 | 597.948 | 26.161 | 26.936 | 1276.868 | 27.216 | 27.45 | 35.8 | 22.001 | 2.9 | 1.9 | 1.7 | 0 | 0.1
2540 | 30/07/2025 10:27:36.204 | 99.744 | 82 | 100 | 70 | 52 | 31.354 | 9.285 | 7.073 | 134.407 | 29.852 | 28.402 | 28.28 | 598.051 | 26.161 | 26.953 | 1284.394 | 27.194 | 27.435 | 36.511 | 22.001 | 2.9 | 1.9 | 1.7 | 0 | 0.1
2541 | 30/07/2025 10:27:37.840 | 99.456 | 83 | 100 | 72 | 52 | 29.715 | 9.432 | 7.072 | 134.727 | 29.857 | 28.409 | 28.279 | 598.203 | 26.162 | 26.936 | 1277.548 | 27.206 | 27.476 | 36.6 | 28.001 | 2 | 2 | 0.8 | 0 | 0.2
2542 | 30/07/2025 10:27:39.476 | 99.384 | 81 | 100 | 70 | 52 | 31.369 | 9.432 | 7.072 | 134.726 | 29.874 | 28.391 | 28.265 | 597.94 | 26.167 | 26.938 | 1276.945 | 27.192 | 27.447 | 36.577 | 26.001 | 3.1 | 2 | 0.3 | 0.5 | 0.2
2543 | 30/07/2025 10:27:41.111 | 99.336 | 81 | 100 | 70 | 52 | 29.022 | 9.512 | 7.069 | 134.696 | 29.883 | 28.384 | 28.289 | 598.204 | 26.147 | 26.931 | 1272.169 | 27.217 | 27.446 | 36.5 | 25.001 | 2.3 | 2.3 | 0 | 0.1 | 0.2
2544 | 30/07/2025 10:27:42.748 | 98.856 | 81 | 100 | 70 | 52 | 27.628 | 9.574 | 7.071 | 134.41 | 29.866 | 28.401 | 28.291 | 598.006 | 26.15 | 26.942 | 1272.946 | 27.22 | 27.443 | 36.587 | 21.001 | 2.4 | 2.3 | 0.9 | 0.5 | 0.2
2545 | 30/07/2025 10:27:44.383 | 98.376 | 81 | 100 | 71 | 52 | 30.943 | 9.549 | 7.073 | 134.764 | 29.9 | 28.393 | 28.287 | 597.998 | 26.165 | 26.943 | 1284.384 | 27.187 | 27.449 | 36.757 | 27.001 | 3 | 1.9 | 0.7 | 0.6 | 0.1
2546 | 30/07/2025 10:27:46.024 | 97.536 | 78 | 100 | 71 | 54 | 31.186 | 9.456 | 7.07 | 134.812 | 29.862 | 28.399 | 28.276 | 598.143 | 26.149 | 26.93 | 1285.397 | 27.188 | 27.474 | 36.544 | 27.001 | 3 | 1.9 | 0.7 | 0.6 | 0.1
2547 | 30/07/2025 10:27:47.660 | 97.632 | 78 | 100 | 71 | 52 | 30.347 | 9.208 | 7.071 | 134.661 | 29.888 | 28.393 | 28.256 | 598.034 | 26.17 | 26.929 | 1279.954 | 27.201 | 27.457 | 36.658 | 28.001 | 1.7 | 1.9 | 0.6 | 0.5 | 0.1
2548 | 30/07/2025 10:27:49.295 | 97.512 | 79 | 100 | 71 | 52 | 31.464 | 9.287 | 7.116 | 134.525 | 29.869 | 28.38 | 28.307 | 598.048 | 26.146 | 26.92 | 1277.134 | 27.227 | 27.46 | 36.625 | 25.001 | 4.6 | 1.1 | 0.9 | 0.6 | 0.1
2549 | 30/07/2025 10:27:50.932 | 97.392 | 79 | 100 | 71 | 54 | 28.708 | 9.289 | 7.13 | 134.422 | 29.874 | 28.407 | 28.282 | 598.127 | 26.152 | 26.934 | 1277.503 | 27.207 | 27.432 | 36.616 | 28.001 | 2.7 | 1.1 | 1.7 | 0.5 | 0.2
2550 | 30/07/2025 10:27:52.569 | 97.752 | 80 | 100 | 70 | 53 | 28.238 | 9.285 | 7.07 | 134.758 | 29.879 | 28.402 | 28.29 | 598.051 | 26.144 | 26.915 | 1267.695 | 27.187 | 27.451 | 34.962 | 31.001 | 4.1 | 3 | 1.5 | 0.8 | 0.2
2551 | 30/07/2025 10:27:54.201 | 98.136 | 81 | 100 | 70 | 52 | 31.143 | 9.468 | 7.071 | 134.57 | 29.863 | 28.398 | 28.268 | 598.07 | 26.155 | 26.918 | 1264.458 | 27.218 | 27.459 | 34.853 | 31.001 | 4.1 | 3 | 1.5 | 0.8 | 0.2
2552 | 30/07/2025 10:27:55.843 | 98.136 | 79 | 100 | 71 | 53 | 27.381 | 9.502 | 7.07 | 134.735 | 29.871 | 28.384 | 28.279 | 598.207 | 26.159 | 26.909 | 1267.007 | 27.22 | 27.455 | 34.702 | 26.001 | 3 | 3 | 1.8 | 0.1 | 0.2
2553 | 30/07/2025 10:27:57.477 | 98.616 | 82 | 100 | 70 | 52 | 30.812 | 9.135 | 7.071 | 134.436 | 29.858 | 28.371 | 28.277 | 597.981 | 26.156 | 26.938 | 1276.399 | 27.22 | 27.439 | 34.574 | 31.001 | 2.7 | 3.1 | 0.7 | 0.5 | 0.2
2554 | 30/07/2025 10:27:59.111 | 98.712 | 80 | 100 | 70 | 52 | 31.395 | 9.432 | 7.07 | 134.551 | 29.874 | 28.401 | 28.292 | 598.088 | 26.18 | 26.929 | 1267.486 | 27.196 | 27.433 | 34.727 | 26.001 | 1.9 | 3.1 | 0.7 | 0.5 | 0.2
2555 | 30/07/2025 10:28:00.747 | 98.904 | 82 | 100 | 70 | 52 | 28.086 | 9.184 | 7.07 | 134.506 | 29.856 | 28.403 | 28.277 | 597.963 | 26.166 | 26.949 | 1269.434 | 27.188 | 27.46 | 34.957 | 27.001 | 1.1 | 2.4 | 0.6 | 1 | 0.2
2556 | 30/07/2025 10:28:02.382 | 99.48 | 81 | 100 | 71 | 50 | 28.575 | 9.215 | 7.073 | 134.592 | 29.851 | 28.389 | 28.252 | 597.974 | 26.158 | 26.96 | 1284.743 | 27.206 | 27.453 | 36.636 | 27.001 | 3.6 | 2.4 | 0.9 | 1.3 | 0.2
2557 | 30/07/2025 10:28:04.025 | 99.24 | 81 | 100 | 70 | 53 | 29.297 | 9.285 | 7.068 | 134.634 | 29.852 | 28.39 | 28.279 | 598.007 | 26.166 | 26.964 | 1287.103 | 27.241 | 27.459 | 36.66 | 27.001 | 3.6 | 2.4 | 0.9 | 1.3 | 0.2
2558 | 30/07/2025 10:28:05.663 | 99.96 | 82 | 100 | 70 | 52 | 27.551 | 9.567 | 7.095 | 134.534 | 29.845 | 28.389 | 28.288 | 598.115 | 26.171 | 26.955 | 1287.391 | 27.222 | 27.435 | 36.577 | 28.001 | 2.4 | 2.5 | 0.6 | 0 | 0.2
2559 | 30/07/2025 10:28:07.299 | 99.696 | 81 | 100 | 71 | 53 | 30.947 | 9.29 | 7.123 | 134.517 | 29.854 | 28.406 | 28.294 | 598.112 | 26.154 | 26.939 | 1272.908 | 27.199 | 27.449 | 36.516 | 24.001 | 3.4 | 2.5 | 1.2 | 0.6 | 0.2
2560 | 30/07/2025 10:28:08.936 | 98.832 | 81 | 99 | 70 | 52 | 31.234 | 9.285 | 7.073 | 134.497 | 29.864 | 28.401 | 28.273 | 598.066 | 26.158 | 26.94 | 1269.583 | 27.2 | 27.455 | 36.75 | 23.001 | 3.4 | 1.1 | 1.2 | 0.6 | 0.2
2561 | 30/07/2025 10:28:10.572 | 97.944 | 81 | 100 | 70 | 52 | 27.556 | 9.478 | 7.068 | 134.638 | 29.88 | 28.385 | 28.266 | 599.248 | 26.175 | 26.931 | 1269.938 | 27.206 | 27.448 | 36.738 | 26.001 | 2.7 | 2 | 1.3 | 0.6 | 0.2
2562 | 30/07/2025 10:28:12.210 | 97.512 | 80 | 100 | 70 | 52 | 29.165 | 9.432 | 7.069 | 134.41 | 29.866 | 28.389 | 28.303 | 599.174 | 26.154 | 26.949 | 1272.156 | 27.221 | 27.459 | 36.582 | 26.001 | 2.7 | 2 | 1.3 | 0.6 | 0.2
2563 | 30/07/2025 10:28:13.847 | 97.512 | 78 | 100 | 70 | 52 | 28.389 | 9.439 | 7.071 | 134.633 | 29.87 | 28.398 | 28.3 | 599.161 | 26.161 | 26.937 | 1274.736 | 27.203 | 27.428 | 36.517 | 26.001 | 2.7 | 1.6 | 1.3 | 0.6 | 0.2
2564 | 30/07/2025 10:28:15.483 | 97.512 | 77 | 100 | 70 | 52 | 27.985 | 9.435 | 7.071 | 134.649 | 29.875 | 28.41 | 28.295 | 599.506 | 26.166 | 26.949 | 1284.816 | 27.199 | 27.471 | 36.644 | 24.001 | 4.1 | 1.1 | 0.9 | 0.5 | 0.1
2565 | 30/07/2025 10:28:17.121 | 97.848 | 79 | 100 | 69 | 52 | 31.053 | 9.578 | 7.089 | 134.687 | 29.884 | 28.394 | 28.262 | 599.377 | 26.169 | 26.939 | 1277.398 | 27.195 | 27.455 | 36.631 | 23.001 | 2.7 | 2.3 | 1.5 | 0.7 | 0.1
2566 | 30/07/2025 10:28:18.766 | 97.104 | 79 | 100 | 70 | 52 | 30.816 | 9.501 | 7.062 | 134.634 | 29.879 | 28.384 | 28.276 | 600.642 | 26.151 | 26.921 | 1270.55 | 27.221 | 27.444 | 36.615 | 25.001 | 2 | 2.3 | 0.3 | 1.2 | 0.2
2567 | 30/07/2025 10:28:20.404 | 98.04 | 79 | 100 | 71 | 52 | 27.233 | 9.525 | 7.06 | 134.348 | 29.861 | 28.398 | 28.288 | 600.491 | 26.144 | 26.942 | 1270.145 | 27.219 | 27.438 | 36.565 | 22.001 | 3.1 | 1.7 | 0.6 | 0.3 | 0.2
2568 | 30/07/2025 10:28:22.045 | 98.232 | 79 | 100 | 70 | 51 | 31.377 | 9.441 | 7.06 | 134.547 | 29.872 | 28.408 | 28.292 | 600.614 | 26.159 | 26.916 | 1276.621 | 27.209 | 27.424 | 36.687 | 22.001 | 3.1 | 1.7 | 0.6 | 0.3 | 0.2
2569 | 30/07/2025 10:28:23.679 | 98.712 | 81 | 100 | 70 | 52 | 28.006 | 9.311 | 7.062 | 134.713 | 29.871 | 28.398 | 28.276 | 600.483 | 26.149 | 26.926 | 1277.252 | 27.186 | 27.461 | 36.778 | 26.001 | 2.4 | 1.7 | 0.7 | 0.5 | 0.1
2570 | 30/07/2025 10:28:25.311 | 98.712 | 81 | 100 | 70 | 52 | 28.765 | 9.195 | 7.06 | 134.755 | 29.881 | 28.395 | 28.267 | 600.765 | 26.146 | 26.917 | 1281.371 | 27.208 | 27.449 | 36.745 | 26.001 | 3 | 1.5 | 0.3 | 1.1 | 0.1
2571 | 30/07/2025 10:28:26.948 | 99.096 | 81 | 100 | 71 | 52 | 31.196 | 9.402 | 7.059 | 133.125 | 29.86 | 28.376 | 28.299 | 600.573 | 26.145 | 26.912 | 1287.413 | 27.225 | 27.459 | 36.689 | 24.001 | 3 | 1.5 | 0.6 | 0.1 | 0.1
2572 | 30/07/2025 10:28:28.588 | 99.216 | 82 | 100 | 70 | 52 | 30.401 | 9.286 | 7.055 | 133.12 | 29.864 | 28.4 | 28.297 | 600.394 | 26.162 | 26.93 | 1289.074 | 27.214 | 27.437 | 36.487 | 24.001 | 4.2 | 0.8 | 0.9 | 0.5 | 0.1
2573 | 30/07/2025 10:28:30.224 | 99.36 | 80 | 100 | 71 | 53 | 27.172 | 9.439 | 7.086 | 133.325 | 29.872 | 28.403 | 28.307 | 600.534 | 26.158 | 26.925 | 1299.461 | 27.185 | 27.458 | 36.652 | 24.001 | 4.2 | 0.8 | 0.9 | 0.5 | 0.1
2574 | 30/07/2025 10:28:31.859 | 100.152 | 82 | 100 | 71 | 52 | 31.215 | 9.431 | 7.087 | 133.143 | 29.876 | 28.397 | 28.273 | 600.521 | 26.184 | 26.927 | 1302.794 | 27.179 | 27.467 | 36.724 | 33.001 | 3.1 | 0.8 | 0.2 | 0 | 0.1
2575 | 30/07/2025 10:28:33.497 | 100.176 | 82 | 100 | 70 | 52 | 27.596 | 9.553 | 7.12 | 133.209 | 29.859 | 28.391 | 28.265 | 600.57 | 26.158 | 26.942 | 1306.547 | 27.217 | 27.454 | 36.417 | 32.001 | 2 | 2.5 | 0.6 | 0 | 0.1
2576 | 30/07/2025 10:28:35.133 | 100.512 | 83 | 100 | 71 | 53 | 29.232 | 9.289 | 7.093 | 133.017 | 29.868 | 28.364 | 28.293 | 600.597 | 26.16 | 27.022 | 1306.553 | 27.214 | 27.434 | 36.707 | 27.001 | 2.5 | 2.5 | 0.9 | 0.5 | 0.1
2577 | 30/07/2025 10:28:36.768 | 100.248 | 84 | 100 | 70 | 53 | 31.291 | 9.437 | 7.069 | 133.034 | 29.854 | 28.407 | 28.284 | 600.522 | 26.163 | 26.939 | 1295.501 | 27.208 | 27.437 | 36.393 | 27.001 | 2.7 | 2.8 | 1 | 1.2 | 0.1
2578 | 30/07/2025 10:28:38.403 | 100.008 | 82 | 100 | 70 | 52 | 29.929 | 9.434 | 7.072 | 133.116 | 29.832 | 28.424 | 28.282 | 600.566 | 26.151 | 27.071 | 1287.242 | 27.206 | 27.457 | 36.715 | 29.001 | 2.8 | 2.8 | 0.1 | 0.8 | 0.1
2579 | 30/07/2025 10:28:40.048 | 100.032 | 81 | 100 | 70 | 52 | 31.118 | 9.286 | 7.071 | 133.269 | 29.859 | 28.396 | 28.281 | 600.668 | 26.158 | 27.108 | 1287.59 | 27.181 | 27.448 | 36.553 | 29.001 | 2.8 | 2.8 | 0.1 | 0.8 | 0.1
2580 | 30/07/2025 10:28:41.687 | 99.984 | 81 | 100 | 71 | 52 | 30.939 | 9.429 | 7.085 | 133.14 | 29.854 | 28.382 | 28.276 | 600.637 | 26.155 | 27.126 | 1296.713 | 27.232 | 27.461 | 36.648 | 27.001 | 3.1 | 2.9 | 0 | 0.4 | 0.1
2581 | 30/07/2025 10:28:43.321 | 100.2 | 82 | 100 | 71 | 52 | 27.263 | 9.568 | 7.07 | 134.569 | 29.874 | 28.393 | 28.282 | 600.57 | 26.171 | 27.129 | 1292.281 | 27.21 | 27.436 | 36.621 | 28.001 | 2.6 | 2.9 | 0 | 0 | 0.1
2582 | 30/07/2025 10:28:44.959 | 100.176 | 83 | 100 | 71 | 51 | 29.676 | 9.58 | 7.071 | 134.585 | 29.866 | 28.412 | 28.296 | 600.5 | 26.157 | 27.1 | 1287.603 | 27.206 | 27.45 | 36.518 | 28.001 | 1.3 | 2.1 | 0.6 | 1.3 | 0.1
2583 | 30/07/2025 10:28:46.599 | 99.816 | 82 | 100 | 70 | 52 | 31.337 | 9.483 | 7.073 | 134.605 | 29.873 | 28.399 | 28.263 | 599.112 | 26.167 | 27.133 | 1296.829 | 27.183 | 27.461 | 36.71 | 27.001 | 1.2 | 2.1 | 0.7 | 0.9 | 0.1
2584 | 30/07/2025 10:28:48.234 | 99.936 | 81 | 100 | 70 | 52 | 29.088 | 9.428 | 7.076 | 134.568 | 29.88 | 28.389 | 28.257 | 599.322 | 26.152 | 27.119 | 1299.442 | 27.216 | 27.447 | 36.652 | 27.001 | 1.2 | 2.1 | 0.7 | 0.9 | 0.1
2585 | 30/07/2025 10:28:49.869 | 99.96 | 82 | 100 | 71 | 51 | 31.146 | 9.287 | 7.121 | 134.622 | 29.886 | 28.377 | 28.278 | 599.226 | 26.166 | 27.13 | 1296.858 | 27.212 | 27.45 | 36.613 | 27.001 | 2.9 | 1.6 | 0.7 | 0.6 | 0.2
2586 | 30/07/2025 10:28:51.502 | 99.792 | 82 | 100 | 71 | 52 | 30.245 | 9.291 | 7.122 | 134.591 | 29.893 | 28.4 | 28.304 | 599.484 | 26.155 | 27.111 | 1302.196 | 27.212 | 27.439 | 36.394 | 25.001 | 2.3 | 1.6 | 0.4 | 0.5 | 0.2
2587 | 30/07/2025 10:28:53.134 | 99.72 | 83 | 100 | 70 | 52 | 27.082 | 9.289 | 7.122 | 134.676 | 29.855 | 28.413 | 28.286 | 598.043 | 26.137 | 27.113 | 1299.548 | 27.213 | 27.454 | 36.635 | 31.001 | 3.9 | 1.7 | 0 | 0.8 | 0.2
2588 | 30/07/2025 10:28:54.770 | 99.624 | 82 | 100 | 71 | 53 | 30.224 | 9.135 | 7.136 | 134.822 | 29.879 | 28.394 | 28.261 | 597.978 | 26.14 | 27.103 | 1297.288 | 27.18 | 27.454 | 36.891 | 27.001 | 2.7 | 1.7 | 0.9 | 1.4 | 0.2
2589 | 30/07/2025 10:28:56.402 | 99.552 | 82 | 100 | 70 | 52 | 31.41 | 9.305 | 7.122 | 134.722 | 29.871 | 28.39 | 28.27 | 599.164 | 26.133 | 27.079 | 1297.132 | 27.218 | 27.463 | 36.682 | 23.001 | 4.6 | 1.9 | 0.7 | 0.6 | 0.2
2590 | 30/07/2025 10:28:58.035 | 99.504 | 82 | 100 | 70 | 52 | 29.208 | 9.287 | 7.12 | 134.809 | 29.888 | 28.385 | 28.301 | 599.386 | 26.16 | 27.111 | 1299.532 | 27.203 | 27.452 | 36.894 | 23.001 | 4.6 | 1.9 | 0.7 | 0.6 | 0.2
2591 | 30/07/2025 10:28:59.669 | 99.072 | 82 | 100 | 70 | 52 | 31.28 | 9.427 | 7.122 | 134.465 | 29.864 | 28.41 | 28.293 | 599.324 | 26.146 | 27.09 | 1291.047 | 27.218 | 27.432 | 36.589 | 27.001 | 2.1 | 1.9 | 0.7 | 0.8 | 0.2
2592 | 30/07/2025 10:29:01.303 | 98.616 | 81 | 100 | 71 | 52 | 29.828 | 9.443 | 7.124 | 134.884 | 29.869 | 28.403 | 28.266 | 599.253 | 26.152 | 27.11 | 1290.775 | 27.187 | 27.456 | 36.652 | 32.001 | 2.1 | 3.5 | 0.9 | 0.2 | 0.2
2593 | 30/07/2025 10:29:02.935 | 98.544 | 80 | 100 | 71 | 53 | 27.35 | 9.485 | 7.088 | 134.795 | 29.881 | 28.408 | 28.282 | 599.18 | 26.161 | 27.098 | 1296.986 | 27.197 | 27.455 | 36.607 | 29.001 | 2.9 | 3.5 | 1 | 0 | 0.2
2594 | 30/07/2025 10:29:04.567 | 97.848 | 80 | 100 | 72 | 52 | 30.726 | 9.431 | 7.086 | 134.428 | 29.852 | 28.371 | 28.293 | 598.01 | 26.163 | 27.116 | 1299.239 | 27.227 | 27.447 | 36.649 | 29.001 | 2.7 | 1.9 | 0.8 | 0.6 | 0.3
2595 | 30/07/2025 10:29:06.205 | 98.136 | 81 | 100 | 70 | 53 | 31.397 | 9.286 | 7.088 | 134.434 | 29.875 | 28.398 | 28.279 | 598.865 | 26.161 | 27.107 | 1302.344 | 27.204 | 27.426 | 36.595 | 29.001 | 2.7 | 1.9 | 0.8 | 0.6 | 0.3
2596 | 30/07/2025 10:29:07.840 | 98.28 | 81 | 100 | 70 | 52 | 29.779 | 9.288 | 7.089 | 134.441 | 29.853 | 28.406 | 28.266 | 599.317 | 26.152 | 27.126 | 1306.698 | 27.215 | 27.433 | 36.678 | 26.001 | 1.3 | 1.9 | 0.7 | 0.3 | 0.3
2597 | 30/07/2025 10:29:09.473 | 98.208 | 80 | 100 | 70 | 52 | 31.329 | 9.437 | 7.087 | 134.901 | 29.866 | 28.396 | 28.289 | 600.533 | 26.177 | 27.127 | 1307.075 | 27.178 | 27.461 | 36.682 | 27.001 | 2.8 | 2.3 | 0.6 | 0.5 | 0.2
2598 | 30/07/2025 10:29:11.109 | 98.4 | 82 | 99 | 70 | 53 | 29.35 | 9.507 | 7.072 | 134.716 | 29.851 | 28.392 | 28.267 | 600.637 | 26.167 | 27.123 | 1299.364 | 27.225 | 27.472 | 36.608 | 26.001 | 3 | 2.3 | 0.6 | 1.2 | 0.2
2599 | 30/07/2025 10:29:12.748 | 98.352 | 82 | 100 | 70 | 52 | 27.685 | 9.431 | 7.07 | 134.524 | 29.837 | 28.378 | 28.285 | 600.331 | 26.153 | 27.132 | 1299.72 | 27.208 | 27.445 | 36.634 | 27.001 | 2.1 | 2.1 | 0.6 | 0 | 0.2
2600 | 30/07/2025 10:29:14.380 | 97.92 | 79 | 100 | 70 | 52 | 31.003 | 9.189 | 7.059 | 134.621 | 29.847 | 28.403 | 28.29 | 601.888 | 26.156 | 27.108 | 1307.046 | 27.205 | 27.432 | 36.478 | 28.001 | 3.8 | 2.1 | 0.9 | 0.5 | 0.2
2601 | 30/07/2025 10:29:16.017 | 97.512 | 79 | 100 | 71 | 52 | 27.276 | 9.274 | 7.061 | 134.61 | 29.849 | 28.404 | 28.291 | 601.957 | 26.16 | 27.125 | 1311.597 | 27.192 | 27.446 | 36.651 | 28.001 | 3.8 | 2.1 | 0.9 | 0.5 | 0.2
2602 | 30/07/2025 10:29:17.651 | 97.392 | 79 | 100 | 70 | 52 | 30.373 | 9.313 | 7.058 | 134.704 | 29.868 | 28.404 | 28.291 | 602.044 | 26.156 | 27.107 | 1317.643 | 27.172 | 27.45 | 36.656 | 24.001 | 2.5 | 2.2 | 0.6 | 1.6 | 0.2
2603 | 30/07/2025 10:29:19.283 | 97.488 | 81 | 100 | 70 | 51 | 31.42 | 9.506 | 7.06 | 134.508 | 29.872 | 28.391 | 28.254 | 600.586 | 26.162 | 27.128 | 1321.904 | 27.245 | 27.457 | 36.678 | 26.001 | 2.1 | 2.2 | 0.6 | 1.5 | 0.2
2604 | 30/07/2025 10:29:20.920 | 97.44 | 78 | 100 | 70 | 53 | 28.6 | 9.49 | 7.06 | 134.768 | 29.898 | 28.386 | 28.291 | 600.462 | 26.173 | 27.117 | 1308.593 | 27.206 | 27.434 | 36.566 | 31.001 | 2.1 | 1.9 | 1.5 | 1.2 | 0.2
2605 | 30/07/2025 10:29:22.555 | 97.392 | 80 | 100 | 71 | 52 | 28.007 | 9.286 | 7.06 | 134.578 | 29.864 | 28.415 | 28.3 | 600.614 | 26.155 | 27.105 | 1306.736 | 27.213 | 27.455 | 36.554 | 26.001 | 2.5 | 1.9 | 2.3 | 0.3 | 0.2
2606 | 30/07/2025 10:29:24.191 | 97.512 | 81 | 100 | 71 | 52 | 31.122 | 9.377 | 7.072 | 134.542 | 29.874 | 28.398 | 28.275 | 600.502 | 26.156 | 27.124 | 1309.337 | 27.183 | 27.451 | 36.83 | 26.001 | 2.5 | 1.9 | 2.3 | 0.3 | 0.2
2607 | 30/07/2025 10:29:25.829 | 97.296 | 81 | 100 | 71 | 53 | 27.315 | 9.579 | 7.073 | 134.654 | 29.868 | 28.392 | 28.266 | 600.582 | 26.159 | 27.104 | 1313.507 | 27.193 | 27.469 | 36.739 | 22.001 | 1.9 | 1.6 | 0.7 | 0.9 | 0.2
2608 | 30/07/2025 10:29:27.476 | 97.392 | 79 | 100 | 70 | 54 | 30.636 | 9.306 | 7.102 | 134.674 | 29.875 | 28.381 | 28.282 | 600.8 | 26.149 | 27.122 | 1311.084 | 27.208 | 27.45 | 36.718 | 25.001 | 1.7 | 1.6 | 0.9 | 0.4 | 0.2
2609 | 30/07/2025 10:29:29.117 | 97.392 | 80 | 100 | 69 | 52 | 31.439 | 9.437 | 7.121 | 134.583 | 29.879 | 28.393 | 28.302 | 601.944 | 26.142 | 27.101 | 1297.571 | 27.209 | 27.429 | 36.542 | 26.001 | 1.9 | 1.4 | 1.1 | 0.5 | 0.2
2610 | 30/07/2025 10:29:30.752 | 97.056 | 79 | 100 | 71 | 53 | 28.058 | 9.349 | 7.124 | 134.321 | 29.862 | 28.412 | 28.256 | 601.966 | 26.132 | 27.102 | 1286.107 | 27.217 | 27.443 | 36.778 | 25.001 | 2.5 | 1.4 | 1.4 | 0.2 | 0.2
2611 | 30/07/2025 10:29:32.389 | 97.32 | 79 | 100 | 70 | 53 | 28.69 | 9.285 | 7.069 | 134.832 | 29.887 | 28.399 | 28.268 | 601.955 | 26.165 | 27.1 | 1276.786 | 27.175 | 27.456 | 36.674 | 25.001 | 1.5 | 2.9 | 0.6 | 0 | 0.2
2612 | 30/07/2025 10:29:34.025 | 97.344 | 80 | 100 | 70 | 51 | 29.151 | 9.34 | 7.073 | 134.595 | 29.866 | 28.393 | 28.263 | 601.996 | 26.155 | 27.109 | 1286.784 | 27.217 | 27.459 | 36.629 | 25.001 | 1.5 | 2.9 | 0.6 | 0 | 0.2
2613 | 30/07/2025 10:29:35.661 | 97.296 | 80 | 100 | 70 | 52 | 27.681 | 9.424 | 7.058 | 134.735 | 29.871 | 28.379 | 28.289 | 600.722 | 26.161 | 27.089 | 1290.665 | 27.203 | 27.442 | 36.605 | 28.001 | 2.8 | 2.9 | 0.6 | 0.5 | 0.2
2614 | 30/07/2025 10:29:37.298 | 97.512 | 80 | 100 | 70 | 52 | 30.996 | 9.294 | 7.061 | 134.422 | 29.867 | 28.405 | 28.287 | 600.415 | 26.146 | 27.077 | 1275.026 | 27.219 | 27.426 | 36.411 | 24.001 | 1.6 | 1.3 | 1.5 | 0.7 | 0.2
2615 | 30/07/2025 10:29:38.934 | 97.656 | 80 | 100 | 72 | 52 | 31.22 | 9.208 | 7.063 | 134.592 | 29.867 | 28.399 | 28.279 | 600.492 | 26.169 | 27.12 | 1275.212 | 27.177 | 27.459 | 36.631 | 29.001 | 4 | 1.3 | 1.2 | 0.3 | 0.3
2616 | 30/07/2025 10:29:40.567 | 97.824 | 79 | 100 | 71 | 52 | 27.5 | 9.289 | 7.005 | 134.796 | 29.866 | 28.403 | 28.284 | 600.665 | 26.174 | 27.116 | 1280.12 | 27.195 | 27.466 | 36.617 | 29.001 | 3 | 1.6 | 1.8 | 0.5 | 0.3
2617 | 30/07/2025 10:29:42.208 | 97.704 | 81 | 100 | 70 | 53 | 29.224 | 9.437 | 7.004 | 134.579 | 29.846 | 28.369 | 28.273 | 601.229 | 26.158 | 27.141 | 1287.101 | 27.233 | 27.468 | 36.7 | 29.001 | 3 | 1.6 | 1.8 | 0.5 | 0.3
2618 | 30/07/2025 10:29:43.852 | 98.088 | 81 | 100 | 70 | 52 | 28.604 | 9.433 | 7.001 | 134.67 | 29.864 | 28.389 | 28.292 | 601.947 | 26.159 | 27.109 | 1286.731 | 27.198 | 27.441 | 36.502 | 27.001 | 1.6 | 1.6 | 2 | 0.2 | 0.3
2619 | 30/07/2025 10:29:45.486 | 97.848 | 80 | 100 | 70 | 53 | 28.159 | 9.137 | 7.005 | 134.385 | 29.849 | 28.412 | 28.29 | 601.992 | 26.162 | 27.139 | 1282.155 | 27.217 | 27.445 | 36.496 | 27.001 | 3.2 | 1.8 | 1.6 | 0.8 | 0.3
2620 | 30/07/2025 10:29:47.121 | 97.056 | 78 | 100 | 71 | 52 | 31.136 | 9.28 | 7.059 | 134.786 | 29.854 | 28.404 | 28.289 | 600.989 | 26.176 | 27.123 | 1270.921 | 27.191 | 27.46 | 36.675 | 26.001 | 2 | 1.8 | 1 | 0.7 | 0.3
2621 | 30/07/2025 10:29:48.759 | 97.512 | 78 | 100 | 71 | 52 | 30.952 | 9.287 | 7.059 | 134.813 | 29.847 | 28.397 | 28.261 | 600.408 | 26.169 | 27.115 | 1270.272 | 27.221 | 27.465 | 36.642 | 25.001 | 2 | 1 | 1 | 0.7 | 0.3
2622 | 30/07/2025 10:29:50.399 | 97.56 | 78 | 100 | 70 | 52 | 27.387 | 9.279 | 7.06 | 134.572 | 29.85 | 28.377 | 28.275 | 600.659 | 26.15 | 27.13 | 1276.99 | 27.21 | 27.443 | 36.626 | 28.001 | 2.9 | 3.3 | 1.3 | 0.8 | 0.3
2623 | 30/07/2025 10:29:52.033 | 97.32 | 79 | 100 | 71 | 51 | 31.435 | 9.294 | 7.069 | 134.338 | 29.853 | 28.408 | 28.288 | 600.636 | 26.154 | 27.117 | 1276.99 | 27.225 | 27.444 | 36.409 | 28.001 | 2.9 | 3.3 | 1.3 | 0.8 | 0.3
2624 | 30/07/2025 10:29:53.668 | 97.392 | 79 | 100 | 70 | 52 | 27.998 | 9.344 | 7.072 | 134.387 | 29.866 | 28.406 | 28.266 | 600.546 | 26.157 | 27.11 | 1273.863 | 27.194 | 27.425 | 36.567 | 25.001 | 3.3 | 3.4 | 0.9 | 0.4 | 0.3
2625 | 30/07/2025 10:29:55.302 | 97.272 | 81 | 100 | 71 | 52 | 28.576 | 9.196 | 7.071 | 134.77 | 29.876 | 28.402 | 28.283 | 600.585 | 26.144 | 27.098 | 1267.334 | 27.172 | 27.452 | 36.691 | 24.001 | 3 | 3.4 | 0.7 | 0.6 | 0.2
2626 | 30/07/2025 10:29:56.938 | 96.888 | 78 | 100 | 70 | 52 | 31.168 | 9.141 | 7.062 | 134.568 | 29.869 | 28.388 | 28.246 | 600.523 | 26.146 | 27.135 | 1256.931 | 27.225 | 27.457 | 36.662 | 21.001 | 3.1 | 2.1 | 0.9 | 0.7 | 0.3
2627 | 30/07/2025 10:29:58.575 | 97.104 | 81 | 100 | 70 | 53 | 30.406 | 9.127 | 7.053 | 134.572 | 29.885 | 28.386 | 28.293 | 600.539 | 26.17 | 27.108 | 1265.023 | 27.207 | 27.433 | 36.127 | 20.001 | 2.8 | 2.1 | 0.4 | 0.6 | 0.2
2628 | 30/07/2025 10:30:00.211 | 97.752 | 81 | 100 | 69 | 52 | 27.204 | 9.226 | 7.004 | 134.555 | 29.864 | 28.42 | 28.285 | 600.431 | 26.161 | 27.104 | 1272.366 | 27.216 | 27.443 | 36.62 | 20.001 | 2.8 | 2.1 | 0.4 | 0.6 | 0.2
2629 | 30/07/2025 10:30:01.850 | 97.992 | 81 | 100 | 70 | 52 | 31.222 | 9.212 | 7.004 | 134.454 | 29.87 | 28.398 | 28.297 | 600.515 | 26.15 | 27.092 | 1270.541 | 27.193 | 27.442 | 36.629 | 26.001 | 2 | 2.5 | 0.9 | 0.8 | 0.2
2630 | 30/07/2025 10:30:03.487 | 97.776 | 79 | 100 | 71 | 52 | 27.681 | 9.288 | 7.005 | 134.644 | 29.873 | 28.414 | 28.28 | 602.007 | 26.129 | 27.104 | 1280.92 | 27.202 | 27.473 | 36.895 | 29.001 | 2.6 | 2.5 | 0.6 | 1.1 | 0.3
2631 | 30/07/2025 10:30:05.123 | 97.992 | 81 | 100 | 70 | 51 | 29.276 | 9.434 | 7.004 | 134.677 | 29.877 | 28.378 | 28.274 | 602.116 | 26.147 | 27.105 | 1277.046 | 27.222 | 27.443 | 36.855 | 24.001 | 1.6 | 1.5 | 0 | 0 | 0.2
2632 | 30/07/2025 10:30:06.757 | 98.4 | 81 | 100 | 70 | 52 | 31.345 | 9.486 | 7.002 | 134.641 | 29.881 | 28.394 | 28.292 | 602.234 | 26.141 | 27.08 | 1272.469 | 27.203 | 27.435 | 36.36 | 25.001 | 1.7 | 1.5 | 0 | 1.7 | 0.2
2633 | 30/07/2025 10:30:08.393 | 98.568 | 81 | 100 | 71 | 52 | 29.77 | 9.283 | 7.004 | 134.394 | 29.861 | 28.405 | 28.264 | 601.856 | 26.144 | 27.097 | 1273.839 | 27.216 | 27.448 | 36.621 | 24.001 | 1.7 | 2 | 0.7 | 1.4 | 0.2
2634 | 30/07/2025 10:30:10.031 | 98.64 | 81 | 100 | 70 | 52 | 27.327 | 9.244 | 7.02 | 134.85 | 29.867 | 28.396 | 28.274 | 601.92 | 26.18 | 27.092 | 1274.369 | 27.169 | 27.455 | 36.699 | 24.001 | 1.7 | 2 | 0.7 | 1.4 | 0.2
2635 | 30/07/2025 10:30:11.667 | 98.016 | 80 | 100 | 70 | 52 | 30.876 | 9.294 | 7.06 | 134.671 | 29.865 | 28.396 | 28.247 | 601.932 | 26.154 | 27.11 | 1276.755 | 27.203 | 27.449 | 36.83 | 25.001 | 3 | 2 | 0.6 | 0.5 | 0.2
2636 | 30/07/2025 10:30:13.302 | 97.464 | 80 | 100 | 71 | 52 | 27.271 | 9.293 | 7.079 | 134.725 | 29.879 | 28.38 | 28.281 | 602.004 | 26.149 | 27.108 | 1300.157 | 27.217 | 27.445 | 36.6 | 24.001 | 1.9 | 1.1 | 0.7 | 0.5 | 0.2
2637 | 30/07/2025 10:30:14.935 | 97.32 | 79 | 100 | 70 | 53 | 29.753 | 9.289 | 7.122 | 134.409 | 29.847 | 28.408 | 28.283 | 601.937 | 26.166 | 27.12 | 1296.725 | 27.226 | 27.438 | 36.294 | 26.001 | 3.5 | 1.1 | 0 | 1.1 | 0.2
2638 | 30/07/2025 10:30:16.572 | 97.128 | 79 | 100 | 69 | 52 | 31.333 | 9.283 | 7.072 | 134.866 | 29.857 | 28.404 | 28.276 | 600.694 | 26.166 | 27.124 | 1293.052 | 27.193 | 27.441 | 36.662 | 26.001 | 2.5 | 1.4 | 0.9 | 0.6 | 0.3
2639 | 30/07/2025 10:30:18.208 | 97.608 | 81 | 100 | 70 | 52 | 29.334 | 9.289 | 7.06 | 134.729 | 29.85 | 28.411 | 28.271 | 600.678 | 26.159 | 27.112 | 1297.124 | 27.196 | 27.447 | 36.701 | 26.001 | 2.5 | 1.4 | 0.9 | 0.6 | 0.3
2640 | 30/07/2025 10:30:19.843 | 98.256 | 80 | 100 | 70 | 52 | 31.203 | 9.138 | 7.06 | 134.783 | 29.861 | 28.388 | 28.253 | 600.526 | 26.17 | 27.13 | 1294.744 | 27.217 | 27.445 | 36.788 | 27.001 | 3.9 | 1.4 | 1.3 | 0.5 | 0.2
2641 | 30/07/2025 10:30:21.479 | 98.304 | 79 | 100 | 70 | 52 | 30.504 | 9.14 | 7.062 | 134.572 | 29.845 | 28.383 | 28.297 | 600.553 | 26.167 | 27.118 | 1287.421 | 27.211 | 27.45 | 36.525 | 28.001 | 4.3 | 1.7 | 1.2 | 0.6 | 0.3
2642 | 30/07/2025 10:30:23.118 | 98.376 | 81 | 100 | 70 | 52 | 27.216 | 9.423 | 7.072 | 134.421 | 29.842 | 28.403 | 28.279 | 601.821 | 26.162 | 27.137 | 1289.036 | 27.205 | 27.434 | 34.658 | 23.001 | 2.6 | 1.7 | 0.7 | 0 | 0.3
2643 | 30/07/2025 10:30:24.751 | 97.776 | 79 | 100 | 70 | 52 | 30.308 | 9.128 | 7.07 | 134.661 | 29.871 | 28.398 | 28.292 | 602.008 | 26.169 | 27.111 | 1289.656 | 27.184 | 27.45 | 34.884 | 25.001 | 4.1 | 2.9 | 0.6 | 0 | 0.3
2644 | 30/07/2025 10:30:26.386 | 97.824 | 81 | 100 | 70 | 52 | 31.483 | 9.199 | 7.071 | 134.601 | 29.873 | 28.401 | 28.286 | 602.074 | 26.158 | 27.104 | 1277.336 | 27.219 | 27.451 | 34.999 | 23.001 | 2.5 | 2.9 | 0 | 0.5 | 0.2
2645 | 30/07/2025 10:30:28.031 | 97.872 | 80 | 100 | 70 | 52 | 28.61 | 9.288 | 7.089 | 134.578 | 29.877 | 28.379 | 28.262 | 600.622 | 26.156 | 27.126 | 1272.252 | 27.206 | 27.451 | 34.931 | 23.001 | 2.5 | 2.9 | 0 | 0.5 | 0.2
2646 | 30/07/2025 10:30:29.673 | 97.752 | 80 | 100 | 70 | 53 | 31.344 | 9.287 | 7.087 | 134.326 | 29.873 | 28.402 | 28.294 | 600.577 | 26.153 | 27.115 | 1271.578 | 27.225 | 27.44 | 34.862 | 25.001 | 1.6 | 2 | 0 | 0.6 | 0.2
2647 | 30/07/2025 10:30:31.309 | 97.488 | 79 | 100 | 70 | 52 | 29.913 | 9.213 | 7.09 | 134.687 | 29.88 | 28.397 | 28.284 | 602.038 | 26.168 | 27.124 | 1265.182 | 27.199 | 27.437 | 34.614 | 26.001 | 2.5 | 2 | 0.6 | 0.1 | 0.2
2648 | 30/07/2025 10:30:32.944 | 97.512 | 78 | 100 | 71 | 52 | 27.388 | 9.461 | 7.135 | 134.743 | 29.886 | 28.401 | 28.28 | 601.899 | 26.141 | 27.098 | 1267.05 | 27.181 | 27.461 | 36.309 | 23.001 | 2.5 | 0.9 | 0.9 | 0 | 0.1
2649 | 30/07/2025 10:30:34.580 | 97.368 | 79 | 100 | 70 | 52 | 30.797 | 9.427 | 7.137 | 134.679 | 29.868 | 28.384 | 28.254 | 601.842 | 26.138 | 27.123 | 1271.906 | 27.22 | 27.446 | 36.742 | 27.001 | 1.8 | 0.9 | 0.4 | 0.5 | 0.1
2650 | 30/07/2025 10:30:36.222 | 97.392 | 79 | 100 | 70 | 52 | 31.533 | 9.56 | 7.15 | 134.595 | 29.875 | 28.387 | 28.3 | 600.61 | 26.136 | 27.096 | 1282.758 | 27.209 | 27.434 | 36.639 | 27.001 | 1.8 | 0.9 | 0.4 | 0.5 | 0.1
2651 | 30/07/2025 10:30:37.857 | 97.56 | 80 | 100 | 70 | 52 | 29.841 | 9.581 | 7.137 | 134.443 | 29.87 | 28.393 | 28.284 | 601.31 | 26.149 | 27.113 | 1290.999 | 27.204 | 27.431 | 36.641 | 30.001 | 2.5 | 1.8 | 0.6 | 0.5 | 0.1
2652 | 30/07/2025 10:30:39.492 | 97.56 | 81 | 100 | 70 | 52 | 31.424 | 9.287 | 7.135 | 134.58 | 29.869 | 28.404 | 28.3 | 602.003 | 26.145 | 27.091 | 1287.2 | 27.194 | 27.461 | 36.519 | 27.001 | 1.2 | 1.8 | 0.1 | 0.2 | 0.1
2653 | 30/07/2025 10:30:41.126 | 97.68 | 79 | 100 | 70 | 52 | 29.26 | 9.287 | 7.152 | 134.588 | 29.855 | 28.405 | 28.277 | 602.004 | 26.137 | 27.087 | 1288.927 | 27.204 | 27.457 | 36.7 | 27.001 | 1.9 | 3 | 0.6 | 0.6 | 0.1
2654 | 30/07/2025 10:30:42.762 | 97.992 | 80 | 100 | 70 | 52 | 27.663 | 9.126 | 7.16 | 134.783 | 29.886 | 28.383 | 28.27 | 602.002 | 26.17 | 27.086 | 1294.32 | 27.22 | 27.443 | 36.763 | 29.001 | 3.5 | 3 | 1.2 | 0.6 | 0.1
2655 | 30/07/2025 10:30:44.397 | 98.136 | 79 | 100 | 70 | 52 | 30.973 | 9.493 | 7.184 | 134.658 | 29.869 | 28.393 | 28.43 | 602.061 | 26.164 | 27.083 | 1297.405 | 27.21 | 27.434 | 36.497 | 23.001 | 2.9 | 1.1 | 0.7 | 0 | 0.1
2656 | 30/07/2025 10:30:46.033 | 97.848 | 81 | 100 | 70 | 52 | 27.313 | 9.581 | 7.186 | 134.667 | 29.88 | 28.398 | 28.427 | 601.965 | 26.172 | 27.098 | 1295.855 | 27.205 | 27.424 | 36.425 | 23.001 | 2.9 | 1.1 | 0.7 | 0 | 0.1
2657 | 30/07/2025 10:30:47.667 | 97.416 | 80 | 100 | 70 | 52 | 30.277 | 9.286 | 7.187 | 134.671 | 29.856 | 28.405 | 28.436 | 602.018 | 26.169 | 27.104 | 1300.387 | 27.188 | 27.472 | 36.616 | 25.001 | 2.3 | 1.1 | 0.6 | 0.5 | 0.1
2658 | 30/07/2025 10:30:49.305 | 97.872 | 82 | 100 | 71 | 52 | 31.49 | 9.427 | 7.136 | 134.54 | 29.857 | 28.395 | 28.402 | 601.993 | 26.161 | 27.123 | 1297.072 | 27.198 | 27.441 | 36.922 | 26.001 | 2.8 | 1.3 | 1.3 | 1.1 | 0.1
2659 | 30/07/2025 10:30:50.943 | 97.656 | 81 | 100 | 70 | 52 | 28.736 | 9.282 | 7.12 | 134.722 | 29.862 | 28.372 | 28.432 | 602.21 | 26.17 | 27.108 | 1289.63 | 27.217 | 27.445 | 36.541 | 28.001 | 1.3 | 1.3 | 1.2 | 0.9 | 0.1
2660 | 30/07/2025 10:30:52.580 | 98.256 | 81 | 100 | 70 | 53 | 28.138 | 9.398 | 7.122 | 134.339 | 29.839 | 28.396 | 28.417 | 602.064 | 26.162 | 27.133 | 1297.175 | 27.227 | 27.439 | 36.361 | 29.001 | 2.6 | 3.8 | 0.9 | 0.1 | 0.1
2661 | 30/07/2025 10:30:54.218 | 98.424 | 81 | 100 | 70 | 52 | 31.121 | 9.284 | 7.124 | 134.632 | 29.864 | 28.397 | 28.428 | 601.757 | 26.175 | 27.121 | 1292.003 | 27.192 | 27.455 | 36.863 | 29.001 | 2.6 | 3.8 | 0.9 | 0.1 | 0.1
2662 | 30/07/2025 10:30:55.853 | 99.048 | 80 | 100 | 70 | 52 | 27.348 | 9.423 | 7.124 | 134.473 | 29.832 | 28.398 | 28.419 | 601.895 | 26.151 | 27.141 | 1288.895 | 27.196 | 27.447 | 36.883 | 29.001 | 4 | 3.8 | 0.9 | 0.5 | 0.1
2663 | 30/07/2025 10:30:57.490 | 99.576 | 82 | 100 | 71 | 53 | 30.685 | 9.568 | 7.134 | 134.793 | 29.865 | 28.396 | 28.396 | 601.799 | 26.17 | 27.124 | 1276.912 | 27.205 | 27.447 | 36.713 | 32.001 | 3 | 1.6 | 0.6 | 0 | 0.1
2664 | 30/07/2025 10:30:59.126 | 99.552 | 82 | 100 | 71 | 52 | 31.403 | 9.433 | 7.122 | 134.707 | 29.841 | 28.389 | 28.436 | 602.042 | 26.162 | 27.107 | 1282.566 | 27.222 | 27.463 | 36.674 | 29.001 | 6.8 | 1.6 | 0 | 0.8 | 0.1
2665 | 30/07/2025 10:31:00.760 | 99.216 | 82 | 100 | 71 | 52 | 28.074 | 9.645 | 7.125 | 134.356 | 29.867 | 28.401 | 28.43 | 603.215 | 26.154 | 27.124 | 1287.092 | 27.203 | 27.423 | 36.292 | 30.001 | 3.5 | 0.8 | 0 | 1 | 0.1
2666 | 30/07/2025 10:31:02.397 | 98.88 | 83 | 100 | 70 | 53 | 28.626 | 9.508 | 7.122 | 134.762 | 29.883 | 28.398 | 28.443 | 603.365 | 26.162 | 27.113 | 1296.779 | 27.189 | 27.447 | 36.699 | 25.001 | 2.8 | 0.8 | 0.9 | 0.5 | 0.1
2667 | 30/07/2025 10:31:04.034 | 98.712 | 82 | 100 | 70 | 52 | 29.314 | 9.287 | 7.122 | 134.595 | 29.883 | 28.395 | 28.416 | 603.189 | 26.158 | 27.114 | 1298.395 | 27.185 | 27.454 | 36.594 | 25.001 | 2.8 | 0.8 | 0.9 | 0.5 | 0.1
2668 | 30/07/2025 10:31:05.669 | 98.4 | 82 | 100 | 71 | 52 | 27.657 | 9.288 | 7.12 | 134.713 | 29.873 | 28.385 | 28.414 | 603.333 | 26.156 | 27.097 | 1303.931 | 27.208 | 27.445 | 36.795 | 25.001 | 2.8 | 1.4 | 0.2 | 0.5 | 0.1
2669 | 30/07/2025 10:31:07.304 | 97.68 | 80 | 100 | 70 | 53 | 31.055 | 9.291 | 7.123 | 134.466 | 29.871 | 28.39 | 28.434 | 603.064 | 26.149 | 27.131 | 1311.383 | 27.226 | 27.453 | 36.492 | 32.001 | 1.8 | 1.4 | 0.7 | 0.6 | 0.1
2670 | 30/07/2025 10:31:08.942 | 98.376 | 80 | 100 | 70 | 52 | 31.372 | 9.563 | 7.123 | 134.424 | 29.874 | 28.402 | 28.419 | 603.177 | 26.159 | 27.103 | 1310.092 | 27.201 | 27.418 | 36.575 | 29.001 | 2.9 | 2 | 0.6 | 0 | 0.1
2671 | 30/07/2025 10:31:10.578 | 98.112 | 80 | 100 | 70 | 52 | 27.745 | 9.429 | 7.133 | 134.864 | 29.863 | 28.404 | 28.429 | 603.266 | 26.15 | 27.09 | 1306.861 | 27.189 | 27.467 | 36.652 | 24.001 | 3.5 | 2 | 0.6 | 0.5 | 0.1
2672 | 30/07/2025 10:31:12.216 | 97.728 | 81 | 100 | 70 | 52 | 29.328 | 9.545 | 7.136 | 134.694 | 29.877 | 28.395 | 28.387 | 602.022 | 26.147 | 27.107 | 1301.581 | 27.217 | 27.449 | 36.64 | 24.001 | 3.5 | 2 | 0.6 | 0.5 | 0.1
2673 | 30/07/2025 10:31:13.850 | 97.464 | 80 | 100 | 70 | 52 | 28.712 | 9.449 | 7.149 | 134.678 | 29.866 | 28.397 | 28.43 | 602.063 | 26.142 | 27.093 | 1299.386 | 27.233 | 27.46 | 36.488 | 28.001 | 2.9 | 2.7 | 0.6 | 0.1 | 0.2
2674 | 30/07/2025 10:31:15.490 | 97.488 | 81 | 100 | 71 | 52 | 28.146 | 9.51 | 7.14 | 134.589 | 29.856 | 28.389 | 28.423 | 601.885 | 26.146 | 27.111 | 1299.627 | 27.212 | 27.432 | 36.54 | 31.001 | 3.8 | 2.7 | 0.9 | 0 | 0.2
2675 | 30/07/2025 10:31:17.126 | 97.56 | 80 | 100 | 70 | 53 | 31.165 | 9.293 | 7.136 | 134.48 | 29.877 | 28.4 | 28.441 | 602.073 | 26.152 | 27.084 | 1296.951 | 27.198 | 27.451 | 36.48 | 24.001 | 5 | 3.1 | 0.1 | 0.5 | 0.2
2676 | 30/07/2025 10:31:18.761 | 97.824 | 81 | 100 | 70 | 52 | 30.94 | 9.505 | 7.148 | 134.568 | 29.857 | 28.395 | 28.407 | 601.941 | 26.148 | 27.109 | 1306.816 | 27.203 | 27.454 | 36.756 | 32.001 | 3.2 | 3.1 | 1.5 | 0 | 0.2
2677 | 30/07/2025 10:31:20.396 | 98.064 | 82 | 100 | 71 | 52 | 27.422 | 9.228 | 7.146 | 134.735 | 29.873 | 28.382 | 28.417 | 602.048 | 26.182 | 27.122 | 1301.889 | 27.224 | 27.458 | 36.681 | 27.001 | 4.3 | 4.3 | 1.5 | 0.5 | 0.2
2678 | 30/07/2025 10:31:22.036 | 98.088 | 81 | 100 | 70 | 52 | 31.45 | 9.281 | 7.135 | 134.598 | 29.86 | 28.367 | 28.424 | 601.931 | 26.178 | 27.133 | 1304.539 | 27.221 | 27.45 | 36.774 | 27.001 | 4.3 | 4.3 | 1.5 | 0.5 | 0.2
2679 | 30/07/2025 10:31:23.670 | 97.68 | 80 | 100 | 70 | 52 | 28.195 | 9.213 | 7.134 | 134.581 | 29.876 | 28.398 | 28.435 | 602.152 | 26.16 | 27.1 | 1303.114 | 27.204 | 27.413 | 36.622 | 26.001 | 2.3 | 4.3 | 0.6 | 0 | 0.2
2680 | 30/07/2025 10:31:25.302 | 97.8 | 81 | 100 | 70 | 52 | 28.634 | 9.217 | 7.152 | 134.487 | 29.85 | 28.408 | 28.436 | 601.965 | 26.153 | 27.115 | 1291.919 | 27.202 | 27.459 | 36.857 | 26.001 | 3 | 2.3 | 1.3 | 0.6 | 0.2
2681 | 30/07/2025 10:31:26.939 | 97.68 | 79 | 100 | 71 | 52 | 31.201 | 9.198 | 7.169 | 134.654 | 29.856 | 28.398 | 28.398 | 601.985 | 26.152 | 27.137 | 1292.421 | 27.194 | 27.441 | 36.71 | 24.001 | 3.3 | 2.3 | 0.3 | 0.8 | 0.1
2682 | 30/07/2025 10:31:28.574 | 97.968 | 81 | 100 | 71 | 53 | 30.439 | 9.307 | 7.169 | 134.619 | 29.857 | 28.38 | 28.434 | 600.604 | 26.16 | 27.111 | 1288.442 | 27.215 | 27.45 | 36.644 | 27.001 | 2.3 | 2.4 | 1.2 | 0.4 | 0.1
2683 | 30/07/2025 10:31:30.210 | 97.8 | 79 | 100 | 70 | 52 | 27.235 | 9.288 | 7.172 | 134.178 | 29.842 | 28.395 | 28.424 | 600.496 | 26.157 | 27.121 | 1292.386 | 27.237 | 27.439 | 36.585 | 27.001 | 2.3 | 2.4 | 1.2 | 0.4 | 0.1
2684 | 30/07/2025 10:31:31.844 | 97.728 | 80 | 100 | 70 | 53 | 31.197 | 9.418 | 7.164 | 134.546 | 29.852 | 28.405 | 28.443 | 600.589 | 26.141 | 27.102 | 1292.652 | 27.195 | 27.435 | 36.551 | 28.001 | 3 | 2.4 | 0.9 | 0.5 | 0.1
2685 | 30/07/2025 10:31:33.480 | 97.056 | 80 | 100 | 70 | 52 | 27.524 | 9.306 | 7.072 | 134.525 | 29.848 | 28.398 | 28.407 | 600.505 | 26.154 | 27.143 | 1294.375 | 27.193 | 27.461 | 36.696 | 31.001 | 2.6 | 2.4 | 0.6 | 0.6 | 0.2
2686 | 30/07/2025 10:31:35.120 | 96.648 | 80 | 100 | 70 | 52 | 29.054 | 9.28 | 7.132 | 134.592 | 29.875 | 28.393 | 28.399 | 600.665 | 26.153 | 27.115 | 1289.073 | 27.203 | 27.451 | 36.669 | 27.001 | 3.2 | 2.4 | 0.6 | 1.4 | 0.1
2687 | 30/07/2025 10:31:36.756 | 96.36 | 79 | 100 | 71 | 52 | 31.323 | 9.325 | 7.142 | 134.553 | 29.866 | 28.378 | 28.433 | 600.624 | 26.155 | 27.117 | 1284.176 | 27.221 | 27.467 | 36.614 | 26.001 | 3.8 | 2.5 | 0.6 | 0.6 | 0.2
2688 | 30/07/2025 10:31:38.392 | 96.6 | 80 | 99 | 70 | 52 | 29.824 | 9.283 | 7.089 | 134.209 | 29.875 | 28.404 | 28.417 | 600.485 | 26.153 | 27.122 | 1296.733 | 27.208 | 27.428 | 36.395 | 24.001 | 2.5 | 2.5 | 0.9 | 0.7 | 0.2
2689 | 30/07/2025 10:31:40.029 | 96.096 | 79 | 100 | 70 | 53 | 31.13 | 9.332 | 7.086 | 134.358 | 29.876 | 28.421 | 28.425 | 600.492 | 26.153 | 27.114 | 1297.117 | 27.215 | 27.449 | 36.61 | 24.001 | 2.5 | 2.5 | 0.9 | 0.7 | 0.2
2690 | 30/07/2025 10:31:41.661 | 96.672 | 79 | 100 | 70 | 51 | 31.038 | 9.286 | 7.089 | 134.608 | 29.881 | 28.4 | 28.418 | 601.824 | 26.157 | 27.113 | 1293.684 | 27.18 | 27.447 | 36.801 | 24.001 | 4.6 | 1.9 | 1.5 | 0.5 | 0.2
2691 | 30/07/2025 10:31:43.295 | 95.904 | 79 | 100 | 70 | 52 | 27.385 | 9.513 | 7.119 | 134.758 | 29.876 | 28.39 | 28.408 | 600.635 | 26.144 | 27.091 | 1287.328 | 27.206 | 27.453 | 36.628 | 24.001 | 2.9 | 1.9 | 1.1 | 0.5 | 0.2
2692 | 30/07/2025 10:31:44.930 | 95.496 | 79 | 100 | 70 | 53 | 29.877 | 9.434 | 7.136 | 134.466 | 29.86 | 28.378 | 28.423 | 601.952 | 26.131 | 27.116 | 1287.349 | 27.221 | 27.445 | 36.46 | 30.001 | 2.2 | 2.3 | 1.8 | 0 | 0.2
2693 | 30/07/2025 10:31:46.565 | 96.24 | 78 | 100 | 71 | 52 | 31.418 | 9.287 | 7.136 | 134.372 | 29.885 | 28.395 | 28.433 | 602.008 | 26.137 | 27.096 | 1277.165 | 27.196 | 27.431 | 36.551 | 27.001 | 3 | 2.3 | 1.5 | 0.5 | 0.2
2694 | 30/07/2025 10:31:48.202 | 96.432 | 78 | 99 | 71 | 52 | 29.306 | 9.285 | 7.09 | 134.705 | 29.857 | 28.408 | 28.431 | 601.904 | 26.134 | 27.071 | 1282.46 | 27.182 | 27.475 | 36.703 | 27.001 | 3 | 2.3 | 1.5 | 0.5 | 0.2
2695 | 30/07/2025 10:31:49.837 | 96.624 | 81 | 100 | 71 | 52 | 31.285 | 9.287 | 7.086 | 134.727 | 29.873 | 28.395 | 28.409 | 601.987 | 26.161 | 27.086 | 1286.511 | 27.187 | 27.455 | 36.691 | 26.001 | 1.7 | 3.8 | 1.2 | 0.5 | 0.2
2696 | 30/07/2025 10:31:51.469 | 96.84 | 81 | 100 | 70 | 52 | 30.514 | 9.275 | 7.088 | 134.529 | 29.858 | 28.392 | 28.414 | 601.964 | 26.171 | 27.093 | 1283.527 | 27.236 | 27.458 | 36.608 | 21.001 | 2.6 | 3.8 | 0.6 | 0.9 | 0.2
2697 | 30/07/2025 10:31:53.105 | 97.2 | 78 | 100 | 70 | 53 | 27.311 | 9.135 | 7.088 | 134.433 | 29.87 | 28.391 | 28.438 | 602.003 | 26.17 | 27.112 | 1277.118 | 27.202 | 27.433 | 36.542 | 27.001 | 2.4 | 2.2 | 1.8 | 0.1 | 0.2
2698 | 30/07/2025 10:31:54.740 | 97.416 | 80 | 100 | 71 | 51 | 30.345 | 9.216 | 7.071 | 134.376 | 29.863 | 28.411 | 28.428 | 602.134 | 26.161 | 27.104 | 1286.622 | 27.204 | 27.446 | 36.476 | 29.001 | 4 | 2.2 | 0.6 | 1 | 0.1
2699 | 30/07/2025 10:31:56.374 | 97.44 | 82 | 99 | 70 | 51 | 31.569 | 9.284 | 7.072 | 134.552 | 29.854 | 28.398 | 28.405 | 602.035 | 26.163 | 27.132 | 1294.633 | 27.2 | 27.452 | 36.697 | 29.001 | 4 | 2.2 | 0.6 | 1 | 0.1
2700 | 30/07/2025 10:31:58.010 | 97.008 | 80 | 100 | 70 | 52 | 29.189 | 9.283 | 7.07 | 134.785 | 29.856 | 28.399 | 28.399 | 602.089 | 26.162 | 27.107 | 1296.941 | 27.212 | 27.454 | 36.588 | 24.001 | 4.6 | 0.7 | 1.9 | 0.8 | 0.2
2701 | 30/07/2025 10:31:59.645 | 96.936 | 80 | 100 | 70 | 52 | 31.407 | 9.297 | 7.072 | 134.636 | 29.844 | 28.369 | 28.437 | 602.072 | 26.164 | 27.129 | 1294.336 | 27.224 | 27.456 | 36.84 | 27.001 | 2.9 | 0.7 | 1 | 0.4 | 0.1
2702 | 30/07/2025 10:32:01.279 | 97.416 | 79 | 100 | 71 | 52 | 30 | 9.285 | 7.069 | 134.529 | 29.865 | 28.399 | 28.445 | 601.953 | 26.152 | 27.108 | 1297.378 | 27.2 | 27.441 | 36.393 | 31.001 | 3 | 1.9 | 1.9 | 0.5 | 0.1
2703 | 30/07/2025 10:32:02.915 | 97.008 | 80 | 100 | 70 | 53 | 27.347 | 9.511 | 7.072 | 134.609 | 29.842 | 28.415 | 28.429 | 601.912 | 26.159 | 27.125 | 1299.458 | 27.206 | 27.461 | 36.826 | 30.001 | 2.9 | 1.9 | 2.6 | 0 | 0.1
2704 | 30/07/2025 10:32:04.546 | 97.296 | 81 | 100 | 70 | 52 | 30.653 | 9.432 | 7.072 | 134.707 | 29.841 | 28.396 | 28.405 | 601.949 | 26.163 | 27.115 | 1306.861 | 27.189 | 27.453 | 36.856 | 25.001 | 2.5 | 2.3 | 2.1 | 0.5 | 0.2
2705 | 30/07/2025 10:32:06.180 | 97.752 | 81 | 100 | 70 | 52 | 27.45 | 9.43 | 7.072 | 134.548 | 29.848 | 28.395 | 28.392 | 602.052 | 26.144 | 27.114 | 1302.033 | 27.227 | 27.447 | 36.741 | 25.001 | 2.5 | 2.3 | 2.1 | 0.5 | 0.2
2706 | 30/07/2025 10:32:07.816 | 97.488 | 81 | 99 | 70 | 52 | 29.662 | 9.451 | 7.07 | 134.686 | 29.878 | 28.378 | 28.438 | 602.054 | 26.175 | 27.127 | 1308.12 | 27.205 | 27.445 | 36.742 | 28.001 | 4.5 | 2.3 | 1 | 0.1 | 0.2
2707 | 30/07/2025 10:32:09.450 | 97.824 | 80 | 100 | 69 | 52 | 31.438 | 9.317 | 7.07 | 134.419 | 29.871 | 28.411 | 28.434 | 602.028 | 26.149 | 27.096 | 1302.568 | 27.211 | 27.432 | 36.403 | 23.001 | 2.9 | 2.4 | 1.9 | 0.5 | 0.2
2708 | 30/07/2025 10:32:11.085 | 97.896 | 79 | 100 | 71 | 52 | 29.321 | 9.413 | 7.088 | 134.638 | 29.883 | 28.402 | 28.415 | 600.441 | 26.154 | 27.133 | 1294.962 | 27.184 | 27.457 | 36.74 | 28.001 | 3 | 2.4 | 1.6 | 1.8 | 0.2
2709 | 30/07/2025 10:32:12.719 | 97.944 | 81 | 100 | 70 | 52 | 27.585 | 9.284 | 7.1 | 134.684 | 29.887 | 28.398 | 28.406 | 600.563 | 26.159 | 27.105 | 1294.751 | 27.202 | 27.455 | 36.673 | 35.001 | 2.6 | 1.8 | 1.1 | 0.9 | 0.2
2710 | 30/07/2025 10:32:14.357 | 98.28 | 81 | 100 | 70 | 52 | 31.057 | 9.432 | 7.135 | 134.68 | 29.872 | 28.382 | 28.428 | 601.963 | 26.151 | 27.105 | 1296.831 | 27.222 | 27.456 | 36.607 | 35.001 | 2.6 | 1.8 | 1.1 | 0.9 | 0.2
2711 | 30/07/2025 10:32:15.991 | 98.712 | 78 | 100 | 72 | 51 | 27.258 | 9.509 | 7.134 | 134.553 | 29.879 | 28.383 | 28.431 | 601.947 | 26.151 | 27.096 | 1287.646 | 27.206 | 27.436 | 36.508 | 29.001 | 2.9 | 1.8 | 0.6 | 0.6 | 0.2
2712 | 30/07/2025 10:32:17.626 | 98.544 | 82 | 100 | 70 | 52 | 30.391 | 9.508 | 7.137 | 134.356 | 29.873 | 28.415 | 28.422 | 600.434 | 26.148 | 27.104 | 1279.628 | 27.216 | 27.445 | 36.622 | 26.001 | 3.1 | 1.2 | 0.6 | 0.5 | 0.2
2713 | 30/07/2025 10:32:19.264 | 98.592 | 81 | 100 | 70 | 52 | 31.572 | 9.429 | 7.136 | 134.823 | 29.877 | 28.399 | 28.415 | 600.646 | 26.158 | 27.104 | 1271.823 | 27.176 | 27.457 | 36.786 | 29.001 | 3.3 | 1.2 | 1.2 | 0.5 | 0.2
2714 | 30/07/2025 10:32:20.899 | 98.208 | 80 | 100 | 71 | 52 | 28.715 | 9.429 | 7.102 | 134.584 | 29.859 | 28.389 | 28.411 | 600.615 | 26.139 | 27.087 | 1266.806 | 27.208 | 27.456 | 36.719 | 28.001 | 2.3 | 1.2 | 1 | 0.8 | 0.3
2715 | 30/07/2025 10:32:22.535 | 98.736 | 81 | 100 | 71 | 52 | 28.169 | 9.453 | 7.089 | 134.529 | 29.867 | 28.373 | 28.431 | 600.596 | 26.143 | 27.095 | 1267.33 | 27.217 | 27.449 | 36.636 | 29.001 | 2.7 | 1.2 | 1.3 | 1.3 | 0.2
2716 | 30/07/2025 10:32:24.168 | 99 | 82 | 100 | 70 | 52 | 29.972 | 9.28 | 7.086 | 134.576 | 29.854 | 28.4 | 28.424 | 600.642 | 26.149 | 27.068 | 1267.444 | 27.218 | 27.433 | 36.597 | 29.001 | 2.7 | 1.2 | 1.3 | 1.3 | 0.2
2717 | 30/07/2025 10:32:25.804 | 99.312 | 82 | 100 | 71 | 52 | 27.445 | 9.34 | 7.09 | 134.61 | 29.864 | 28.401 | 28.426 | 600.48 | 26.155 | 27.098 | 1257.696 | 27.198 | 27.444 | 36.84 | 24.001 | 3.2 | 4.1 | 1 | 1.1 | 0.2
2718 | 30/07/2025 10:32:27.438 | 99.216 | 82 | 100 | 70 | 52 | 30.823 | 9.198 | 7.122 | 134.568 | 29.867 | 28.399 | 28.421 | 600.475 | 26.154 | 27.087 | 1253.084 | 27.181 | 27.455 | 36.804 | 30.001 | 2.8 | 4.1 | 0.7 | 0 | 0.2
2719 | 30/07/2025 10:32:29.074 | 99.072 | 82 | 100 | 71 | 52 | 31.537 | 9.356 | 7.122 | 134.734 | 29.854 | 28.391 | 28.409 | 600.453 | 26.158 | 27.107 | 1257.363 | 27.236 | 27.456 | 36.727 | 27.001 | 2.5 | 0.6 | 0.7 | 0.5 | 0.2
2720 | 30/07/2025 10:32:30.709 | 98.808 | 81 | 100 | 70 | 52 | 28.313 | 9.503 | 7.134 | 134.635 | 29.876 | 28.385 | 28.426 | 600.646 | 26.172 | 27.127 | 1249.215 | 27.196 | 27.442 | 36.36 | 27.001 | 3.5 | 0.6 | 1.3 | 0.1 | 0.2
2721 | 30/07/2025 10:32:32.344 | 98.76 | 81 | 100 | 71 | 52 | 28.734 | 9.285 | 7.123 | 134.614 | 29.846 | 28.403 | 28.42 | 600.654 | 26.17 | 27.111 | 1255.395 | 27.184 | 27.447 | 36.464 | 27.001 | 3.5 | 0.6 | 1.3 | 0.1 | 0.2
2722 | 30/07/2025 10:32:33.979 | 98.592 | 82 | 100 | 70 | 52 | 29.44 | 9.281 | 7.123 | 134.776 | 29.869 | 28.4 | 28.421 | 601.614 | 26.178 | 27.139 | 1254.932 | 27.181 | 27.454 | 36.638 | 26.001 | 2.1 | 0.8 | 0.3 | 0 | 0.2
2723 | 30/07/2025 10:32:35.614 | 98.808 | 81 | 100 | 70 | 52 | 27.72 | 9.317 | 7.124 | 134.632 | 29.856 | 28.402 | 28.405 | 602.06 | 26.156 | 27.104 | 1253.184 | 27.199 | 27.467 | 36.75 | 26.001 | 2.2 | 0.8 | 0.6 | 0.9 | 0.2
2724 | 30/07/2025 10:32:37.251 | 98.304 | 79 | 100 | 71 | 52 | 30.979 | 9.565 | 7.122 | 134.609 | 29.843 | 28.368 | 28.415 | 601.965 | 26.166 | 27.137 | 1246.988 | 27.217 | 27.449 | 36.741 | 26.001 | 2.3 | 1.4 | 0.6 | 0.6 | 0.2
2725 | 30/07/2025 10:32:38.886 | 98.28 | 81 | 100 | 71 | 52 | 31.301 | 9.29 | 7.122 | 134.582 | 29.85 | 28.401 | 28.448 | 602.063 | 26.16 | 27.106 | 1240.972 | 27.205 | 27.432 | 36.323 | 31.001 | 2.6 | 1.4 | 1.2 | 0.6 | 0.1
2726 | 30/07/2025 10:32:40.521 | 98.688 | 82 | 100 | 70 | 52 | 27.746 | 9.157 | 7.124 | 134.494 | 29.862 | 28.416 | 28.427 | 601.994 | 26.157 | 27.122 | 1252.099 | 27.221 | 27.455 | 34.889 | 24.001 | 2.3 | 2 | 0.6 | 1.2 | 0.2
2727 | 30/07/2025 10:32:42.162 | 98.832 | 80 | 100 | 70 | 54 | 31.552 | 9.126 | 7.123 | 134.881 | 29.859 | 28.403 | 28.424 | 602.106 | 26.153 | 27.104 | 1252.788 | 27.183 | 27.469 | 36.428 | 24.001 | 2.3 | 2 | 0.6 | 1.2 | 0.2
2728 | 30/07/2025 10:32:43.809 | 98.808 | 81 | 100 | 70 | 52 | 28.714 | 9.432 | 7.122 | 134.794 | 29.872 | 28.384 | 28.38 | 601.932 | 26.157 | 27.124 | 1248.185 | 27.221 | 27.464 | 36.58 | 26.001 | 2.7 | 2 | 0.9 | 1.1 | 0.2
2729 | 30/07/2025 10:32:45.452 | 98.592 | 81 | 100 | 70 | 53 | 27.966 | 9.432 | 7.122 | 134.717 | 29.88 | 28.378 | 28.433 | 601.87 | 26.171 | 27.112 | 1255.35 | 27.199 | 27.446 | 36.609 | 31.001 | 2.2 | 2.3 | 0.6 | 0.9 | 0.2
2730 | 30/07/2025 10:32:47.086 | 98.376 | 81 | 100 | 70 | 53 | 31.174 | 9.44 | 7.134 | 134.37 | 29.873 | 28.409 | 28.435 | 602.041 | 26.145 | 27.103 | 1262.48 | 27.209 | 27.446 | 36.66 | 29.001 | 2.3 | 2.3 | 1.9 | 0.6 | 0.2
2731 | 30/07/2025 10:32:48.721 | 98.016 | 80 | 100 | 72 | 52 | 30.998 | 9.287 | 7.125 | 134.652 | 29.876 | 28.403 | 28.424 | 602.017 | 26.15 | 27.116 | 1266.209 | 27.183 | 27.462 | 36.847 | 28.001 | 3.6 | 1.4 | 1 | 0.5 | 0.2
2732 | 30/07/2025 10:32:50.355 | 98.472 | 80 | 100 | 70 | 52 | 27.368 | 9.291 | 7.101 | 134.625 | 29.873 | 28.396 | 28.408 | 602.244 | 26.139 | 27.098 | 1261.08 | 27.195 | 27.452 | 36.62 | 28.001 | 3.6 | 1.4 | 1 | 0.5 | 0.2
2733 | 30/07/2025 10:32:51.990 | 98.448 | 82 | 100 | 70 | 53 | 31.54 | 9.28 | 7.09 | 134.723 | 29.876 | 28.385 | 28.397 | 602.017 | 26.147 | 27.119 | 1259.236 | 27.216 | 27.442 | 36.678 | 30.001 | 3.2 | 1.4 | 0.6 | 0.2 | 0.1
2734 | 30/07/2025 10:32:53.624 | 98.28 | 81 | 100 | 70 | 52 | 28.168 | 9.138 | 7.086 | 134.502 | 29.876 | 28.385 | 28.45 | 602.098 | 26.145 | 27.087 | 1276.262 | 27.214 | 27.437 | 36.414 | 30.001 | 2.2 | 2.1 | 0.6 | 0.5 | 0.1
2735 | 30/07/2025 10:32:55.259 | 98.376 | 81 | 100 | 71 | 52 | 28.758 | 9.15 | 7.088 | 134.475 | 29.864 | 28.401 | 28.418 | 600.603 | 26.144 | 27.108 | 1287.297 | 27.223 | 27.444 | 36.457 | 28.001 | 2.2 | 2.1 | 0.6 | 0.8 | 0.1
2736 | 30/07/2025 10:32:56.897 | 97.92 | 81 | 100 | 70 | 51 | 31.314 | 9.216 | 7.087 | 134.836 | 29.885 | 28.399 | 28.424 | 600.592 | 26.148 | 27.107 | 1284.447 | 27.181 | 27.458 | 36.754 | 28.001 | 2.8 | 1.8 | 0.7 | 0.8 | 0.1
2737 | 30/07/2025 10:32:58.533 | 96.912 | 80 | 100 | 71 | 52 | 30.556 | 9.409 | 7.071 | 134.702 | 29.862 | 28.389 | 28.404 | 600.474 | 26.143 | 27.084 | 1294.765 | 27.213 | 27.46 | 36.498 | 24.001 | 4 | 1.8 | 1.3 | 0.8 | 0.1
2738 | 30/07/2025 10:33:00.167 | 96.384 | 79 | 100 | 70 | 52 | 27.333 | 9.27 | 7.07 | 134.462 | 29.861 | 28.383 | 28.44 | 600.473 | 26.161 | 27.116 | 1296.761 | 27.217 | 27.451 | 36.53 | 24.001 | 4 | 1.8 | 1.3 | 0.8 | 0.1
2739 | 30/07/2025 10:33:01.803 | 97.008 | 79 | 100 | 70 | 52 | 31.396 | 9.136 | 7.07 | 134.594 | 29.86 | 28.399 | 28.429 | 600.497 | 26.149 | 27.102 | 1301.75 | 27.213 | 27.435 | 36.448 | 23.001 | 1.8 | 2 | 1.2 | 0.4 | 0.1
2740 | 30/07/2025 10:33:03.442 | 96.984 | 79 | 100 | 70 | 52 | 27.823 | 9.432 | 7.07 | 134.524 | 29.857 | 28.4 | 28.412 | 600.557 | 26.176 | 27.112 | 1309.13 | 27.198 | 27.441 | 36.601 | 32.001 | 0.9 | 2 | 1.5 | 0.5 | 0.1
2741 | 30/07/2025 10:33:05.081 | 97.176 | 78 | 100 | 70 | 52 | 29.341 | 9.288 | 6.937 | 134.603 | 29.853 | 28.405 | 28.417 | 600.611 | 26.153 | 27.1 | 1313.822 | 27.17 | 27.444 | 36.587 | 26.001 | 3.3 | 1.3 | 0.6 | 0.8 | 0.1
2742 | 30/07/2025 10:33:06.719 | 97.488 | 81 | 100 | 70 | 52 | 31.387 | 9.175 | 6.935 | 134.537 | 29.85 | 28.385 | 28.4 | 600.54 | 26.155 | 27.133 | 1312.86 | 27.235 | 27.449 | 36.539 | 25.001 | 3 | 1.3 | 0.7 | 0.5 | 0.1
2743 | 30/07/2025 10:33:08.355 | 97.416 | 81 | 100 | 71 | 52 | 30.069 | 9.177 | 6.932 | 134.897 | 29.868 | 28.389 | 28.448 | 600.496 | 26.182 | 27.13 | 1304.51 | 27.204 | 27.432 | 36.637 | 25.001 | 3 | 1.3 | 0.7 | 0.5 | 0.1
2744 | 30/07/2025 10:33:09.989 | 97.968 | 81 | 100 | 70 | 53 | 31.227 | 9.288 | 6.935 | 134.415 | 29.851 | 28.405 | 28.419 | 600.53 | 26.163 | 27.121 | 1306.275 | 27.212 | 27.439 | 36.329 | 29.001 | 3.4 | 2.1 | 0.7 | 0.5 | 0.2
2745 | 30/07/2025 10:33:11.625 | 98.28 | 81 | 100 | 71 | 53 | 31.077 | 9.281 | 7.004 | 134.691 | 29.852 | 28.404 | 28.433 | 600.602 | 26.179 | 27.114 | 1309.139 | 27.185 | 27.455 | 36.608 | 22.001 | 2.9 | 2.1 | 0.6 | 0.2 | 0.2
2746 | 30/07/2025 10:33:13.260 | 98.184 | 81 | 100 | 70 | 54 | 27.497 | 9.286 | 7.004 | 134.578 | 29.845 | 28.4 | 28.405 | 600.565 | 26.148 | 27.119 | 1302.508 | 27.201 | 27.467 | 36.596 | 25.001 | 4.8 | 1.3 | 1.5 | 0 | 0.2
2747 | 30/07/2025 10:33:14.896 | 98.52 | 82 | 100 | 70 | 53 | 29.686 | 9.432 | 7.005 | 134.559 | 29.867 | 28.371 | 28.406 | 600.501 | 26.163 | 27.125 | 1286.633 | 27.211 | 27.449 | 36.143 | 27.001 | 2.8 | 1.3 | 1.9 | 0.5 | 0.3
2748 | 30/07/2025 10:33:16.532 | 98.304 | 79 | 100 | 71 | 51 | 31.462 | 9.489 | 7.067 | 134.56 | 29.869 | 28.399 | 28.448 | 600.67 | 26.158 | 27.108 | 1296.6 | 27.201 | 27.437 | 34.592 | 26.001 | 3.4 | 2.8 | 0.8 | 0.1 | 0.3
2749 | 30/07/2025 10:33:18.166 | 98.208 | 79 | 100 | 71 | 52 | 28.567 | 9.489 | 7.068 | 134.315 | 29.864 | 28.406 | 28.409 | 600.471 | 26.164 | 27.123 | 1288.11 | 27.202 | 27.423 | 34.756 | 26.001 | 3.4 | 2.8 | 0.8 | 0.1 | 0.3
2750 | 30/07/2025 10:33:19.801 | 97.92 | 82 | 100 | 71 | 52 | 31.283 | 9.306 | 7.06 | 134.752 | 29.882 | 28.399 | 28.432 | 602.077 | 26.147 | 27.104 | 1279.493 | 27.188 | 27.46 | 36.724 | 26.001 | 2.5 | 2.8 | 0.8 | 0 | 0.3
2751 | 30/07/2025 10:33:21.448 | 98.064 | 81 | 100 | 71 | 52 | 30.605 | 9.26 | 7.07 | 134.591 | 29.877 | 28.393 | 28.375 | 602.009 | 26.151 | 27.119 | 1282.23 | 27.215 | 27.443 | 36.681 | 26.001 | 4.3 | 1.2 | 0.7 | 1 | 0.2
2752 | 30/07/2025 10:33:23.082 | 97.752 | 81 | 100 | 71 | 53 | 27.319 | 9.431 | 7.066 | 134.67 | 29.885 | 28.38 | 28.423 | 602.156 | 26.173 | 27.103 | 1277.393 | 27.212 | 27.44 | 36.735 | 27.001 | 0.9 | 1.2 | 0.9 | 0.6 | 0.2
2753 | 30/07/2025 10:33:24.715 | 98.328 | 81 | 100 | 70 | 52 | 30.344 | 9.291 | 7.087 | 134.549 | 29.862 | 28.411 | 28.442 | 602.124 | 26.151 | 27.097 | 1283.617 | 27.218 | 27.451 | 36.409 | 26.001 | 3.2 | 2.8 | 1.3 | 0.6 | 0.3
2754 | 30/07/2025 10:33:26.350 | 98.568 | 81 | 100 | 70 | 52 | 31.581 | 9.281 | 7.09 | 134.701 | 29.878 | 28.393 | 28.411 | 601.909 | 26.139 | 27.113 | 1284.649 | 27.182 | 27.457 | 36.495 | 26.001 | 3.2 | 2.8 | 1.3 | 0.6 | 0.3
2755 | 30/07/2025 10:33:27.995 | 98.544 | 81 | 100 | 70 | 52 | 29.24 | 9.315 | 7.088 | 134.551 | 29.853 | 28.404 | 28.413 | 601.803 | 26.136 | 27.098 | 1287.986 | 27.179 | 27.45 | 36.444 | 27.001 | 2.3 | 2.8 | 1 | 0.9 | 0.2
2756 | 30/07/2025 10:33:29.629 | 98.496 | 81 | 100 | 70 | 53 | 31.417 | 9.291 | 7.072 | 134.65 | 29.859 | 28.38 | 28.398 | 601.938 | 26.151 | 27.101 | 1286.233 | 27.208 | 27.457 | 36.611 | 25.001 | 4.2 | 1.9 | 1.5 | 1.2 | 0.2
2757 | 30/07/2025 10:33:31.265 | 98.52 | 79 | 100 | 71 | 52 | 29.944 | 9.213 | 7.067 | 134.711 | 29.872 | 28.386 | 28.426 | 602.174 | 26.146 | 27.079 | 1288.036 | 27.203 | 27.445 | 36.63 | 28.001 | 2.1 | 1.9 | 0.6 | 0.3 | 0.2
2758 | 30/07/2025 10:33:32.899 | 98.568 | 80 | 100 | 70 | 52 | 27.396 | 9.291 | 7.071 | 134.291 | 29.866 | 28.398 | 28.411 | 600.508 | 26.152 | 27.108 | 1277.526 | 27.208 | 27.434 | 36.528 | 26.001 | 1.5 | 1.2 | 0 | 0 | 0.3
2759 | 30/07/2025 10:33:34.535 | 99.024 | 81 | 100 | 71 | 52 | 30.705 | 9.282 | 7.06 | 134.786 | 29.891 | 28.408 | 28.418 | 600.564 | 26.162 | 27.096 | 1284.65 | 27.17 | 27.454 | 36.88 | 28.001 | 1.7 | 1.2 | 1.2 | 0.8 | 0.3
2760 | 30/07/2025 10:33:36.171 | 98.976 | 81 | 100 | 70 | 52 | 27.335 | 9.341 | 7.061 | 134.803 | 29.859 | 28.397 | 28.405 | 600.392 | 26.161 | 27.118 | 1287.541 | 27.175 | 27.442 | 36.791 | 28.001 | 1.7 | 1.2 | 1.2 | 0.8 | 0.3
2761 | 30/07/2025 10:33:37.806 | 99.168 | 80 | 100 | 71 | 52 | 29.751 | 9.263 | 7.058 | 134.77 | 29.873 | 28.385 | 28.433 | 602.145 | 26.156 | 27.112 | 1289.336 | 27.218 | 27.45 | 36.65 | 26.001 | 2.9 | 2 | 1.2 | 0.7 | 0.3
2762 | 30/07/2025 10:33:39.442 | 98.856 | 81 | 100 | 70 | 53 | 31.513 | 9.253 | 7.058 | 134.355 | 29.85 | 28.401 | 28.429 | 602.127 | 26.164 | 27.13 | 1274.779 | 27.228 | 27.447 | 36.512 | 29.001 | 1.9 | 2 | 0.9 | 0.5 | 0.2
2763 | 30/07/2025 10:33:41.077 | 98.52 | 82 | 100 | 70 | 53 | 29.422 | 9.21 | 7.062 | 134.568 | 29.846 | 28.399 | 28.427 | 601.935 | 26.161 | 27.128 | 1287.475 | 27.191 | 27.436 | 36.771 | 29.001 | 2.1 | 1 | 0.8 | 0.5 | 0.2
2764 | 30/07/2025 10:33:42.714 | 98.808 | 82 | 100 | 70 | 52 | 27.736 | 9.286 | 7.059 | 134.579 | 29.842 | 28.404 | 28.405 | 601.992 | 26.16 | 27.111 | 1291.962 | 27.171 | 27.462 | 36.64 | 30.001 | 2.4 | 1 | 2.3 | 0.6 | 0.2
2765 | 30/07/2025 10:33:44.349 | 98.64 | 82 | 100 | 70 | 52 | 31.038 | 9.285 | 7.061 | 134.726 | 29.839 | 28.386 | 28.393 | 601.92 | 26.159 | 27.143 | 1298.044 | 27.22 | 27.447 | 36.591 | 30.001 | 2.4 | 1 | 2.3 | 0.6 | 0.2
2766 | 30/07/2025 10:33:45.983 | 98.76 | 82 | 100 | 70 | 52 | 27.368 | 9.142 | 7.057 | 134.565 | 29.837 | 28.381 | 28.419 | 601.822 | 26.153 | 27.113 | 1306.019 | 27.22 | 27.457 | 36.577 | 29.001 | 3.1 | 1.4 | 1 | 0.5 | 0.2
2767 | 30/07/2025 10:33:47.619 | 98.928 | 82 | 100 | 70 | 52 | 30.318 | 8.988 | 7.063 | 134.44 | 29.856 | 28.398 | 28.427 | 602.095 | 26.149 | 27.129 | 1310.944 | 27.203 | 27.43 | 36.404 | 26.001 | 3.2 | 1.4 | 1.1 | 0 | 0.2
2768 | 30/07/2025 10:33:49.254 | 99 | 82 | 100 | 71 | 52 | 31.558 | 9.306 | 7.06 | 134.686 | 29.874 | 28.399 | 28.425 | 602.061 | 26.164 | 27.105 | 1301.045 | 27.198 | 27.447 | 36.613 | 25.001 | 2.9 | 1.7 | 0.6 | 0 | 0.2
2769 | 30/07/2025 10:33:50.886 | 99.168 | 80 | 99 | 70 | 53 | 28.874 | 8.986 | 7.06 | 134.57 | 29.86 | 28.42 | 28.419 | 601.913 | 26.153 | 27.112 | 1291.716 | 27.202 | 27.457 | 36.568 | 32.001 | 3.9 | 1.7 | 0.9 | 0.5 | 0.2
2770 | 30/07/2025 10:33:52.522 | 98.832 | 80 | 100 | 70 | 51 | 27.996 | 9.207 | 7.06 | 134.794 | 29.889 | 28.376 | 28.401 | 602.519 | 26.153 | 27.115 | 1297.009 | 27.225 | 27.44 | 36.637 | 28.001 | 2.8 | 2.3 | 0.4 | 0.5 | 0.2
2771 | 30/07/2025 10:33:54.192 | 98.496 | 79 | 100 | 71 | 52 | 31.232 | 9.287 | 7.072 | 134.733 | 29.878 | 28.39 | 28.442 | 602.105 | 26.141 | 27.106 | 1294.751 | 27.214 | 27.448 | 36.4 | 28.001 | 2.8 | 2.3 | 0.4 | 0.5 | 0.2
2772 | 30/07/2025 10:33:55.825 | 98.376 | 81 | 100 | 70 | 52 | 27.327 | 9.287 | 7.07 | 134.448 | 29.89 | 28.4 | 28.426 | 602.021 | 26.171 | 27.128 | 1297.216 | 27.206 | 27.427 | 36.505 | 28.001 | 3.2 | 2.3 | 0.6 | 0.1 | 0.1
2773 | 30/07/2025 10:33:57.457 | 97.704 | 79 | 100 | 69 | 54 | 30.785 | 9.269 | 7.123 | 134.869 | 29.874 | 28.406 | 28.422 | 602.138 | 26.146 | 27.111 | 1299.411 | 27.192 | 27.471 | 36.753 | 22.001 | 2.5 | 2.5 | 0 | 0.6 | 0.1
2774 | 30/07/2025 10:33:59.089 | 97.824 | 79 | 100 | 70 | 52 | 31.596 | 9.467 | 7.091 | 134.64 | 29.871 | 28.39 | 28.38 | 601.999 | 26.152 | 27.113 | 1299.064 | 27.2 | 27.456 | 36.719 | 25.001 | 4.2 | 2.5 | 0.6 | 0.9 | 0.1
2775 | 30/07/2025 10:34:00.729 | 97.968 | 81 | 100 | 70 | 51 | 28.271 | 9.173 | 7.087 | 134.677 | 29.87 | 28.382 | 28.428 | 601.954 | 26.156 | 27.091 | 1292.142 | 27.214 | 27.447 | 36.603 | 29.001 | 3.4 | 1.6 | 1 | 0.6 | 0.1
2776 | 30/07/2025 10:34:02.361 | 97.344 | 79 | 100 | 70 | 52 | 28.605 | 9.288 | 7.087 | 134.425 | 29.86 | 28.405 | 28.43 | 602.079 | 26.143 | 27.098 | 1287.466 | 27.218 | 27.437 | 36.319 | 29.001 | 3.4 | 1.6 | 1 | 0.6 | 0.1
2777 | 30/07/2025 10:34:03.995 | 96.696 | 79 | 100 | 71 | 52 | 29.317 | 9.289 | 7.088 | 134.533 | 29.872 | 28.402 | 28.434 | 602.139 | 26.14 | 27.083 | 1290.004 | 27.202 | 27.432 | 36.493 | 29.001 | 2.4 | 1.6 | 1 | 0.6 | 0.1
2778 | 30/07/2025 10:34:05.629 | 97.44 | 78 | 100 | 70 | 53 | 27.647 | 9.131 | 7.136 | 134.66 | 29.853 | 28.41 | 28.423 | 601.896 | 26.151 | 27.079 | 1296.792 | 27.183 | 27.455 | 36.681 | 24.001 | 3 | 2 | 0.9 | 0.6 | 0.1
2779 | 30/07/2025 10:34:07.264 | 97.536 | 79 | 100 | 70 | 52 | 31.007 | 9.286 | 7.136 | 134.817 | 29.874 | 28.391 | 28.398 | 600.604 | 26.173 | 27.101 | 1287.022 | 27.219 | 27.445 | 38.27 | 31.001 | 2.1 | 2 | 0.8 | 0.3 | 0.1
2780 | 30/07/2025 10:34:08.898 | 97.464 | 81 | 100 | 71 | 52 | 31.383 | 9.205 | 7.132 | 134.665 | 29.848 | 28.383 | 28.435 | 600.539 | 26.161 | 27.089 | 1276.798 | 27.223 | 27.451 | 38.384 | 28.001 | 2.8 | 1.4 | 0.6 | 0 | 0.1
2781 | 30/07/2025 10:34:10.535 | 97.944 | 81 | 100 | 70 | 52 | 27.746 | 9.133 | 7.125 | 134.473 | 29.859 | 28.401 | 28.43 | 601.852 | 26.16 | 27.116 | 1274.581 | 27.214 | 27.447 | 36.491 | 25.001 | 3.2 | 1.4 | 1.3 | 0 | 0.2
2782 | 30/07/2025 10:34:12.170 | 97.44 | 79 | 100 | 71 | 52 | 29.211 | 9.128 | 7.122 | 134.847 | 29.864 | 28.4 | 28.425 | 602.19 | 26.147 | 27.121 | 1277.263 | 27.168 | 27.465 | 37.848 | 25.001 | 3.2 | 1.4 | 1.3 | 0 | 0.2
2783 | 30/07/2025 10:34:13.806 | 97.368 | 79 | 100 | 69 | 52 | 28.777 | 9.208 | 7.125 | 134.85 | 29.847 | 28.398 | 28.411 | 601.873 | 26.167 | 27.138 | 1276.911 | 27.167 | 27.457 | 38.658 | 23.001 | 2.3 | 1.7 | 0.6 | 1.6 | 0.2
2784 | 30/07/2025 10:34:15.443 | 97.2 | 79 | 100 | 71 | 52 | 28.179 | 8.989 | 7.12 | 134.827 | 29.853 | 28.386 | 28.418 | 602.094 | 26.165 | 27.12 | 1276.836 | 27.219 | 27.44 | 36.54 | 29.001 | 2.1 | 1.7 | 1 | 0.5 | 0.2
2785 | 30/07/2025 10:34:17.079 | 97.728 | 79 | 100 | 70 | 52 | 31.197 | 9.19 | 7.134 | 134.483 | 29.827 | 28.386 | 28.423 | 601.985 | 26.149 | 27.126 | 1270.348 | 27.219 | 27.431 | 36.453 | 29.001 | 2.2 | 3.4 | 0.5 | 0.2 | 0.2
2786 | 30/07/2025 10:34:18.717 | 97.464 | 81 | 100 | 70 | 52 | 31.086 | 9.136 | 7.152 | 134.572 | 29.853 | 28.403 | 28.437 | 601.97 | 26.173 | 27.13 | 1274.56 | 27.199 | 27.431 | 36.592 | 29.001 | 2.3 | 3.4 | 0.6 | 0.6 | 0.2
2787 | 30/07/2025 10:34:20.351 | 96.504 | 77 | 100 | 70 | 52 | 27.437 | 9.428 | 7.134 | 134.747 | 29.839 | 28.404 | 28.419 | 602.049 | 26.155 | 27.104 | 1271.683 | 27.179 | 27.473 | 36.597 | 29.001 | 2.3 | 3.4 | 0.6 | 0.6 | 0.2
2788 | 30/07/2025 10:34:21.985 | 97.104 | 78 | 100 | 70 | 52 | 31.558 | 9.363 | 7.122 | 134.892 | 29.861 | 28.395 | 28.413 | 602.127 | 26.161 | 27.117 | 1275.556 | 27.189 | 27.453 | 36.73 | 25.001 | 0.6 | 1 | 0 | 0.1 | 0.2
2789 | 30/07/2025 10:34:23.619 | 97.176 | 80 | 100 | 70 | 53 | 28.341 | 9.212 | 7.091 | 134.683 | 29.863 | 28.382 | 28.429 | 602.029 | 26.156 | 27.11 | 1277.046 | 27.227 | 27.461 | 36.687 | 23.001 | 3.4 | 1 | 1 | 0 | 0.2
2790 | 30/07/2025 10:34:25.253 | 97.488 | 80 | 100 | 70 | 52 | 28.605 | 9.503 | 7.072 | 134.582 | 29.865 | 28.392 | 28.42 | 602.003 | 26.148 | 27.111 | 1273.079 | 27.207 | 27.417 | 36.43 | 24.001 | 3.9 | 2.8 | 1 | 0 | 0.2
2791 | 30/07/2025 10:34:26.889 | 97.344 | 80 | 100 | 70 | 53 | 31.319 | 9.273 | 7.121 | 134.54 | 29.886 | 28.403 | 28.438 | 602.045 | 26.147 | 27.099 | 1276.976 | 27.194 | 27.453 | 36.565 | 23.001 | 2.2 | 2.8 | 1.3 | 0 | 0.2
2792 | 30/07/2025 10:34:28.523 | 97.776 | 79 | 100 | 70 | 53 | 30.709 | 9.381 | 7.122 | 134.457 | 29.858 | 28.403 | 28.386 | 601.983 | 26.146 | 27.122 | 1277.012 | 27.202 | 27.459 | 36.692 | 25.001 | 2.8 | 2.8 | 1.3 | 0.5 | 0.1
2793 | 30/07/2025 10:34:30.161 | 98.208 | 81 | 100 | 71 | 53 | 27.34 | 9.289 | 7.121 | 134.775 | 29.883 | 28.382 | 28.415 | 603.183 | 26.164 | 27.117 | 1271.445 | 27.211 | 27.45 | 36.736 | 25.001 | 2.8 | 2.8 | 1.3 | 0.5 | 0.1
2794 | 30/07/2025 10:34:31.800 | 98.616 | 81 | 100 | 70 | 50 | 31.491 | 9.292 | 7.12 | 134.451 | 29.868 | 28.379 | 28.419 | 602.027 | 26.15 | 27.121 | 1276.865 | 27.232 | 27.449 | 36.668 | 26.001 | 4.2 | 2.8 | 2.2 | 0.1 | 0.1
2795 | 30/07/2025 10:34:33.439 | 98.328 | 80 | 100 | 70 | 52 | 27.883 | 9.141 | 7.124 | 134.426 | 29.889 | 28.41 | 28.433 | 603.236 | 26.168 | 27.108 | 1286.754 | 27.211 | 27.422 | 36.407 | 25.001 | 5.3 | 3.8 | 1.6 | 0.5 | 0.2
2796 | 30/07/2025 10:34:35.077 | 98.376 | 79 | 100 | 71 | 51 | 29.287 | 9.203 | 7.122 | 134.602 | 29.871 | 28.398 | 28.431 | 602.534 | 26.133 | 27.088 | 1301.847 | 27.197 | 27.463 | 36.638 | 28.001 | 4.4 | 3.8 | 1.5 | 0.5 | 0.2
2797 | 30/07/2025 10:34:36.711 | 98.448 | 81 | 100 | 70 | 51 | 31.439 | 9.211 | 7.123 | 134.803 | 29.869 | 28.402 | 28.403 | 603.323 | 26.148 | 27.106 | 1288.569 | 27.196 | 27.466 | 36.829 | 29.001 | 4 | 2.1 | 0.7 | 0.8 | 0.1
2798 | 30/07/2025 10:34:38.345 | 98.376 | 80 | 100 | 70 | 52 | 30.033 | 9.225 | 7.134 | 134.516 | 29.871 | 28.38 | 28.431 | 603.359 | 26.152 | 27.08 | 1289.607 | 27.214 | 27.454 | 36.534 | 29.001 | 4 | 2.1 | 0.7 | 0.8 | 0.1
2799 | 30/07/2025 10:34:39.980 | 99 | 82 | 100 | 72 | 52 | 31.201 | 9.214 | 7.134 | 134.653 | 29.863 | 28.377 | 28.434 | 603.16 | 26.159 | 27.101 | 1289.739 | 27.209 | 27.436 | 36.688 | 28.001 | 2 | 2.1 | 0.6 | 0.6 | 0.1
2800 | 30/07/2025 10:34:41.614 | 98.832 | 81 | 100 | 70 | 52 | 31.071 | 8.989 | 7.135 | 134.443 | 29.881 | 28.412 | 28.436 | 603.295 | 26.138 | 27.089 | 1283.275 | 27.205 | 27.442 | 36.351 | 30.001 | 2.6 | 1.8 | 1.8 | 0.5 | 0.2
2801 | 30/07/2025 10:34:43.250 | 98.448 | 81 | 100 | 70 | 51 | 27.498 | 9.282 | 7.123 | 134.819 | 29.863 | 28.401 | 28.425 | 603.151 | 26.156 | 27.107 | 1288.34 | 27.191 | 27.46 | 34.968 | 27.001 | 2.3 | 1.8 | 1.5 | 0.6 | 0.2
2802 | 30/07/2025 10:34:44.888 | 98.736 | 82 | 99 | 70 | 52 | 29.752 | 9.284 | 7.122 | 134.557 | 29.882 | 28.393 | 28.404 | 603.32 | 26.18 | 27.12 | 1269.777 | 27.201 | 27.449 | 35.037 | 23.001 | 3.5 | 2.8 | 1.9 | 0.1 | 0.2
2803 | 30/07/2025 10:34:46.522 | 98.448 | 79 | 100 | 70 | 52 | 31.52 | 9.288 | 7.121 | 134.588 | 29.844 | 28.382 | 28.427 | 603.328 | 26.17 | 27.11 | 1287.171 | 27.226 | 27.448 | 36.67 | 28.001 | 3.6 | 2.8 | 1.7 | 0.6 | 0.2
2804 | 30/07/2025 10:34:48.158 | 98.136 | 81 | 100 | 70 | 52 | 28.656 | 9.3 | 7.094 | 134.518 | 29.866 | 28.397 | 28.438 | 602.157 | 26.165 | 27.114 | 1290.985 | 27.203 | 27.426 | 36.672 | 28.001 | 3.6 | 2.8 | 1.7 | 0.6 | 0.2
2805 | 30/07/2025 10:34:49.793 | 97.944 | 81 | 100 | 70 | 52 | 31.385 | 9.284 | 7.06 | 134.443 | 29.843 | 28.408 | 28.428 | 602.021 | 26.157 | 27.123 | 1293.924 | 27.209 | 27.451 | 36.621 | 28.001 | 3.5 | 2.4 | 0.8 | 0.3 | 0.2
2806 | 30/07/2025 10:34:51.428 | 98.304 | 82 | 100 | 70 | 52 | 30.547 | 8.997 | 7.077 | 134.818 | 29.843 | 28.397 | 28.405 | 603.028 | 26.166 | 27.126 | 1294.429 | 27.181 | 27.459 | 36.694 | 24.001 | 2.2 | 2.4 | 0.7 | 0.6 | 0.2
2807 | 30/07/2025 10:34:53.063 | 98.424 | 80 | 100 | 70 | 52 | 27.273 | 9.517 | 7.087 | 134.735 | 29.855 | 28.384 | 28.419 | 603.24 | 26.151 | 27.108 | 1301.543 | 27.227 | 27.449 | 36.491 | 24.001 | 2.6 | 2.2 | 1.2 | 0.5 | 0.2
2808 | 30/07/2025 10:34:54.703 | 98.448 | 81 | 100 | 71 | 52 | 30.243 | 9.289 | 7.086 | 134.413 | 29.847 | 28.382 | 28.425 | 603.237 | 26.148 | 27.127 | 1298.174 | 27.225 | 27.44 | 36.508 | 26.001 | 3.9 | 2.2 | 0.9 | 1.1 | 0.2
2809 | 30/07/2025 10:34:56.338 | 98.496 | 82 | 100 | 70 | 52 | 31.553 | 9.291 | 7.06 | 134.619 | 29.875 | 28.402 | 28.429 | 603.28 | 26.17 | 27.129 | 1288.473 | 27.205 | 27.448 | 36.651 | 26.001 | 3.9 | 2.2 | 0.9 | 1.1 | 0.2
2810 | 30/07/2025 10:34:57.973 | 98.592 | 82 | 100 | 70 | 52 | 29.181 | 9.285 | 7.062 | 134.476 | 29.86 | 28.403 | 28.41 | 603.16 | 26.154 | 27.121 | 1287.151 | 27.194 | 27.447 | 36.796 | 28.001 | 3.2 | 1.3 | 0.7 | 0.8 | 0.2
2811 | 30/07/2025 10:34:59.607 | 98.376 | 81 | 100 | 70 | 53 | 31.451 | 9.43 | 7.059 | 134.61 | 29.883 | 28.398 | 28.408 | 602.126 | 26.164 | 27.107 | 1287.616 | 27.188 | 27.452 | 36.806 | 23.001 | 2.8 | 1.3 | 1.5 | 0.6 | 0.2
2812 | 30/07/2025 10:35:01.245 | 98.448 | 81 | 100 | 70 | 52 | 30.197 | 9.433 | 7.06 | 134.586 | 29.886 | 28.382 | 28.435 | 601.996 | 26.16 | 27.12 | 1288.938 | 27.229 | 27.468 | 36.971 | 26.001 | 4 | 1.9 | 0.7 | 0.5 | 0.2
2813 | 30/07/2025 10:35:02.879 | 98.136 | 82 | 100 | 70 | 52 | 27.415 | 9.293 | 7.06 | 134.384 | 29.878 | 28.393 | 28.42 | 601.817 | 26.156 | 27.119 | 1299.804 | 27.208 | 27.432 | 36.554 | 26.001 | 3.4 | 1.9 | 1.8 | 0.5 | 0.2
2814 | 30/07/2025 10:35:04.514 | 98.136 | 81 | 100 | 70 | 50 | 30.839 | 9.131 | 7.06 | 134.654 | 29.88 | 28.4 | 28.429 | 602.015 | 26.147 | 27.097 | 1292.312 | 27.201 | 27.444 | 36.476 | 25.001 | 2.7 | 2.1 | 0.6 | 1.1 | 0.2
2815 | 30/07/2025 10:35:06.149 | 98.568 | 81 | 100 | 71 | 52 | 31.63 | 9.154 | 7.061 | 134.587 | 29.871 | 28.392 | 28.409 | 601.923 | 26.137 | 27.109 | 1278.799 | 27.196 | 27.463 | 36.075 | 25.001 | 2.7 | 2.1 | 0.6 | 1.1 | 0.2
2816 | 30/07/2025 10:35:07.783 | 98.232 | 81 | 100 | 70 | 52 | 29.895 | 9.283 | 7.07 | 134.692 | 29.867 | 28.394 | 28.415 | 602.035 | 26.124 | 27.1 | 1272.388 | 27.201 | 27.462 | 34.877 | 29.001 | 2.7 | 2.1 | 1.1 | 0.7 | 0.2
2817 | 30/07/2025 10:35:09.419 | 98.064 | 80 | 100 | 70 | 52 | 31.578 | 9.185 | 7.07 | 134.452 | 29.862 | 28.374 | 28.411 | 601.858 | 26.149 | 27.107 | 1271.575 | 27.223 | 27.455 | 34.835 | 29.001 | 2.1 | 2 | 1.1 | 0.3 | 0.2
2818 | 30/07/2025 10:35:11.052 | 98.664 | 81 | 100 | 71 | 52 | 29.549 | 9.099 | 7.085 | 134.543 | 29.892 | 28.404 | 28.441 | 602.06 | 26.146 | 27.084 | 1277.091 | 27.209 | 27.425 | 34.619 | 25.001 | 2.9 | 2 | 0.8 | 0.8 | 0.2
2819 | 30/07/2025 10:35:12.687 | 98.28 | 81 | 100 | 70 | 52 | 27.653 | 9.429 | 7.088 | 134.608 | 29.861 | 28.408 | 28.427 | 601.877 | 26.14 | 27.079 | 1264.947 | 27.19 | 27.46 | 36.628 | 27.001 | 1.6 | 3.5 | 0.6 | 0.1 | 0.3
2820 | 30/07/2025 10:35:14.326 | 98.4 | 81 | 100 | 70 | 53 | 31.073 | 9.357 | 7.082 | 134.499 | 29.875 | 28.395 | 28.403 | 601.768 | 26.161 | 27.106 | 1269.733 | 27.177 | 27.45 | 36.799 | 27.001 | 1.6 | 3.5 | 0.6 | 0.1 | 0.3
2821 | 30/07/2025 10:35:15.961 | 98.928 | 81 | 100 | 71 | 52 | 27.284 | 9.287 | 7.071 | 134.615 | 29.86 | 28.403 | 28.394 | 601.943 | 26.162 | 27.093 | 1267.341 | 27.223 | 27.441 | 36.938 | 30.001 | 3.7 | 3.5 | 0.9 | 0.5 | 0.3
2822 | 30/07/2025 10:35:17.678 | 99.072 | 82 | 100 | 70 | 52 | 30.321 | 9.417 | 7.069 | 134.635 | 29.884 | 28.374 | 28.443 | 601.954 | 26.169 | 27.11 | 1267.265 | 27.206 | 27.451 | 36.55 | 28.001 | 3.1 | 1.8 | 0.7 | 0 | 0.3
2823 | 30/07/2025 10:35:19.312 | 99.264 | 84 | 100 | 70 | 52 | 31.638 | 9.402 | 7.086 | 134.18 | 29.863 | 28.407 | 28.439 | 603.177 | 26.154 | 27.114 | 1265.31 | 27.206 | 27.443 | 36.46 | 25.001 | 2.4 | 1.8 | 1.5 | 0 | 0.2
2824 | 30/07/2025 10:35:20.949 | 99.504 | 82 | 100 | 69 | 52 | 28.787 | 9.183 | 7.087 | 134.625 | 29.849 | 28.4 | 28.417 | 602.014 | 26.155 | 27.134 | 1264.876 | 27.177 | 27.457 | 36.863 | 24.001 | 2.6 | 3.1 | 1.2 | 0.5 | 0.2
2825 | 30/07/2025 10:35:22.584 | 98.856 | 81 | 100 | 70 | 52 | 28.067 | 9.292 | 7.088 | 134.577 | 29.871 | 28.396 | 28.424 | 603.192 | 26.174 | 27.116 | 1269.806 | 27.199 | 27.455 | 36.885 | 31.001 | 2.3 | 3.1 | 0.6 | 0.5 | 0.2
2826 | 30/07/2025 10:35:24.220 | 98.376 | 80 | 100 | 70 | 52 | 31.197 | 9.432 | 7.135 | 134.581 | 29.841 | 28.375 | 28.441 | 602.009 | 26.151 | 27.13 | 1269.613 | 27.225 | 27.468 | 36.742 | 31.001 | 2.3 | 3.1 | 0.6 | 0.5 | 0.2
2827 | 30/07/2025 10:35:25.854 | 98.376 | 80 | 100 | 70 | 52 | 27.391 | 9.445 | 7.133 | 134.624 | 29.854 | 28.393 | 28.449 | 602.129 | 26.156 | 27.128 | 1273.979 | 27.21 | 27.435 | 36.729 | 31.001 | 2.2 | 4 | 0.7 | 0.2 | 0.2
2828 | 30/07/2025 10:35:27.491 | 98.904 | 81 | 100 | 70 | 52 | 30.677 | 9.2 | 7.136 | 134.301 | 29.837 | 28.419 | 28.42 | 601.891 | 26.15 | 27.132 | 1277.013 | 27.217 | 27.445 | 36.641 | 31.001 | 3.5 | 4 | 0.7 | 1.6 | 0.2
2829 | 30/07/2025 10:35:29.125 | 98.952 | 81 | 100 | 70 | 52 | 31.522 | 9.509 | 7.137 | 134.68 | 29.857 | 28.396 | 28.415 | 601.778 | 26.162 | 27.129 | 1274.381 | 27.181 | 27.452 | 36.769 | 29.001 | 3.3 | 2.1 | 1.2 | 0.3 | 0.2
2830 | 30/07/2025 10:35:30.761 | 99.072 | 82 | 100 | 70 | 52 | 28.207 | 9.217 | 7.132 | 134.586 | 29.866 | 28.391 | 28.41 | 601.99 | 26.143 | 27.115 | 1269.619 | 27.21 | 27.456 | 34.691 | 28.001 | 3.5 | 2.1 | 1.2 | 1.1 | 0.2
2831 | 30/07/2025 10:35:32.395 | 98.52 | 82 | 100 | 70 | 52 | 28.508 | 9.287 | 7.121 | 134.506 | 29.872 | 28.372 | 28.43 | 601.875 | 26.143 | 27.131 | 1277.776 | 27.223 | 27.44 | 36.562 | 25.001 | 3.5 | 2.3 | 0.6 | 0.3 | 0.3
2832 | 30/07/2025 10:35:34.033 | 98.616 | 82 | 100 | 70 | 52 | 29.552 | 8.994 | 7.12 | 134.433 | 29.867 | 28.412 | 28.423 | 602.086 | 26.149 | 27.105 | 1282.784 | 27.206 | 27.446 | 36.344 | 25.001 | 3.5 | 2.3 | 0.6 | 0.3 | 0.3
2833 | 30/07/2025 10:35:35.670 | 98.424 | 81 | 100 | 69 | 52 | 27.657 | 9.16 | 7.138 | 134.53 | 29.876 | 28.397 | 28.416 | 601.891 | 26.153 | 27.133 | 1284.105 | 27.185 | 27.446 | 36.752 | 24.001 | 3.3 | 2.3 | 0.3 | 0 | 0.3
2834 | 30/07/2025 10:35:37.306 | 98.376 | 81 | 100 | 71 | 52 | 31.095 | 9.284 | 7.135 | 134.801 | 29.89 | 28.399 | 28.424 | 601.174 | 26.151 | 27.107 | 1273.712 | 27.183 | 27.459 | 36.573 | 22.001 | 4.6 | 2.7 | 0.6 | 0.5 | 0.2
2835 | 30/07/2025 10:35:38.942 | 98.184 | 82 | 100 | 70 | 52 | 31.482 | 9.311 | 7.135 | 134.353 | 29.872 | 28.389 | 28.414 | 600.398 | 26.15 | 27.113 | 1269.257 | 27.243 | 27.457 | 36.667 | 32.001 | 3.3 | 2.7 | 0.7 | 0.7 | 0.2
2836 | 30/07/2025 10:35:40.577 | 98.136 | 81 | 100 | 69 | 52 | 27.853 | 9.291 | 7.136 | 134.593 | 29.868 | 28.391 | 28.408 | 601.81 | 26.141 | 27.108 | 1247.46 | 27.212 | 27.429 | 36.569 | 27.001 | 3.6 | 1.7 | 1.3 | 0.7 | 0.2
2837 | 30/07/2025 10:35:42.213 | 97.8 | 81 | 100 | 71 | 51 | 29.314 | 9.214 | 7.136 | 134.58 | 29.872 | 28.408 | 28.423 | 600.681 | 26.149 | 27.084 | 1258.038 | 27.203 | 27.448 | 34.678 | 27.001 | 3.6 | 1.7 | 1.3 | 0.7 | 0.2
2838 | 30/07/2025 10:35:43.848 | 98.376 | 81 | 100 | 70 | 52 | 28.945 | 9.271 | 7.135 | 134.889 | 29.893 | 28.405 | 28.427 | 600.551 | 26.158 | 27.102 | 1253.213 | 27.183 | 27.449 | 34.913 | 30.001 | 2 | 1.7 | 1.3 | 0 | 0.2
2839 | 30/07/2025 10:35:45.482 | 98.472 | 82 | 100 | 71 | 52 | 28.172 | 9.435 | 7.135 | 134.741 | 29.868 | 28.405 | 28.42 | 600.576 | 26.153 | 27.075 | 1257.928 | 27.2 | 27.47 | 36.334 | 31.001 | 3.1 | 1.8 | 1.2 | 0.5 | 0.1
2840 | 30/07/2025 10:35:47.120 | 98.664 | 81 | 100 | 70 | 52 | 31.272 | 9.436 | 7.152 | 134.547 | 29.866 | 28.378 | 28.419 | 600.5 | 26.136 | 27.09 | 1267.063 | 27.211 | 27.453 | 36.747 | 24.001 | 3.4 | 1.8 | 1.1 | 0.5 | 0.1
2841 | 30/07/2025 10:35:48.760 | 98.928 | 81 | 100 | 70 | 52 | 31.212 | 9.47 | 7.135 | 134.341 | 29.872 | 28.402 | 28.442 | 600.842 | 26.154 | 27.096 | 1277.282 | 27.206 | 27.425 | 36.556 | 25.001 | 2.3 | 2.2 | 0.6 | 0.5 | 0.1
2842 | 30/07/2025 10:35:50.393 | 98.904 | 81 | 100 | 71 | 52 | 27.576 | 9.262 | 7.134 | 134.559 | 29.862 | 28.413 | 28.424 | 600.566 | 26.152 | 27.106 | 1280.05 | 27.21 | 27.459 | 36.638 | 29.001 | 2.4 | 2.2 | 0 | 0.5 | 0.1
2843 | 30/07/2025 10:35:52.043 | 99.024 | 81 | 100 | 70 | 51 | 31.636 | 9.43 | 7.135 | 134.648 | 29.867 | 28.405 | 28.437 | 600.518 | 26.172 | 27.102 | 1277.623 | 27.184 | 27.463 | 36.634 | 29.001 | 2.4 | 2.2 | 0 | 0.5 | 0.1
2844 | 30/07/2025 10:35:53.680 | 99.168 | 82 | 100 | 70 | 52 | 28.416 | 9.285 | 7.156 | 134.525 | 29.858 | 28.393 | 28.395 | 600.545 | 26.167 | 27.13 | 1273.319 | 27.219 | 27.465 | 36.626 | 24.001 | 2.9 | 1.2 | 1.2 | 0 | 0.1
2845 | 30/07/2025 10:35:55.315 | 99.408 | 81 | 100 | 71 | 52 | 28.628 | 9.432 | 7.186 | 134.593 | 29.863 | 28.377 | 28.428 | 600.597 | 26.165 | 27.13 | 1277.761 | 27.21 | 27.437 | 36.733 | 24.001 | 2.7 | 1.2 | 0.6 | 0 | 0.1
2846 | 30/07/2025 10:35:56.952 | 99.384 | 81 | 100 | 71 | 52 | 31.39 | 9.292 | 7.17 | 134.347 | 29.851 | 28.41 | 28.432 | 600.529 | 26.165 | 27.123 | 1279.608 | 27.215 | 27.437 | 36.496 | 29.001 | 2.7 | 2.4 | 1.2 | 0.5 | 0.1
2847 | 30/07/2025 10:35:58.588 | 98.832 | 81 | 100 | 70 | 52 | 30.576 | 9.428 | 7.183 | 134.629 | 29.834 | 28.396 | 28.409 | 600.534 | 26.159 | 27.14 | 1276.878 | 27.192 | 27.459 | 36.879 | 27.001 | 2.1 | 2.4 | 0.7 | 0 | 0.1
2848 | 30/07/2025 10:36:00.224 | 98.688 | 81 | 98 | 70 | 52 | 27.356 | 9.129 | 7.186 | 134.72 | 29.858 | 28.4 | 28.417 | 600.562 | 26.153 | 27.116 | 1284.953 | 27.199 | 27.451 | 36.685 | 27.001 | 2.1 | 2.4 | 0.7 | 0 | 0.1
2849 | 30/07/2025 10:36:01.859 | 98.832 | 81 | 100 | 71 | 52 | 31.422 | 9.192 | 7.188 | 134.628 | 29.855 | 28.389 | 28.409 | 600.491 | 26.167 | 27.14 | 1284.562 | 27.216 | 27.454 | 36.735 | 22.001 | 1.4 | 1.9 | 1 | 0.5 | 0.1
2850 | 30/07/2025 10:36:03.493 | 98.352 | 82 | 100 | 71 | 51 | 27.773 | 9.168 | 7.185 | 134.374 | 29.863 | 28.395 | 28.455 | 600.44 | 26.143 | 27.107 | 1280.036 | 27.205 | 27.443 | 36.707 | 29.001 | 2.6 | 1.9 | 2 | 0.5 | 0.1
2851 | 30/07/2025 10:36:05.129 | 98.376 | 81 | 100 | 70 | 53 | 29.048 | 8.993 | 7.206 | 134.319 | 29.856 | 28.422 | 28.411 | 600.609 | 26.163 | 27.125 | 1287.082 | 27.231 | 27.447 | 36.534 | 30.001 | 2.3 | 3.4 | 2.2 | 0.6 | 0.1
2852 | 30/07/2025 10:36:06.764 | 98.424 | 82 | 100 | 71 | 51 | 31.42 | 9.281 | 7.196 | 134.879 | 29.876 | 28.394 | 28.417 | 600.574 | 26.171 | 27.116 | 1301.949 | 27.174 | 27.457 | 36.847 | 28.001 | 2.3 | 3.4 | 1.1 | 1.2 | 0.1
2853 | 30/07/2025 10:36:08.398 | 99.096 | 83 | 100 | 72 | 52 | 30.048 | 9.196 | 7.187 | 134.702 | 29.872 | 28.392 | 28.403 | 601.995 | 26.151 | 27.11 | 1297.161 | 27.215 | 27.462 | 36.631 | 25.001 | 3.6 | 3.9 | 1.8 | 0.7 | 0.1
2854 | 30/07/2025 10:36:10.034 | 98.544 | 79 | 100 | 70 | 53 | 31.207 | 9.203 | 7.186 | 134.72 | 29.882 | 28.382 | 28.422 | 601.917 | 26.178 | 27.111 | 1296.58 | 27.211 | 27.46 | 36.637 | 25.001 | 3.6 | 3.9 | 1.8 | 0.7 | 0.1
2855 | 30/07/2025 10:36:11.671 | 98.52 | 81 | 100 | 70 | 53 | 31.121 | 9.223 | 7.17 | 134.495 | 29.875 | 28.401 | 28.425 | 602.143 | 26.145 | 27.104 | 1287.989 | 27.213 | 27.451 | 36.439 | 28.001 | 4 | 3.9 | 0.7 | 0.8 | 0.2
2856 | 30/07/2025 10:36:13.307 | 98.496 | 82 | 100 | 70 | 52 | 27.522 | 9.266 | 7.172 | 134.404 | 29.872 | 28.41 | 28.417 | 601.944 | 26.156 | 27.115 | 1297.066 | 27.199 | 27.442 | 36.564 | 26.001 | 2.5 | 3.1 | 0.7 | 1.1 | 0.1
2857 | 30/07/2025 10:36:14.941 | 98.736 | 81 | 100 | 71 | 52 | 29.831 | 9.218 | 7.139 | 134.852 | 29.883 | 28.406 | 28.424 | 602.185 | 26.138 | 27.092 | 1293.188 | 27.185 | 27.443 | 36.673 | 25.001 | 1.9 | 3.1 | 1.1 | 0.2 | 0.2
2858 | 30/07/2025 10:36:16.586 | 98.544 | 82 | 100 | 70 | 52 | 31.567 | 9.135 | 7.122 | 134.471 | 29.868 | 28.39 | 28.415 | 603.083 | 26.147 | 27.099 | 1287.705 | 27.226 | 27.454 | 36.791 | 32.001 | 1.4 | 0.9 | 0.8 | 0.8 | 0.2
2859 | 30/07/2025 10:36:18.221 | 98.616 | 82 | 100 | 70 | 51 | 29.554 | 9.101 | 7.121 | 134.545 | 29.88 | 28.382 | 28.429 | 603.1 | 26.163 | 27.116 | 1292.33 | 27.204 | 27.435 | 36.681 | 32.001 | 1.4 | 0.9 | 0.8 | 0.8 | 0.2
2860 | 30/07/2025 10:36:19.862 | 98.88 | 82 | 100 | 70 | 52 | 31.394 | 9.164 | 7.122 | 134.281 | 29.853 | 28.407 | 28.429 | 603.292 | 26.134 | 27.102 | 1290.832 | 27.216 | 27.448 | 36.423 | 25.001 | 2.3 | 0.9 | 0.6 | 1.2 | 0.1
2861 | 30/07/2025 10:36:21.497 | 98.856 | 82 | 100 | 70 | 53 | 30.738 | 9.204 | 7.087 | 134.741 | 29.877 | 28.405 | 28.424 | 603.245 | 26.16 | 27.089 | 1297.139 | 27.18 | 27.453 | 36.73 | 28.001 | 2.2 | 3.1 | 1.5 | 0.8 | 0.2
2862 | 30/07/2025 10:36:23.133 | 98.376 | 80 | 100 | 70 | 52 | 27.454 | 9.293 | 7.088 | 134.644 | 29.866 | 28.401 | 28.41 | 603.319 | 26.153 | 27.091 | 1294.471 | 27.201 | 27.462 | 36.746 | 30.001 | 3.8 | 3.1 | 1.1 | 0.5 | 0.2
2863 | 30/07/2025 10:36:24.769 | 98.424 | 83 | 100 | 71 | 51 | 30.5 | 9.317 | 7.088 | 134.511 | 29.865 | 28.375 | 28.42 | 603.104 | 26.151 | 27.115 | 1277.577 | 27.213 | 27.446 | 36.796 | 24.001 | 3.6 | 1.8 | 1.5 | 0.5 | 0.1
2864 | 30/07/2025 10:36:26.406 | 98.64 | 81 | 99 | 69 | 52 | 31.632 | 9.393 | 7.119 | 134.393 | 29.867 | 28.395 | 28.436 | 603.396 | 26.161 | 27.107 | 1272.409 | 27.209 | 27.438 | 36.55 | 23.001 | 1.2 | 1.8 | 1.5 | 0.2 | 0.1
2865 | 30/07/2025 10:36:28.043 | 98.712 | 80 | 100 | 71 | 52 | 29.021 | 9.436 | 7.121 | 134.521 | 29.856 | 28.417 | 28.431 | 603.227 | 26.16 | 27.131 | 1266.953 | 27.221 | 27.457 | 36.534 | 23.001 | 1.2 | 1.8 | 1.5 | 0.2 | 0.1
2866 | 30/07/2025 10:36:29.681 | 98.76 | 82 | 100 | 71 | 52 | 31.459 | 9.432 | 7.134 | 134.682 | 29.859 | 28.407 | 28.424 | 603.292 | 26.162 | 27.112 | 1267.511 | 27.184 | 27.46 | 36.658 | 29.001 | 2.2 | 2.1 | 1.3 | 0 | 0.2
2867 | 30/07/2025 10:36:31.316 | 98.616 | 81 | 100 | 72 | 52 | 30.101 | 9.434 | 7.125 | 134.54 | 29.837 | 28.391 | 28.383 | 603.285 | 26.158 | 27.131 | 1265.783 | 27.224 | 27.455 | 36.845 | 26.001 | 5 | 2.1 | 0.7 | 0 | 0.2
2868 | 30/07/2025 10:36:32.952 | 98.904 | 82 | 100 | 72 | 52 | 27.49 | 9.289 | 7.12 | 134.965 | 29.85 | 28.375 | 28.444 | 603.211 | 26.17 | 27.116 | 1275.877 | 27.21 | 27.443 | 36.724 | 22.001 | 5.2 | 1.1 | 0.6 | 0.8 | 0.2
2869 | 30/07/2025 10:36:34.587 | 98.184 | 81 | 100 | 70 | 52 | 30.732 | 9.437 | 7.135 | 134.326 | 29.845 | 28.399 | 28.421 | 603.321 | 26.164 | 27.12 | 1285.26 | 27.218 | 27.44 | 36.547 | 28.001 | 4 | 1.1 | 1.9 | 0.6 | 0.2
2870 | 30/07/2025 10:36:36.223 | 98.016 | 80 | 100 | 70 | 52 | 31.63 | 9.262 | 7.136 | 134.819 | 29.857 | 28.4 | 28.413 | 603.13 | 26.15 | 27.133 | 1271.065 | 27.182 | 27.465 | 36.805 | 28.001 | 4 | 1.1 | 1.9 | 0.6 | 0.2
2871 | 30/07/2025 10:36:37.858 | 97.872 | 81 | 100 | 69 | 52 | 29.656 | 9 | 7.135 | 134.51 | 29.996 | 28.405 | 28.411 | 603.158 | 26.163 | 27.116 | 1269.273 | 27.187 | 27.474 | 36.658 | 25.001 | 3.8 | 0.5 | 2.1 | 0.5 | 0.2
2872 | 30/07/2025 10:36:39.504 | 97.656 | 80 | 100 | 70 | 52 | 31.574 | 9.511 | 7.136 | 134.57 | 29.996 | 28.383 | 28.395 | 603.269 | 26.163 | 27.112 | 1285.002 | 27.221 | 27.441 | 36.915 | 26.001 | 3.2 | 0.5 | 1.8 | 0.5 | 0.2
2873 | 30/07/2025 10:36:41.141 | 97.296 | 80 | 100 | 70 | 52 | 29.517 | 9.361 | 7.133 | 134.527 | 29.872 | 28.391 | 28.455 | 603.278 | 26.153 | 27.102 | 1288.951 | 27.217 | 27.437 | 36.675 | 27.001 | 2.6 | 2.8 | 1.5 | 0 | 0.2
2874 | 30/07/2025 10:36:42.777 | 97.704 | 81 | 100 | 70 | 52 | 27.747 | 9.129 | 7.136 | 134.359 | 29.886 | 28.41 | 28.431 | 603.223 | 26.156 | 27.125 | 1290.541 | 27.236 | 27.447 | 36.442 | 27.001 | 2.9 | 2.8 | 0.4 | 0.9 | 0.1
2875 | 30/07/2025 10:36:44.414 | 97.728 | 80 | 100 | 69 | 51 | 31.063 | 9.252 | 7.135 | 134.762 | 29.889 | 28.391 | 28.426 | 603.138 | 26.174 | 27.112 | 1299.921 | 27.169 | 27.453 | 36.75 | 26.001 | 2.3 | 2 | 0.6 | 1 | 0.1
2876 | 30/07/2025 10:36:46.050 | 98.088 | 82 | 100 | 71 | 53 | 27.37 | 9.432 | 7.153 | 134.571 | 29.935 | 28.397 | 28.398 | 603.064 | 26.154 | 27.135 | 1294.544 | 27.196 | 27.455 | 36.627 | 26.001 | 2.3 | 2 | 0.6 | 1 | 0.1
2877 | 30/07/2025 10:36:47.690 | 97.824 | 80 | 100 | 70 | 50 | 30.289 | 9.507 | 7.151 | 134.624 | 29.874 | 28.378 | 28.4 | 602.171 | 26.146 | 27.096 | 1292.406 | 27.206 | 27.441 | 36.838 | 29.001 | 2.3 | 2 | 0.6 | 0 | 0.1
2878 | 30/07/2025 10:36:49.326 | 98.184 | 82 | 100 | 70 | 52 | 31.645 | 9.295 | 7.15 | 134.5 | 29.862 | 28.405 | 28.436 | 601.921 | 26.149 | 27.1 | 1291.218 | 27.221 | 27.447 | 36.657 | 27.001 | 1.8 | 2 | 0.9 | 1.9 | 0.1
2879 | 30/07/2025 10:36:50.963 | 97.992 | 82 | 100 | 70 | 52 | 28.888 | 9.282 | 7.136 | 134.567 | 30.023 | 28.403 | 28.431 | 602.961 | 26.151 | 27.114 | 1287.358 | 27.197 | 27.455 | 36.779 | 26.001 | 3.4 | 2 | 0.4 | 0.6 | 0.1
2880 | 30/07/2025 10:36:52.597 | 98.352 | 81 | 100 | 71 | 52 | 28.149 | 9.344 | 7.135 | 134.833 | 30.015 | 28.402 | 28.417 | 602.135 | 26.151 | 27.082 | 1287.39 | 27.174 | 27.459 | 36.677 | 22.001 | 3.1 | 3 | 0.6 | 0.6 | 0.1
2881 | 30/07/2025 10:36:54.233 | 98.352 | 81 | 100 | 70 | 52 | 31.258 | 9.431 | 7.136 | 134.406 | 30.001 | 28.381 | 28.395 | 601.867 | 26.146 | 27.106 | 1293.663 | 27.226 | 27.453 | 36.736 | 22.001 | 3.1 | 3 | 0.6 | 0.6 | 0.1
2882 | 30/07/2025 10:36:55.868 | 98.208 | 79 | 100 | 69 | 54 | 27.474 | 9.286 | 7.133 | 134.709 | 30.011 | 28.388 | 28.42 | 602 | 26.142 | 27.077 | 1287.444 | 27.218 | 27.452 | 36.576 | 24.001 | 4.8 | 3 | 1.1 | 0.5 | 0.1
2883 | 30/07/2025 10:36:57.506 | 97.848 | 81 | 100 | 71 | 52 | 30.82 | 9.137 | 7.152 | 134.292 | 30.007 | 28.4 | 28.417 | 601.781 | 26.16 | 27.108 | 1277.308 | 27.212 | 27.429 | 36.538 | 23.001 | 3.3 | 1.7 | 0.6 | 0.5 | 0.1
2884 | 30/07/2025 10:36:59.139 | 97.992 | 79 | 100 | 70 | 51 | 31.632 | 9.209 | 7.135 | 134.601 | 30.026 | 28.407 | 28.424 | 601.816 | 26.16 | 27.096 | 1277.08 | 27.183 | 27.452 | 36.585 | 25.001 | 2.5 | 1.7 | 1 | 0.8 | 0.3
2885 | 30/07/2025 10:37:00.774 | 97.488 | 80 | 100 | 70 | 51 | 28.448 | 9.263 | 7.135 | 134.654 | 30.01 | 28.408 | 28.419 | 602.059 | 26.161 | 27.128 | 1277.224 | 27.203 | 27.471 | 36.691 | 28.001 | 2.2 | 1.8 | 1.2 | 1.1 | 0.2
2886 | 30/07/2025 10:37:02.407 | 97.008 | 80 | 100 | 70 | 52 | 28.728 | 9.281 | 7.136 | 134.461 | 30.009 | 28.369 | 28.414 | 601.812 | 26.167 | 27.124 | 1285.839 | 27.213 | 27.446 | 36.756 | 30.001 | 2.2 | 1.8 | 0.9 | 0.5 | 0.2
2887 | 30/07/2025 10:37:04.045 | 97.296 | 79 | 100 | 70 | 51 | 29.585 | 9.284 | 7.134 | 134.533 | 29.986 | 28.388 | 28.426 | 602.004 | 26.16 | 27.115 | 1277.563 | 27.227 | 27.449 | 36.81 | 30.001 | 2.2 | 1.8 | 0.9 | 0.5 | 0.2
2888 | 30/07/2025 10:37:05.682 | 97.872 | 79 | 100 | 70 | 52 | 27.755 | 9.291 | 7.135 | 134.454 | 30.01 | 28.403 | 28.422 | 601.859 | 26.17 | 27.123 | 1277.036 | 27.2 | 27.429 | 36.616 | 26.001 | 2.8 | 2.1 | 1.7 | 0.5 | 0.2
2889 | 30/07/2025 10:37:07.317 | 98.376 | 79 | 100 | 71 | 52 | 31.144 | 9.244 | 7.134 | 134.459 | 29.988 | 28.406 | 28.428 | 601.993 | 26.15 | 27.124 | 1270.086 | 27.186 | 27.472 | 36.735 | 28.001 | 1.6 | 2.1 | 1.1 | 0.8 | 0.2
2890 | 30/07/2025 10:37:08.953 | 98.16 | 82 | 100 | 70 | 52 | 31.481 | 9.357 | 7.137 | 133.025 | 29.986 | 28.392 | 28.389 | 601.909 | 26.152 | 27.128 | 1262.177 | 27.21 | 27.448 | 36.724 | 24.001 | 2.6 | 1.5 | 2 | 0.9 | 0.2
2891 | 30/07/2025 10:37:10.588 | 98.544 | 81 | 100 | 71 | 52 | 27.949 | 9.286 | 7.151 | 133.33 | 30.004 | 28.384 | 28.437 | 601.86 | 26.168 | 27.113 | 1259.909 | 27.214 | 27.439 | 36.666 | 24.001 | 2.3 | 1.5 | 0.8 | 0.5 | 0.2
2892 | 30/07/2025 10:37:12.227 | 98.736 | 82 | 100 | 71 | 52 | 29.112 | 9.214 | 7.135 | 132.78 | 29.998 | 28.409 | 28.434 | 602.04 | 26.157 | 27.108 | 1257.425 | 27.226 | 27.438 | 36.405 | 24.001 | 2.3 | 1.5 | 0.8 | 0.5 | 0.2
2893 | 30/07/2025 10:37:13.862 | 98.64 | 82 | 100 | 70 | 52 | 28.993 | 9.127 | 7.136 | 132.995 | 30.023 | 28.412 | 28.439 | 601.949 | 26.16 | 27.109 | 1257.792 | 27.204 | 27.442 | 36.417 | 31.001 | 2.1 | 1.1 | 0.8 | 0 | 0.2
2894 | 30/07/2025 10:37:15.499 | 99.048 | 81 | 100 | 70 | 52 | 28.131 | 9.276 | 7.135 | 133.037 | 30.011 | 28.41 | 28.418 | 601.833 | 26.152 | 27.113 | 1264.695 | 27.185 | 27.466 | 36.656 | 26.001 | 2.4 | 1.1 | 0.9 | 1 | 0.2
2895 | 30/07/2025 10:37:17.137 | 99.504 | 81 | 100 | 71 | 52 | 31.274 | 9.431 | 7.137 | 133.243 | 30.019 | 28.385 | 28.39 | 602.025 | 26.153 | 27.118 | 1273.789 | 27.212 | 27.452 | 36.676 | 26.001 | 2.7 | 2.4 | 0.6 | 0.5 | 0.2
2896 | 30/07/2025 10:37:18.771 | 100.584 | 83 | 100 | 70 | 51 | 31.185 | 9.432 | 7.132 | 133.048 | 30.01 | 28.388 | 28.435 | 602.01 | 26.155 | 27.104 | 1279.898 | 27.211 | 27.454 | 36.505 | 28.001 | 4.8 | 2.4 | 0.6 | 0.8 | 0.1
2897 | 30/07/2025 10:37:20.407 | 100.728 | 83 | 100 | 70 | 52 | 27.541 | 9.389 | 7.137 | 132.848 | 30.015 | 28.409 | 28.41 | 601.781 | 26.142 | 27.119 | 1276.999 | 27.211 | 27.434 | 36.433 | 29.001 | 4.5 | 2.1 | 0.6 | 0.5 | 0.1
2898 | 30/07/2025 10:37:22.042 | 100.248 | 83 | 100 | 71 | 52 | 29.756 | 9.282 | 7.135 | 133.349 | 30.027 | 28.394 | 28.421 | 600.381 | 26.147 | 27.092 | 1278.269 | 27.174 | 27.447 | 36.892 | 29.001 | 4.5 | 2.1 | 0.6 | 0.5 | 0.1
2899 | 30/07/2025 10:37:23.677 | 100.224 | 83 | 100 | 70 | 52 | 28.328 | 9.504 | 7.137 | 133.258 | 30.015 | 28.403 | 28.402 | 600.398 | 26.149 | 27.102 | 1282.497 | 27.181 | 27.456 | 36.903 | 27.001 | 3.3 | 2.1 | 2.1 | 1 | 0.2
2900 | 30/07/2025 10:37:25.316 | 101.04 | 83 | 100 | 70 | 51 | 28.588 | 9.434 | 7.134 | 133.171 | 30.037 | 28.384 | 28.424 | 602.074 | 26.138 | 27.094 | 1289.712 | 27.211 | 27.449 | 36.744 | 29.001 | 3.2 | 1.5 | 0.5 | 0.5 | 0.2
2901 | 30/07/2025 10:37:26.952 | 101.568 | 84 | 100 | 70 | 52 | 31.421 | 9.296 | 7.133 | 133.056 | 30.011 | 28.396 | 28.434 | 602.046 | 26.145 | 27.08 | 1291.947 | 27.227 | 27.443 | 36.684 | 21.001 | 2.6 | 1.5 | 0.9 | 0.2 | 0.2
2902 | 30/07/2025 10:37:28.587 | 101.088 | 84 | 100 | 70 | 52 | 30.773 | 9.288 | 7.135 | 133.292 | 30.025 | 28.4 | 28.415 | 601.971 | 26.154 | 27.085 | 1291.161 | 27.202 | 27.437 | 36.693 | 30.001 | 1.2 | 1.4 | 2.2 | 0.5 | 0.2
2903 | 30/07/2025 10:37:30.221 | 100.824 | 84 | 100 | 70 | 52 | 27.39 | 9.284 | 7.135 | 133.265 | 30.002 | 28.405 | 28.416 | 601.947 | 26.152 | 27.082 | 1303.951 | 27.177 | 27.461 | 36.679 | 30.001 | 1.2 | 1.4 | 2.2 | 0.5 | 0.2
2904 | 30/07/2025 10:37:31.856 | 100.392 | 84 | 100 | 72 | 53 | 31.508 | 9.396 | 7.136 | 133.333 | 30.018 | 28.393 | 28.387 | 601.774 | 26.172 | 27.1 | 1308.353 | 27.193 | 27.457 | 36.592 | 28.001 | 2 | 1.4 | 0.9 | 0 | 0.3
2905 | 30/07/2025 10:37:33.491 | 100.008 | 83 | 100 | 70 | 52 | 27.956 | 9.434 | 7.134 | 134.56 | 29.994 | 28.373 | 28.423 | 602.006 | 26.156 | 27.105 | 1306.744 | 27.217 | 27.464 | 36.618 | 25.001 | 2.3 | 2 | 0.2 | 1 | 0.3
2906 | 30/07/2025 10:37:35.126 | 99.504 | 83 | 100 | 70 | 50 | 29.328 | 9.289 | 7.124 | 134.405 | 29.996 | 28.398 | 28.42 | 600.519 | 26.149 | 27.129 | 1304.637 | 27.215 | 27.445 | 36.482 | 28.001 | 2.3 | 2 | 1.2 | 0.8 | 0.3
2907 | 30/07/2025 10:37:36.761 | 99.504 | 82 | 100 | 71 | 52 | 31.545 | 9.13 | 7.123 | 134.658 | 30.003 | 28.399 | 28.426 | 602.096 | 26.162 | 27.12 | 1307.231 | 27.192 | 27.447 | 36.672 | 31.001 | 2.3 | 3.5 | 1.7 | 1 | 0.3
2908 | 30/07/2025 10:37:38.397 | 99.432 | 83 | 100 | 71 | 52 | 30.227 | 9.287 | 7.12 | 134.592 | 29.984 | 28.414 | 28.399 | 601.858 | 26.158 | 27.116 | 1309.36 | 27.201 | 27.456 | 36.715 | 28.001 | 1.5 | 3.5 | 1.4 | 0.6 | 0.3
2909 | 30/07/2025 10:37:40.035 | 99.72 | 83 | 100 | 71 | 52 | 27.471 | 9.458 | 7.124 | 134.537 | 29.997 | 28.372 | 28.404 | 601.881 | 26.163 | 27.12 | 1302.758 | 27.215 | 27.447 | 36.539 | 28.001 | 1.5 | 3.5 | 1.4 | 0.6 | 0.3
2910 | 30/07/2025 10:37:41.670 | 99.216 | 82 | 100 | 70 | 52 | 31.256 | 9.284 | 7.121 | 134.582 | 29.979 | 28.375 | 28.413 | 601.803 | 26.153 | 27.133 | 1296.861 | 27.213 | 27.45 | 36.675 | 25.001 | 2.1 | 2.2 | 1 | 0.6 | 0.3
2911 | 30/07/2025 10:37:43.306 | 99.48 | 82 | 100 | 72 | 52 | 27.601 | 9.286 | 7.06 | 134.545 | 29.998 | 28.404 | 28.428 | 600.74 | 26.167 | 27.115 | 1306.658 | 27.203 | 27.424 | 36.529 | 26.001 | 2.4 | 2.2 | 1.3 | 0.3 | 0.2
2912 | 30/07/2025 10:37:44.942 | 99.456 | 82 | 100 | 70 | 52 | 29.814 | 9.211 | 7.059 | 134.601 | 30.01 | 28.408 | 28.427 | 600.528 | 26.154 | 27.106 | 1305.328 | 27.183 | 27.472 | 36.715 | 28.001 | 1.9 | 2.3 | 1.2 | 0 | 0.3
2913 | 30/07/2025 10:37:46.580 | 99.624 | 82 | 100 | 71 | 52 | 31.587 | 9.429 | 7.062 | 134.641 | 30.006 | 28.392 | 28.405 | 600.457 | 26.153 | 27.134 | 1297.129 | 27.193 | 27.455 | 36.756 | 22.001 | 3.3 | 2.3 | 0.6 | 0.5 | 0.3
2914 | 30/07/2025 10:37:48.216 | 98.88 | 82 | 100 | 71 | 52 | 29.647 | 9.579 | 7.07 | 134.595 | 30.024 | 28.382 | 28.438 | 600.676 | 26.169 | 27.113 | 1303.575 | 27.211 | 27.454 | 36.494 | 22.001 | 3.3 | 2.3 | 0.6 | 0.5 | 0.3
2915 | 30/07/2025 10:37:49.851 | 98.952 | 81 | 100 | 71 | 52 | 31.401 | 9.293 | 7.074 | 134.636 | 30.007 | 28.385 | 28.428 | 600.449 | 26.155 | 27.126 | 1295.474 | 27.2 | 27.434 | 36.503 | 26.001 | 3.4 | 3.9 | 1.2 | 0 | 0.3
2916 | 30/07/2025 10:37:51.486 | 98.88 | 82 | 100 | 69 | 52 | 30.761 | 9.187 | 7.072 | 134.608 | 30.024 | 28.408 | 28.442 | 600.566 | 26.153 | 27.101 | 1297.34 | 27.203 | 27.441 | 36.456 | 27.001 | 5 | 3.9 | 0.6 | 1.5 | 0.3
2917 | 30/07/2025 10:37:53.123 | 98.832 | 82 | 100 | 70 | 52 | 27.409 | 9.133 | 7.07 | 134.601 | 30.014 | 28.405 | 28.403 | 600.504 | 26.155 | 27.123 | 1301.719 | 27.199 | 27.458 | 36.763 | 29.001 | 3.9 | 1.8 | 0.6 | 0.7 | 0.3
2918 | 30/07/2025 10:37:54.758 | 98.64 | 81 | 100 | 70 | 52 | 30.275 | 9.286 | 7.07 | 134.814 | 30.03 | 28.392 | 28.396 | 600.484 | 26.156 | 27.113 | 1296.705 | 27.209 | 27.445 | 36.586 | 29.001 | 4.3 | 1.8 | 1.6 | 0.5 | 0.3
2919 | 30/07/2025 10:37:56.392 | 98.832 | 82 | 100 | 70 | 52 | 31.667 | 9.16 | 7.057 | 134.503 | 30.004 | 28.382 | 28.432 | 600.558 | 26.139 | 27.094 | 1307.316 | 27.22 | 27.455 | 36.314 | 25.001 | 2.8 | 1.9 | 0.6 | 0.6 | 0.3
2920 | 30/07/2025 10:37:58.037 | 97.848 | 82 | 100 | 70 | 51 | 29.11 | 9.326 | 7.058 | 134.652 | 30.034 | 28.394 | 28.421 | 600.663 | 26.148 | 27.108 | 1311.742 | 27.198 | 27.429 | 36.426 | 25.001 | 2.8 | 1.9 | 0.6 | 0.6 | 0.3
2921 | 30/07/2025 10:37:59.673 | 98.376 | 81 | 100 | 70 | 52 | 31.51 | 9.286 | 7.061 | 134.534 | 29.998 | 28.411 | 28.428 | 600.493 | 26.127 | 27.072 | 1301.83 | 27.209 | 27.458 | 36.54 | 25.001 | 1.7 | 1.9 | 2.5 | 0 | 0.3
2922 | 30/07/2025 10:38:01.307 | 98.112 | 81 | 100 | 71 | 51 | 30.175 | 9.286 | 6.99 | 134.625 | 30.012 | 28.399 | 28.411 | 600.412 | 26.145 | 27.098 | 1309.182 | 27.165 | 27.457 | 36.701 | 26.001 | 3.8 | 3.2 | 1.2 | 0.5 | 0.3
2923 | 30/07/2025 10:38:02.943 | 98.04 | 82 | 100 | 71 | 52 | 27.44 | 9.288 | 6.933 | 134.711 | 30.014 | 28.389 | 28.429 | 600.605 | 26.149 | 27.102 | 1312.329 | 27.209 | 27.466 | 36.679 | 26.001 | 2.5 | 3.2 | 0.3 | 0 | 0.3
2924 | 30/07/2025 10:38:04.577 | 98.4 | 82 | 100 | 70 | 52 | 30.778 | 9.29 | 6.95 | 134.498 | 29.991 | 28.396 | 28.419 | 600.347 | 26.164 | 27.099 | 1298.525 | 27.232 | 27.438 | 36.502 | 25.001 | 0.9 | 2.1 | 1 | 0 | 0.3
2925 | 30/07/2025 10:38:06.214 | 98.712 | 82 | 100 | 70 | 52 | 31.629 | 9.13 | 6.935 | 134.57 | 30.023 | 28.402 | 28.423 | 600.99 | 26.162 | 27.11 | 1297.369 | 27.2 | 27.44 | 36.647 | 25.001 | 0.9 | 2.1 | 1 | 0 | 0.3
2926 | 30/07/2025 10:38:07.850 | 98.376 | 81 | 100 | 70 | 52 | 29.811 | 9.167 | 6.935 | 134.613 | 30.01 | 28.404 | 28.415 | 601.937 | 26.158 | 27.128 | 1298.497 | 27.21 | 27.461 | 36.73 | 27.001 | 2.1 | 2.1 | 0.7 | 0 | 0.3
2927 | 30/07/2025 10:38:09.486 | 98.376 | 82 | 100 | 70 | 52 | 31.614 | 9.283 | 6.925 | 134.791 | 30.024 | 28.404 | 28.404 | 602.001 | 26.179 | 27.108 | 1288.136 | 27.184 | 27.45 | 36.771 | 22.001 | 2.5 | 3 | 1.9 | 0.5 | 0.3
2928 | 30/07/2025 10:38:11.121 | 98.16 | 80 | 100 | 71 | 52 | 29.575 | 9.287 | 6.915 | 134.563 | 29.997 | 28.381 | 28.436 | 601.942 | 26.167 | 27.114 | 1282.165 | 27.223 | 27.476 | 36.522 | 24.001 | 1.8 | 3 | 0.6 | 0.8 | 0.2
2929 | 30/07/2025 10:38:12.761 | 99.072 | 82 | 100 | 70 | 52 | 27.734 | 9.227 | 6.952 | 134.499 | 29.982 | 28.392 | 28.427 | 601.834 | 26.158 | 27.142 | 1274.406 | 27.205 | 27.444 | 36.502 | 25.001 | 3.7 | 1.1 | 1.1 | 0.4 | 0.2
2930 | 30/07/2025 10:38:14.399 | 98.952 | 82 | 100 | 71 | 51 | 31.058 | 9.206 | 6.962 | 134.634 | 29.992 | 28.405 | 28.428 | 602.134 | 26.157 | 27.094 | 1276.263 | 27.195 | 27.451 | 36.576 | 26.001 | 2.7 | 1.1 | 2.3 | 0.5 | 0.2
2931 | 30/07/2025 10:38:16.046 | 99.192 | 81 | 99 | 72 | 52 | 27.422 | 9.182 | 7.005 | 134.896 | 29.986 | 28.4 | 28.42 | 601.941 | 26.163 | 27.125 | 1276.767 | 27.179 | 27.462 | 36.747 | 26.001 | 2.7 | 1.1 | 2.3 | 0.5 | 0.2
2932 | 30/07/2025 10:38:17.685 | 99.36 | 83 | 100 | 70 | 52 | 30.304 | 9.303 | 7.004 | 134.611 | 29.994 | 28.399 | 28.411 | 602.036 | 26.152 | 27.102 | 1279.513 | 27.203 | 27.453 | 36.667 | 22.001 | 2.3 | 1.9 | 1.2 | 0 | 0.2
2933 | 30/07/2025 10:38:19.325 | 99.36 | 83 | 100 | 70 | 52 | 31.644 | 9.285 | 7.003 | 134.435 | 29.999 | 28.377 | 28.42 | 601.875 | 26.154 | 27.125 | 1284.093 | 27.23 | 27.443 | 36.598 | 25.001 | 3.5 | 1.9 | 2.8 | 0.5 | 0.2
2934 | 30/07/2025 10:38:20.961 | 99.576 | 82 | 100 | 70 | 52 | 29.029 | 9.218 | 7.039 | 134.612 | 30.014 | 28.407 | 28.421 | 602.01 | 26.168 | 27.123 | 1295.086 | 27.204 | 27.42 | 36.381 | 29.001 | 1.8 | 2.1 | 2 | 0.5 | 0.2
2935 | 30/07/2025 10:38:22.598 | 99.336 | 82 | 100 | 70 | 52 | 28.213 | 9.32 | 7.06 | 134.688 | 30.001 | 28.413 | 28.424 | 602.006 | 26.15 | 27.113 | 1297.185 | 27.19 | 27.475 | 36.635 | 22.001 | 2.7 | 2.1 | 1.5 | 0.6 | 0.2
2936 | 30/07/2025 10:38:24.234 | 98.928 | 83 | 100 | 70 | 53 | 31.291 | 9.39 | 7.071 | 134.715 | 30.019 | 28.398 | 28.375 | 601.94 | 26.157 | 27.128 | 1296.465 | 27.188 | 27.449 | 36.684 | 22.001 | 2.7 | 2.1 | 1.5 | 0.6 | 0.2
2937 | 30/07/2025 10:38:25.871 | 99.048 | 82 | 100 | 71 | 52 | 27.458 | 9.507 | 7.073 | 134.571 | 30.021 | 28.395 | 28.4 | 602.087 | 26.149 | 27.107 | 1296.491 | 27.236 | 27.462 | 36.646 | 24.001 | 4.7 | 1.8 | 0.7 | 0 | 0.1
2938 | 30/07/2025 10:38:27.508 | 98.784 | 82 | 100 | 70 | 51 | 30.817 | 9.221 | 7.122 | 134.591 | 30.029 | 28.379 | 28.433 | 601.927 | 26.155 | 27.118 | 1314.394 | 27.213 | 27.438 | 36.489 | 29.001 | 2.3 | 1.8 | 2.4 | 0.5 | 0.1
2939 | 30/07/2025 10:38:29.144 | 98.424 | 81 | 100 | 71 | 52 | 31.639 | 9.11 | 7.06 | 134.504 | 30.02 | 28.4 | 28.43 | 602.008 | 26.145 | 27.104 | 1307.024 | 27.205 | 27.446 | 36.299 | 31.001 | 1.7 | 3.1 | 1 | 0.6 | 0.2
2940 | 30/07/2025 10:38:30.778 | 99.096 | 84 | 100 | 72 | 52 | 28.502 | 9.283 | 7.061 | 134.741 | 29.999 | 28.405 | 28.409 | 601.909 | 26.14 | 27.124 | 1321.744 | 27.189 | 27.471 | 36.672 | 22.001 | 2.9 | 3.1 | 0.9 | 0.8 | 0.2
2941 | 30/07/2025 10:38:32.411 | 99.312 | 83 | 100 | 70 | 52 | 28.59 | 9.133 | 7.06 | 134.754 | 30.024 | 28.394 | 28.4 | 601.877 | 26.168 | 27.102 | 1321.725 | 27.196 | 27.439 | 36.652 | 30.001 | 4.5 | 2.4 | 1.7 | 0.4 | 0.2
2942 | 30/07/2025 10:38:34.047 | 99.024 | 81 | 100 | 71 | 52 | 29.722 | 9.464 | 7.061 | 134.604 | 30.002 | 28.378 | 28.41 | 601.804 | 26.148 | 27.107 | 1316.785 | 27.226 | 27.453 | 36.721 | 30.001 | 4.5 | 2.4 | 1.7 | 0.4 | 0.2
2943 | 30/07/2025 10:38:35.682 | 99.096 | 83 | 100 | 70 | 52 | 27.652 | 9.29 | 7.084 | 134.618 | 30.018 | 28.399 | 28.438 | 601.9 | 26.148 | 27.087 | 1311.669 | 27.214 | 27.423 | 36.445 | 29.001 | 1.9 | 2.4 | 1 | 0 | 0.2
2944 | 30/07/2025 10:38:37.316 | 98.568 | 82 | 100 | 70 | 52 | 31.153 | 9.136 | 7.15 | 134.482 | 30.002 | 28.407 | 28.421 | 601.983 | 26.152 | 27.094 | 1304.561 | 27.217 | 27.445 | 36.555 | 27.001 | 1.9 | 1.8 | 1.1 | 1.6 | 0.2
2945 | 30/07/2025 10:38:38.952 | 99.168 | 83 | 100 | 70 | 52 | 31.544 | 9.137 | 7.138 | 134.767 | 30.024 | 28.395 | 28.409 | 601.775 | 26.156 | 27.103 | 1309.288 | 27.183 | 27.449 | 36.579 | 30.001 | 2.3 | 1.8 | 1.3 | 0.6 | 0.2
2946 | 30/07/2025 10:38:40.592 | 99.192 | 82 | 100 | 71 | 52 | 27.932 | 9.393 | 7.134 | 134.675 | 30.019 | 28.381 | 28.405 | 602.139 | 26.141 | 27.093 | 1306.925 | 27.213 | 27.451 | 36.519 | 27.001 | 1.8 | 3.9 | 0.3 | 0 | 0.2
2947 | 30/07/2025 10:38:42.228 | 98.928 | 81 | 99 | 70 | 52 | 29.241 | 9.412 | 7.135 | 134.555 | 30.005 | 28.382 | 28.445 | 601.975 | 26.169 | 27.134 | 1306.971 | 27.228 | 27.454 | 36.429 | 27.001 | 1.8 | 3.9 | 0.3 | 0 | 0.2
2948 | 30/07/2025 10:38:43.862 | 98.808 | 82 | 100 | 70 | 52 | 28.998 | 9.252 | 7.135 | 134.469 | 30.004 | 28.405 | 28.43 | 602.012 | 26.156 | 27.117 | 1311.599 | 27.206 | 27.446 | 36.359 | 25.001 | 2.1 | 3.9 | 0.6 | 0 | 0.3
2949 | 30/07/2025 10:38:45.494 | 99.024 | 81 | 100 | 71 | 54 | 28.172 | 9.128 | 7.137 | 134.523 | 29.994 | 28.401 | 28.402 | 601.987 | 26.151 | 27.143 | 1309.437 | 27.19 | 27.458 | 36.688 | 25.001 | 3.5 | 1.9 | 0.9 | 0 | 0.2
2950 | 30/07/2025 10:38:47.127 | 98.4 | 81 | 100 | 70 | 52 | 31.326 | 9.5 | 7.134 | 134.797 | 29.999 | 28.4 | 28.393 | 602.059 | 26.155 | 27.112 | 1304.376 | 27.178 | 27.462 | 36.587 | 25.001 | 3.5 | 1.9 | 1.4 | 0 | 0.2
2951 | 30/07/2025 10:38:48.761 | 98.64 | 83 | 100 | 71 | 52 | 31.281 | 9.289 | 7.134 | 134.659 | 29.975 | 28.387 | 28.419 | 601.926 | 26.17 | 27.117 | 1314.773 | 27.234 | 27.462 | 36.597 | 27.001 | 2.2 | 3.1 | 0 | 1 | 0.2
2952 | 30/07/2025 10:38:50.393 | 98.76 | 82 | 100 | 71 | 52 | 27.552 | 9.581 | 7.135 | 134.587 | 29.996 | 28.398 | 28.429 | 601.85 | 26.159 | 27.116 | 1318.283 | 27.204 | 27.432 | 36.544 | 28.001 | 2.8 | 3.1 | 0.9 | 1.1 | 0.2
2953 | 30/07/2025 10:38:52.035 | 98.04 | 82 | 100 | 70 | 53 | 31.648 | 9.47 | 7.135 | 134.332 | 29.991 | 28.418 | 28.43 | 601.787 | 26.157 | 27.125 | 1307.58 | 27.23 | 27.439 | 36.556 | 28.001 | 2.8 | 3.1 | 0.9 | 1.1 | 0.2
2954 | 30/07/2025 10:38:53.666 | 98.376 | 81 | 100 | 70 | 52 | 28.38 | 9.494 | 7.15 | 134.758 | 29.996 | 28.399 | 28.422 | 602.097 | 26.161 | 27.115 | 1306.057 | 27.185 | 27.454 | 36.764 | 28.001 | 2 | 3.7 | 0.4 | 1.1 | 0.2
2955 | 30/07/2025 10:38:55.301 | 98.976 | 82 | 100 | 70 | 50 | 28.666 | 9.432 | 7.14 | 134.672 | 30.011 | 28.397 | 28.411 | 602.172 | 26.145 | 27.094 | 1311.363 | 27.197 | 27.454 | 36.716 | 26.001 | 2 | 3.7 | 1.5 | 0.7 | 0.2
2956 | 30/07/2025 10:38:56.936 | 98.136 | 80 | 100 | 70 | 52 | 31.416 | 9.434 | 7.136 | 134.623 | 30.008 | 28.371 | 28.418 | 602.04 | 26.151 | 27.12 | 1290.089 | 27.217 | 27.446 | 36.777 | 29.001 | 3.1 | 2.1 | 0.7 | 0 | 0.2
2957 | 30/07/2025 10:38:58.573 | 98.784 | 82 | 100 | 70 | 52 | 30.83 | 9.128 | 7.164 | 134.534 | 30.03 | 28.405 | 28.423 | 603.245 | 26.168 | 27.107 | 1285.551 | 27.205 | 27.423 | 36.469 | 26.001 | 2.9 | 2.1 | 0.6 | 0.5 | 0.1
2958 | 30/07/2025 10:39:00.209 | 97.992 | 82 | 100 | 70 | 52 | 27.453 | 9.286 | 7.163 | 134.596 | 30.023 | 28.404 | 28.426 | 603.189 | 26.147 | 27.103 | 1289.765 | 27.2 | 27.472 | 36.68 | 26.001 | 2.9 | 2.1 | 0.6 | 0.5 | 0.1
2959 | 30/07/2025 10:39:01.847 | 97.704 | 81 | 100 | 70 | 52 | 31.502 | 9.416 | 7.135 | 134.836 | 30.018 | 28.403 | 28.429 | 603.315 | 26.153 | 27.103 | 1289.754 | 27.182 | 27.466 | 36.714 | 26.001 | 3 | 3 | 0.6 | 0.5 | 0.2
2960 | 30/07/2025 10:39:03.483 | 98.064 | 81 | 100 | 70 | 52 | 27.986 | 9.352 | 7.136 | 134.662 | 30.01 | 28.396 | 28.392 | 603.228 | 26.14 | 27.101 | 1279.237 | 27.229 | 27.448 | 36.674 | 31.001 | 1.9 | 3 | 1.2 | 0.5 | 0.2
2961 | 30/07/2025 10:39:05.119 | 97.536 | 80 | 100 | 70 | 52 | 29.122 | 9.287 | 7.136 | 134.585 | 30.021 | 28.379 | 28.434 | 603.16 | 26.149 | 27.108 | 1276.9 | 27.203 | 27.432 | 36.673 | 28.001 | 2.7 | 2 | 0.9 | 0.8 | 0.2
2962 | 30/07/2025 10:39:06.756 | 97.728 | 82 | 100 | 70 | 52 | 31.574 | 9.333 | 7.134 | 134.501 | 30.011 | 28.401 | 28.432 | 603.112 | 26.143 | 27.081 | 1277.276 | 27.212 | 27.433 | 36.441 | 26.001 | 1.1 | 2 | 1.6 | 0.1 | 0.2
2963 | 30/07/2025 10:39:08.392 | 97.992 | 81 | 100 | 70 | 51 | 30.358 | 9.284 | 7.137 | 134.637 | 30.013 | 28.401 | 28.413 | 603.064 | 26.133 | 27.088 | 1281.875 | 27.187 | 27.457 | 36.842 | 29.001 | 2.4 | 0.7 | 0.9 | 0 | 0.2
2964 | 30/07/2025 10:39:10.035 | 97.656 | 81 | 100 | 70 | 51 | 31.36 | 9.284 | 7.136 | 134.655 | 30.012 | 28.399 | 28.409 | 603.391 | 26.149 | 27.072 | 1285.955 | 27.188 | 27.465 | 36.946 | 29.001 | 2.4 | 0.7 | 0.9 | 0 | 0.2
2965 | 30/07/2025 10:39:11.668 | 97.536 | 81 | 100 | 70 | 52 | 31.334 | 9.29 | 7.136 | 134.575 | 30.003 | 28.376 | 28.415 | 603.22 | 26.148 | 27.102 | 1291.929 | 27.218 | 27.448 | 36.798 | 25.001 | 2.7 | 0.7 | 0.6 | 0.5 | 0.2
2966 | 30/07/2025 10:39:13.303 | 97.896 | 81 | 100 | 71 | 53 | 27.646 | 9.431 | 7.133 | 134.538 | 30.028 | 28.388 | 28.441 | 603.224 | 26.156 | 27.096 | 1297.041 | 27.205 | 27.437 | 36.41 | 27.001 | 2.6 | 2.6 | 1.7 | 0.5 | 0.1
2967 | 30/07/2025 10:39:14.939 | 97.704 | 81 | 100 | 70 | 52 | 29.808 | 9.174 | 7.138 | 134.379 | 30.001 | 28.415 | 28.413 | 603.213 | 26.163 | 27.119 | 1290.476 | 27.225 | 27.45 | 36.592 | 31.001 | 3.2 | 2.6 | 0.9 | 0.6 | 0.1
2968 | 30/07/2025 10:39:16.576 | 97.944 | 80 | 100 | 70 | 52 | 31.636 | 9.128 | 7.135 | 134.853 | 30.005 | 28.401 | 28.402 | 603.182 | 26.169 | 27.118 | 1280.666 | 27.173 | 27.447 | 36.771 | 24.001 | 2.1 | 1.6 | 1.6 | 0.5 | 0.1
2969 | 30/07/2025 10:39:18.213 | 98.328 | 81 | 100 | 69 | 53 | 29.564 | 9.434 | 7.134 | 134.667 | 30.006 | 28.394 | 28.401 | 602.043 | 26.151 | 27.118 | 1271.854 | 27.211 | 27.447 | 36.719 | 24.001 | 2.1 | 1.6 | 1.6 | 0.5 | 0.1
2970 | 30/07/2025 10:39:19.849 | 98.64 | 82 | 100 | 70 | 52 | 31.459 | 9.487 | 7.132 | 134.721 | 30.019 | 28.379 | 28.423 | 601.916 | 26.19 | 27.129 | 1274.182 | 27.216 | 27.445 | 36.731 | 29.001 | 1.8 | 1.6 | 0.9 | 0.6 | 0.1
2971 | 30/07/2025 10:39:21.484 | 98.472 | 82 | 100 | 70 | 52 | 30.718 | 9.691 | 7.121 | 134.351 | 29.982 | 28.406 | 28.425 | 601.964 | 26.172 | 27.115 | 1281.38 | 27.216 | 27.445 | 36.345 | 28.001 | 3.2 | 2 | 1 | 0 | 0.1
2972 | 30/07/2025 10:39:23.118 | 98.328 | 80 | 100 | 70 | 52 | 27.404 | 9.209 | 7.065 | 134.549 | 29.986 | 28.401 | 28.42 | 601.828 | 26.161 | 27.134 | 1284.574 | 27.19 | 27.443 | 36.671 | 28.001 | 3 | 2 | 0.9 | 0.5 | 0.1
2973 | 30/07/2025 10:39:24.752 | 98.304 | 81 | 100 | 70 | 52 | 30.217 | 9.492 | 7.06 | 134.767 | 29.995 | 28.401 | 28.418 | 601.864 | 26.158 | 27.111 | 1285.061 | 27.18 | 27.448 | 36.72 | 29.001 | 4 | 1.8 | 1.3 | 0.2 | 0.1
2974 | 30/07/2025 10:39:26.388 | 97.68 | 82 | 100 | 71 | 52 | 31.654 | 9.304 | 7.059 | 134.666 | 29.989 | 28.386 | 28.399 | 602.052 | 26.148 | 27.116 | 1291.516 | 27.238 | 27.463 | 36.555 | 29.001 | 4 | 1.8 | 1.3 | 0.2 | 0.1
2975 | 30/07/2025 10:39:28.025 | 98.352 | 84 | 100 | 71 | 52 | 29.078 | 9.508 | 7.062 | 134.542 | 30.02 | 28.388 | 28.411 | 601.913 | 26.16 | 27.114 | 1290.3 | 27.216 | 27.439 | 36.529 | 29.001 | 2.6 | 1.8 | 0.6 | 0.5 | 0.1
2976 | 30/07/2025 10:39:29.659 | 98.04 | 82 | 100 | 69 | 52 | 31.485 | 9.435 | 7.073 | 134.444 | 30.006 | 28.402 | 28.406 | 601.887 | 26.147 | 27.125 | 1286.474 | 27.227 | 27.439 | 36.413 | 33.001 | 2.8 | 3 | 1.3 | 0.6 | 0.1
2977 | 30/07/2025 10:39:31.298 | 97.992 | 82 | 99 | 70 | 52 | 30.319 | 9.148 | 7.072 | 134.978 | 30.03 | 28.398 | 28.41 | 602.006 | 26.172 | 27.122 | 1277.089 | 27.175 | 27.445 | 36.87 | 27.001 | 2.3 | 3 | 0.6 | 0.5 | 0
2978 | 30/07/2025 10:39:32.932 | 97.776 | 82 | 100 | 71 | 52 | 27.471 | 9.284 | 7.069 | 134.633 | 30.011 | 28.406 | 28.403 | 602.023 | 26.154 | 27.104 | 1276.798 | 27.201 | 27.464 | 36.606 | 26.001 | 3.7 | 1.7 | 0.6 | 0.5 | 0.1
2979 | 30/07/2025 10:39:34.568 | 98.304 | 83 | 100 | 70 | 52 | 30.787 | 9.189 | 7.072 | 134.615 | 30.014 | 28.377 | 28.414 | 601.784 | 26.143 | 27.127 | 1276.951 | 27.216 | 27.445 | 36.784 | 28.001 | 3.7 | 1.7 | 0.6 | 0 | 0.1
2980 | 30/07/2025 10:39:36.202 | 97.992 | 81 | 100 | 70 | 52 | 31.626 | 9.284 | 7.059 | 134.359 | 30.016 | 28.394 | 28.442 | 602.168 | 26.144 | 27.101 | 1267.136 | 27.209 | 27.425 | 36.381 | 28.001 | 3.7 | 1.7 | 0.6 | 0 | 0.1
2981 | 30/07/2025 10:39:37.839 | 98.376 | 82 | 100 | 70 | 53 | 29.753 | 9.289 | 7.063 | 134.269 | 30.023 | 28.406 | 28.426 | 601.959 | 26.15 | 27.109 | 1267.16 | 27.207 | 27.434 | 36.357 | 28.001 | 2.6 | 2.2 | 1.2 | 0.5 | 0.1
2982 | 30/07/2025 10:39:39.474 | 98.496 | 82 | 100 | 71 | 52 | 31.68 | 9.205 | 7.068 | 134.764 | 30.014 | 28.402 | 28.432 | 600.586 | 26.143 | 27.093 | 1267.541 | 27.171 | 27.453 | 36.798 | 26.001 | 3.1 | 2.2 | 0.7 | 0.2 | 0.1
2983 | 30/07/2025 10:39:41.107 | 99.216 | 83 | 100 | 70 | 52 | 29.836 | 9.172 | 7.071 | 134.53 | 30.001 | 28.395 | 28.398 | 601.754 | 26.125 | 27.094 | 1269.084 | 27.23 | 27.451 | 36.677 | 27.001 | 3.5 | 2.8 | 0.1 | 0 | 0.1
2984 | 30/07/2025 10:39:42.741 | 98.568 | 84 | 100 | 70 | 54 | 27.706 | 9.15 | 7.122 | 134.634 | 30.024 | 28.378 | 28.415 | 601.98 | 26.158 | 27.088 | 1275.014 | 27.201 | 27.444 | 36.597 | 26.001 | 3.6 | 2.8 | 0.6 | 0 | 0.2
2985 | 30/07/2025 10:39:44.376 | 99 | 82 | 100 | 70 | 52 | 31.19 | 9.133 | 7.122 | 134.527 | 29.997 | 28.417 | 28.424 | 602.031 | 26.145 | 27.08 | 1267.063 | 27.21 | 27.444 | 36.384 | 26.001 | 3.6 | 2.8 | 0.6 | 0 | 0.2
2986 | 30/07/2025 10:39:46.011 | 99.192 | 83 | 100 | 71 | 53 | 31.571 | 9.284 | 7.124 | 134.74 | 30.006 | 28.4 | 28.407 | 601.847 | 26.149 | 27.126 | 1270.746 | 27.19 | 27.459 | 36.606 | 29.001 | 1.9 | 2.8 | 0.6 | 0 | 0.1
2987 | 30/07/2025 10:39:47.647 | 99.576 | 83 | 100 | 70 | 52 | 30.5 | 9.19 | 7.124 | 134.749 | 30.007 | 28.404 | 28.424 | 601.903 | 26.159 | 27.097 | 1265.871 | 27.192 | 27.456 | 36.657 | 28.001 | 1.9 | 2.8 | 0.7 | 0.5 | 0.2
2988 | 30/07/2025 10:39:49.283 | 99.504 | 82 | 100 | 70 | 52 | 31.699 | 9.131 | 7.135 | 134.428 | 30.015 | 28.387 | 28.408 | 601.879 | 26.175 | 27.124 | 1269.239 | 27.216 | 27.445 | 36.639 | 32.001 | 3.9 | 2.2 | 0.7 | 0.1 | 0.2
2989 | 30/07/2025 10:39:50.915 | 99.72 | 82 | 100 | 70 | 52 | 29.08 | 9.135 | 7.133 | 134.35 | 30.015 | 28.386 | 28.441 | 602.129 | 26.16 | 27.099 | 1279.704 | 27.202 | 27.431 | 36.505 | 31.001 | 1.7 | 2.2 | 0.6 | 0.8 | 0.2
2990 | 30/07/2025 10:39:52.549 | 99.408 | 81 | 100 | 71 | 51 | 28.138 | 9.151 | 7.089 | 134.34 | 29.972 | 28.42 | 28.431 | 602.008 | 26.148 | 27.116 | 1284.822 | 27.225 | 27.433 | 36.475 | 30.001 | 2.5 | 2.1 | 0.9 | 0.1 | 0.2
2991 | 30/07/2025 10:39:54.187 | 99.72 | 82 | 100 | 69 | 52 | 30.254 | 9.127 | 7.07 | 134.58 | 30.001 | 28.408 | 28.436 | 602.012 | 26.163 | 27.113 | 1287.18 | 27.192 | 27.452 | 36.555 | 30.001 | 2.5 | 2.1 | 0.9 | 0.1 | 0.2
2992 | 30/07/2025 10:39:55.825 | 99.696 | 83 | 100 | 72 | 52 | 27.477 | 9.212 | 7.072 | 134.454 | 29.977 | 28.399 | 28.401 | 601.814 | 26.15 | 27.142 | 1285.216 | 27.193 | 27.464 | 36.719 | 25.001 | 3.6 | 2.1 | 1.4 | 0 | 0.2
2993 | 30/07/2025 10:39:57.461 | 99.504 | 83 | 100 | 70 | 52 | 30.679 | 9.237 | 7.086 | 134.747 | 29.997 | 28.384 | 28.422 | 601.773 | 26.165 | 27.115 | 1280.221 | 27.215 | 27.445 | 36.905 | 28.001 | 3.5 | 2.9 | 1 | 0 | 0.2
2994 | 30/07/2025 10:39:59.095 | 99.288 | 83 | 100 | 70 | 52 | 31.658 | 9.136 | 7.086 | 134.516 | 29.979 | 28.401 | 28.427 | 602.057 | 26.153 | 27.115 | 1276.78 | 27.218 | 27.448 | 36.504 | 31.001 | 2.8 | 2.9 | 0.9 | 0.5 | 0.1
2995 | 30/07/2025 10:40:00.732 | 98.448 | 81 | 100 | 70 | 51 | 28.475 | 9.141 | 7.098 | 134.742 | 30.009 | 28.404 | 28.423 | 601.871 | 26.162 | 27.123 | 1267.176 | 27.201 | 27.454 | 37.194 | 26.001 | 2 | 2.3 | 0.8 | 0.6 | 0.2
2996 | 30/07/2025 10:40:02.367 | 98.4 | 82 | 100 | 70 | 52 | 28.587 | 9.285 | 7.122 | 134.766 | 29.998 | 28.402 | 28.419 | 602.031 | 26.159 | 27.116 | 1270.981 | 27.169 | 27.451 | 36.734 | 26.001 | 2 | 2.3 | 0.8 | 0.6 | 0.2
2997 | 30/07/2025 10:40:04.003 | 98.64 | 82 | 100 | 71 | 53 | 29.586 | 9.409 | 7.123 | 134.715 | 30.022 | 28.399 | 28.395 | 601.851 | 26.159 | 27.111 | 1277.099 | 27.192 | 27.446 | 36.666 | 27.001 | 1.6 | 2.3 | 1.2 | 0.5 | 0.2
2998 | 30/07/2025 10:40:05.644 | 99.144 | 82 | 99 | 71 | 52 | 27.769 | 9.411 | 7.122 | 134.612 | 30.029 | 28.383 | 28.436 | 602.039 | 26.159 | 27.103 | 1276.738 | 27.212 | 27.451 | 36.324 | 26.001 | 3.6 | 1.6 | 1.2 | 0.5 | 0.1
2999 | 30/07/2025 10:40:07.279 | 98.784 | 84 | 100 | 71 | 52 | 31.152 | 9.29 | 7.136 | 134.357 | 30.009 | 28.406 | 28.411 | 602.155 | 26.153 | 27.125 | 1284.825 | 27.224 | 27.437 | 36.51 | 29.001 | 4.8 | 1.6 | 0 | 0.8 | 0.3
3000 | 30/07/2025 10:40:08.916 | 98.568 | 81 | 100 | 70 | 52 | 31.478 | 9.404 | 7.134 | 134.887 | 30.02 | 28.398 | 28.423 | 601.94 | 26.168 | 27.102 | 1290.04 | 27.183 | 27.45 | 36.844 | 29.001 | 3 | 4.5 | 0.6 | 1.2 | 0.3
3001 | 30/07/2025 10:40:10.550 | 99 | 83 | 100 | 70 | 52 | 27.915 | 9.295 | 7.136 | 134.626 | 30.008 | 28.396 | 28.421 | 602.078 | 26.138 | 27.097 | 1277.673 | 27.196 | 27.466 | 37.012 | 24.001 | 3 | 4.5 | 0.6 | 1.2 | 0.3
3002 | 30/07/2025 10:40:12.185 | 99.192 | 82 | 100 | 71 | 53 | 31.694 | 9.283 | 7.134 | 134.595 | 30.022 | 28.398 | 28.403 | 601.829 | 26.15 | 27.09 | 1277.075 | 27.196 | 27.453 | 36.593 | 24.001 | 3 | 4.5 | 0.6 | 1.2 | 0.3
3003 | 30/07/2025 10:40:13.821 | 99.816 | 84 | 100 | 70 | 52 | 29.167 | 9.295 | 7.135 | 134.49 | 30 | 28.387 | 28.438 | 602.07 | 26.142 | 27.095 | 1277.104 | 27.221 | 27.459 | 36.709 | 27.001 | 3.1 | 3.1 | 0.9 | 1.1 | 0.3
3004 | 30/07/2025 10:40:15.454 | 99.792 | 84 | 100 | 70 | 52 | 28.109 | 9.212 | 7.153 | 134.454 | 30.023 | 28.406 | 28.423 | 602 | 26.152 | 27.093 | 1283.537 | 27.206 | 27.437 | 36.51 | 23.001 | 3.1 | 3.1 | 0.6 | 1.8 | 0.3
3005 | 30/07/2025 10:40:17.091 | 100.08 | 84 | 100 | 71 | 53 | 31.352 | 9.146 | 7.152 | 134.85 | 30.017 | 28.403 | 28.433 | 602.055 | 26.143 | 27.075 | 1297.157 | 27.17 | 27.464 | 36.812 | 28.001 | 2.6 | 1.8 | 1.5 | 0.9 | 0.3
3006 | 30/07/2025 10:40:18.727 | 100.392 | 85 | 100 | 71 | 52 | 31.357 | 9.278 | 7.153 | 134.544 | 30.012 | 28.392 | 28.395 | 601.891 | 26.154 | 27.087 | 1296.192 | 27.211 | 27.445 | 38.545 | 26.001 | 3 | 1.8 | 0.3 | 0.1 | 0.2
3007 | 30/07/2025 10:40:20.364 | 99.72 | 84 | 100 | 71 | 52 | 27.706 | 9.277 | 7.168 | 134.766 | 30.033 | 28.384 | 28.432 | 601.885 | 26.16 | 27.099 | 1302.072 | 27.209 | 27.46 | 36.797 | 26.001 | 3 | 1.8 | 0.3 | 0.1 | 0.2
3008 | 30/07/2025 10:40:21.999 | 99.504 | 84 | 100 | 70 | 52 | 31.669 | 9.436 | 7.186 | 134.476 | 29.99 | 28.387 | 28.43 | 601.866 | 26.155 | 27.11 | 1298.182 | 27.219 | 27.444 | 36.491 | 34.001 | 3.1 | 2.1 | 0 | 0.5 | 0.2
3009 | 30/07/2025 10:40:23.635 | 99.6 | 83 | 100 | 69 | 52 | 28.606 | 9.14 | 7.186 | 134.609 | 30.032 | 28.398 | 28.444 | 602.148 | 26.144 | 27.109 | 1304.877 | 27.201 | 27.453 | 38.47 | 28.001 | 2.2 | 2.1 | 1.2 | 0.2 | 0.2
3010 | 30/07/2025 10:40:25.268 | 99 | 83 | 100 | 70 | 53 | 28.699 | 9.165 | 7.187 | 134.666 | 29.997 | 28.412 | 28.4 | 602.071 | 26.162 | 27.122 | 1297.357 | 27.193 | 27.449 | 38.718 | 27.001 | 2.8 | 1 | 1.2 | 0 | 0.2
3011 | 30/07/2025 10:40:26.904 | 98.856 | 80 | 100 | 70 | 53 | 31.525 | 9.295 | 7.189 | 134.706 | 29.994 | 28.387 | 28.409 | 600.403 | 26.17 | 27.122 | 1303.765 | 27.209 | 27.449 | 38.513 | 28.001 | 3.8 | 1 | 1.2 | 0 | 0.2
3012 | 30/07/2025 10:40:28.540 | 97.992 | 82 | 100 | 71 | 52 | 30.829 | 9.503 | 7.169 | 134.625 | 30.003 | 28.385 | 28.427 | 602.002 | 26.17 | 27.126 | 1308.935 | 27.204 | 27.444 | 38.31 | 26.001 | 3.8 | 3.1 | 1.8 | 0.5 | 0.2
3013 | 30/07/2025 10:40:30.174 | 97.656 | 82 | 100 | 70 | 53 | 27.475 | 9.133 | 7.171 | 134.372 | 29.996 | 28.42 | 28.409 | 601.991 | 26.16 | 27.134 | 1313.715 | 27.231 | 27.435 | 38.446 | 26.001 | 3.8 | 3.1 | 1.8 | 0.5 | 0.2
3014 | 30/07/2025 10:40:31.808 | 96.912 | 82 | 100 | 70 | 54 | 31.549 | 9.21 | 7.177 | 134.594 | 29.983 | 28.41 | 28.427 | 602.005 | 26.158 | 27.116 | 1314.794 | 27.194 | 27.47 | 38.371 | 23.001 | 3.5 | 3.1 | 2 | 0.1 | 0.2
3015 | 30/07/2025 10:40:33.442 | 97.512 | 82 | 100 | 70 | 52 | 27.941 | 9.258 | 7.188 | 134.49 | 29.982 | 28.394 | 28.402 | 601.874 | 26.158 | 27.131 | 1311.437 | 27.198 | 27.454 | 38.552 | 25.001 | 3 | 2 | 1.4 | 0 | 0.2
3016 | 30/07/2025 10:40:35.078 | 97.152 | 81 | 100 | 71 | 53 | 29.091 | 9.285 | 7.173 | 134.619 | 30.017 | 28.382 | 28.401 | 601.916 | 26.158 | 27.111 | 1312.896 | 27.209 | 27.44 | 36.583 | 23.001 | 2.8 | 2 | 0.3 | 0.5 | 0.2
3017 | 30/07/2025 10:40:36.716 | 97.008 | 81 | 100 | 70 | 52 | 31.573 | 9.219 | 7.186 | 134.452 | 30.006 | 28.389 | 28.429 | 601.925 | 26.155 | 27.107 | 1304.5 | 27.221 | 27.452 | 36.511 | 29.001 | 3.4 | 2.9 | 0.6 | 0.2 | 0.2
3018 | 30/07/2025 10:40:38.355 | 97.416 | 82 | 100 | 70 | 52 | 30.262 | 9.195 | 7.189 | 134.418 | 30.024 | 28.405 | 28.425 | 602.027 | 26.162 | 27.12 | 1297.07 | 27.197 | 27.435 | 36.464 | 29.001 | 3.4 | 2.9 | 0.6 | 0.2 | 0.2
3019 | 30/07/2025 10:40:39.990 | 97.8 | 81 | 100 | 70 | 52 | 31.36 | 8.973 | 7.205 | 134.699 | 30.002 | 28.409 | 28.409 | 601.887 | 26.153 | 27.115 | 1296.982 | 27.202 | 27.452 | 36.702 | 28.001 | 2.2 | 2.9 | 0 | 0 | 0.2
3020 | 30/07/2025 10:40:41.627 | 97.848 | 81 | 100 | 70 | 52 | 31.186 | 9.211 | 7.207 | 134.68 | 30.026 | 28.399 | 28.388 | 603.18 | 26.159 | 27.121 | 1282.43 | 27.192 | 27.451 | 36.603 | 26.001 | 1.5 | 3.3 | 0.7 | 0 | 0.2
3021 | 30/07/2025 10:40:43.266 | 97.776 | 81 | 100 | 70 | 52 | 27.634 | 9.499 | 7.22 | 134.671 | 30.022 | 28.391 | 28.429 | 603.268 | 26.152 | 27.104 | 1277.326 | 27.219 | 27.444 | 36.675 | 26.001 | 2.2 | 3.3 | 0.7 | 0 | 0.2
3022 | 30/07/2025 10:40:44.903 | 97.824 | 81 | 100 | 71 | 51 | 29.682 | 9.251 | 7.138 | 134.204 | 30.009 | 28.404 | 28.408 | 603.113 | 26.146 | 27.12 | 1277.984 | 27.22 | 27.444 | 36.498 | 28.001 | 2 | 2 | 1.9 | 1.6 | 0.2
3023 | 30/07/2025 10:40:46.540 | 98.088 | 82 | 100 | 71 | 52 | 31.662 | 9.208 | 7.134 | 134.746 | 30.033 | 28.406 | 28.433 | 603.381 | 26.151 | 27.089 | 1287.054 | 27.186 | 27.443 | 36.716 | 25.001 | 2.5 | 2 | 2.1 | 0.3 | 0.2
3024 | 30/07/2025 10:40:48.177 | 97.944 | 82 | 100 | 69 | 52 | 29.797 | 9.426 | 7.153 | 134.701 | 30.013 | 28.407 | 28.411 | 603.272 | 26.14 | 27.096 | 1283.914 | 27.194 | 27.479 | 36.708 | 25.001 | 2.5 | 2 | 2.1 | 0.3 | 0.2
3025 | 30/07/2025 10:40:49.812 | 97.656 | 81 | 100 | 70 | 51 | 31.482 | 9.502 | 7.138 | 134.631 | 30.012 | 28.388 | 28.409 | 603.373 | 26.15 | 27.082 | 1282.446 | 27.208 | 27.451 | 36.56 | 31.001 | 2.5 | 0.7 | 0.5 | 0 | 0.3
3026 | 30/07/2025 10:40:51.449 | 97.992 | 82 | 100 | 70 | 52 | 31.011 | 9.212 | 7.134 | 134.611 | 30.003 | 28.387 | 28.436 | 603.175 | 26.144 | 27.072 | 1277.729 | 27.23 | 27.442 | 36.458 | 33.001 | 3.3 | 0.7 | 0.9 | 0.6 | 0.3
3027 | 30/07/2025 10:40:53.085 | 98.376 | 82 | 100 | 70 | 52 | 27.483 | 9.132 | 7.149 | 134.412 | 30.005 | 28.404 | 28.426 | 601.757 | 26.165 | 27.097 | 1276.961 | 27.207 | 27.427 | 36.473 | 25.001 | 3.9 | 1.9 | 2.2 | 1.5 | 0.3
3028 | 30/07/2025 10:40:54.722 | 98.544 | 82 | 100 | 70 | 52 | 30.418 | 9.282 | 7.143 | 134.658 | 30.008 | 28.41 | 28.412 | 601.896 | 26.143 | 27.079 | 1283.107 | 27.178 | 27.463 | 36.811 | 26.001 | 3.3 | 1.9 | 1.1 | 0.4 | 0.3
3029 | 30/07/2025 10:40:56.366 | 98.376 | 82 | 100 | 70 | 53 | 31.707 | 9.207 | 7.136 | 134.533 | 30.01 | 28.394 | 28.404 | 601.94 | 26.158 | 27.126 | 1267.262 | 27.207 | 27.463 | 36.639 | 26.001 | 3.3 | 1.9 | 1.1 | 0.4 | 0.3
3030 | 30/07/2025 10:40:57.998 | 98.808 | 83 | 100 | 70 | 52 | 29.126 | 9.265 | 7.12 | 134.771 | 30.01 | 28.388 | 28.423 | 601.945 | 26.159 | 27.112 | 1277.008 | 27.213 | 27.428 | 36.741 | 24.001 | 2.3 | 2.1 | 1.5 | 1 | 0.3
3031 | 30/07/2025 10:40:59.634 | 98.856 | 83 | 100 | 70 | 52 | 31.601 | 9.288 | 7.122 | 134.584 | 29.998 | 28.391 | 28.431 | 601.834 | 26.163 | 27.121 | 1275.507 | 27.21 | 27.446 | 36.679 | 22.001 | 3.9 | 2.1 | 1.6 | 0.5 | 0.3
3032 | 30/07/2025 10:41:01.268 | 98.448 | 82 | 100 | 70 | 52 | 30.378 | 9.287 | 7.131 | 134.624 | 30.006 | 28.404 | 28.434 | 602.022 | 26.169 | 27.12 | 1269.758 | 27.205 | 27.442 | 36.47 | 23.001 | 3.7 | 2.6 | 0.9 | 0 | 0.3
3033 | 30/07/2025 10:41:02.905 | 98.232 | 82 | 100 | 71 | 53 | 27.513 | 9.381 | 7.127 | 134.67 | 29.988 | 28.407 | 28.421 | 602.034 | 26.151 | 27.128 | 1274.273 | 27.197 | 27.46 | 36.749 | 27.001 | 2.7 | 2.6 | 1 | 0.6 | 0.3
3034 | 30/07/2025 10:41:04.540 | 98.376 | 83 | 100 | 70 | 52 | 30.755 | 9.283 | 7.088 | 134.595 | 29.992 | 28.384 | 28.41 | 602 | 26.162 | 27.114 | 1277.016 | 27.213 | 27.435 | 36.845 | 24.001 | 3.4 | 2 | 1.8 | 0.3 | 0.3
3035 | 30/07/2025 10:41:06.178 | 98.592 | 82 | 100 | 70 | 52 | 31.711 | 9.435 | 7.086 | 134.707 | 30.002 | 28.388 | 28.435 | 602.002 | 26.151 | 27.108 | 1286.493 | 27.209 | 27.445 | 36.707 | 24.001 | 3.4 | 2 | 1.8 | 0.3 | 0.3
3036 | 30/07/2025 10:41:07.811 | 98.496 | 82 | 100 | 70 | 53 | 29.705 | 9.29 | 7.086 | 134.459 | 29.998 | 28.401 | 28.425 | 602.005 | 26.172 | 27.115 | 1285.336 | 27.201 | 27.437 | 36.5 | 30.001 | 1.8 | 2 | 1 | 1.1 | 0.3
3037 | 30/07/2025 10:41:09.446 | 98.136 | 82 | 100 | 70 | 52 | 31.678 | 9.4 | 7.072 | 134.649 | 29.991 | 28.412 | 28.427 | 602.011 | 26.158 | 27.115 | 1287.619 | 27.207 | 27.46 | 36.558 | 27.001 | 2.4 | 1.5 | 0.9 | 0.1 | 0.3
3038 | 30/07/2025 10:41:11.079 | 97.776 | 81 | 100 | 70 | 52 | 29.754 | 8.989 | 7.071 | 134.586 | 30.015 | 28.396 | 28.391 | 601.883 | 26.151 | 27.114 | 1287.203 | 27.183 | 27.444 | 38.664 | 28.001 | 2.1 | 1.5 | 1.3 | 0.8 | 0.3
3039 | 30/07/2025 10:41:12.714 | 97.92 | 81 | 100 | 69 | 52 | 27.695 | 9.418 | 7.058 | 134.525 | 30.024 | 28.386 | 28.417 | 603.196 | 26.153 | 27.093 | 1287.407 | 27.202 | 27.444 | 36.688 | 26.001 | 1.1 | 1.8 | 1.6 | 0.4 | 0.3
3040 | 30/07/2025 10:41:14.349 | 98.136 | 82 | 100 | 70 | 52 | 31.128 | 9.505 | 7.07 | 134.522 | 30.015 | 28.399 | 28.438 | 603.271 | 26.152 | 27.112 | 1293.064 | 27.229 | 27.448 | 37.589 | 26.001 | 1.1 | 1.8 | 1.6 | 0.4 | 0.3
3041 | 30/07/2025 10:41:15.984 | 98.328 | 82 | 100 | 71 | 52 | 27.481 | 9.439 | 7.069 | 134.54 | 30.022 | 28.405 | 28.453 | 603.305 | 26.15 | 27.102 | 1298.782 | 27.207 | 27.425 | 36.369 | 25.001 | 2.3 | 1.8 | 2 | 0 | 0.3
3042 | 30/07/2025 10:41:17.619 | 98.112 | 81 | 100 | 71 | 52 | 30.237 | 9.195 | 7.071 | 134.583 | 30.028 | 28.405 | 28.429 | 603.162 | 26.142 | 27.117 | 1305.103 | 27.209 | 27.453 | 36.677 | 26.001 | 2.7 | 1.6 | 0.7 | 0.9 | 0.3
3043 | 30/07/2025 10:41:19.258 | 98.088 | 83 | 100 | 70 | 52 | 31.699 | 9.287 | 7.071 | 134.686 | 30.013 | 28.393 | 28.406 | 603.209 | 26.167 | 27.116 | 1299.926 | 27.179 | 27.454 | 36.79 | 25.001 | 4 | 1.6 | 1.5 | 0.5 | 0.3
3044 | 30/07/2025 10:41:20.891 | 98.376 | 81 | 100 | 70 | 52 | 29.087 | 9.449 | 7.07 | 134.472 | 30.01 | 28.378 | 28.42 | 603.203 | 26.136 | 27.095 | 1293.075 | 27.219 | 27.458 | 36.669 | 29.001 | 1 | 1.9 | 1.1 | 1.1 | 0.3
3045 | 30/07/2025 10:41:22.526 | 98.064 | 83 | 100 | 70 | 52 | 28.058 | 9.221 | 7.072 | 134.337 | 30.014 | 28.394 | 28.428 | 603.09 | 26.145 | 27.096 | 1287.989 | 27.206 | 27.433 | 36.452 | 29.001 | 1.7 | 1.9 | 0.1 | 0.9 | 0.3
3046 | 30/07/2025 10:41:24.161 | 98.208 | 81 | 100 | 70 | 52 | 31.36 | 9.17 | 7.07 | 134.569 | 30.019 | 28.404 | 28.433 | 603.215 | 26.161 | 27.082 | 1294.592 | 27.193 | 27.45 | 36.441 | 29.001 | 1.7 | 1.9 | 0.1 | 0.9 | 0.3
3047 | 30/07/2025 10:41:25.796 | 98.616 | 82 | 100 | 70 | 52 | 27.503 | 9.28 | 7.073 | 134.83 | 30.016 | 28.406 | 28.416 | 601.993 | 26.15 | 27.105 | 1296.779 | 27.18 | 27.456 | 36.752 | 24.001 | 2.4 | 1.6 | 1.2 | 0.6 | 0.3
3048 | 30/07/2025 10:41:27.429 | 97.944 | 81 | 100 | 70 | 52 | 30.866 | 9.286 | 7.07 | 134.466 | 30.005 | 28.4 | 28.401 | 603.252 | 26.16 | 27.075 | 1290.182 | 27.208 | 27.451 | 36.616 | 29.001 | 1.7 | 1.6 | 0.6 | 0.1 | 0.3
3049 | 30/07/2025 10:41:29.065 | 97.344 | 81 | 100 | 70 | 52 | 31.65 | 9.286 | 7.12 | 134.528 | 30.01 | 28.388 | 28.423 | 603.197 | 26.148 | 27.116 | 1278.118 | 27.238 | 27.448 | 36.693 | 31.001 | 2.7 | 2.7 | 1.5 | 0.8 | 0.3
3050 | 30/07/2025 10:41:30.703 | 97.008 | 81 | 100 | 70 | 52 | 28.582 | 9.133 | 7.089 | 134.602 | 30.017 | 28.402 | 28.418 | 601.797 | 26.186 | 27.105 | 1289.104 | 27.208 | 27.423 | 36.582 | 32.001 | 2.6 | 2.7 | 0.6 | 0.6 | 0.3
3051 | 30/07/2025 10:41:32.339 | 97.512 | 80 | 100 | 70 | 52 | 28.727 | 9.284 | 7.088 | 134.832 | 30.007 | 28.405 | 28.429 | 602.081 | 26.162 | 27.109 | 1301.118 | 27.191 | 27.462 | 36.911 | 32.001 | 2.6 | 2.7 | 0.6 | 0.6 | 0.3
3052 | 30/07/2025 10:41:33.976 | 97.416 | 80 | 100 | 71 | 52 | 29.811 | 9.159 | 7.086 | 134.756 | 30.01 | 28.399 | 28.414 | 601.983 | 26.159 | 27.111 | 1301.726 | 27.167 | 27.458 | 36.749 | 27.001 | 2 | 1.6 | 1 | 1.3 | 0.3
3053 | 30/07/2025 10:41:35.612 | 97.896 | 82 | 100 | 70 | 52 | 27.718 | 9.435 | 7.086 | 134.519 | 29.982 | 28.392 | 28.404 | 601.948 | 26.149 | 27.12 | 1309.022 | 27.214 | 27.461 | 36.574 | 23.001 | 3 | 1.6 | 1.3 | 0.6 | 0.2
3054 | 30/07/2025 10:41:37.249 | 98.328 | 81 | 100 | 70 | 52 | 31.161 | 9.252 | 7.123 | 134.586 | 29.984 | 28.39 | 28.428 | 601.979 | 26.152 | 27.128 | 1309.913 | 27.204 | 27.443 | 36.602 | 23.001 | 1.9 | 1 | 1 | 0 | 0.2
3055 | 30/07/2025 10:41:38.883 | 98.76 | 82 | 100 | 70 | 52 | 31.556 | 9.226 | 7.123 | 134.51 | 30.006 | 28.406 | 28.435 | 602.063 | 26.165 | 27.11 | 1316.768 | 27.202 | 27.446 | 36.409 | 27.001 | 1.5 | 1 | 1.2 | 0 | 0.2
3056 | 30/07/2025 10:41:40.518 | 98.376 | 81 | 100 | 71 | 53 | 28.135 | 9.132 | 7.123 | 134.672 | 30.003 | 28.419 | 28.416 | 601.926 | 26.157 | 27.136 | 1316.917 | 27.19 | 27.459 | 36.653 | 30.001 | 1.7 | 1.3 | 1.5 | 0 | 0.3
3057 | 30/07/2025 10:41:42.152 | 98.016 | 81 | 100 | 71 | 52 | 29.198 | 9.285 | 7.123 | 134.696 | 30.016 | 28.39 | 28.404 | 601.875 | 26.176 | 27.118 | 1329.113 | 27.214 | 27.45 | 36.767 | 30.001 | 1.7 | 1.3 | 1.5 | 0 | 0.3
3058 | 30/07/2025 10:41:43.790 | 97.824 | 82 | 100 | 70 | 51 | 29.17 | 9.217 | 7.121 | 134.679 | 30.008 | 28.377 | 28.402 | 601.75 | 26.149 | 27.123 | 1327.315 | 27.219 | 27.458 | 36.786 | 23.001 | 2.4 | 1.3 | 0.9 | 0.5 | 0.3
3059 | 30/07/2025 10:41:45.425 | 97.512 | 80 | 100 | 70 | 52 | 28.153 | 9.211 | 7.122 | 134.681 | 30.044 | 28.397 | 28.428 | 601.804 | 26.166 | 27.107 | 1330.914 | 27.204 | 27.439 | 36.496 | 24.001 | 3.9 | 3 | 1.9 | 0.2 | 0.3
3060 | 30/07/2025 10:41:47.060 | 97.872 | 82 | 100 | 70 | 52 | 31.39 | 8.995 | 7.123 | 134.755 | 30.016 | 28.419 | 28.431 | 601.91 | 26.149 | 27.108 | 1326.949 | 27.211 | 27.461 | 36.551 | 34.001 | 1.7 | 3 | 1.1 | 0 | 0.3
3061 | 30/07/2025 10:41:48.702 | 97.944 | 80 | 100 | 70 | 52 | 31.252 | 9.208 | 7.125 | 134.657 | 30.014 | 28.395 | 28.417 | 601.723 | 26.151 | 27.125 | 1312.457 | 27.18 | 27.461 | 36.669 | 24.001 | 2.5 | 3.3 | 0.2 | 1 | 0.3
3062 | 30/07/2025 10:41:50.338 | 98.04 | 82 | 100 | 72 | 51 | 27.647 | 9.216 | 7.089 | 134.622 | 30.015 | 28.382 | 28.396 | 603.307 | 26.134 | 27.104 | 1316.985 | 27.204 | 27.448 | 36.547 | 24.001 | 2.5 | 3.3 | 0.2 | 1 | 0.3
3063 | 30/07/2025 10:41:51.976 | 97.992 | 81 | 100 | 70 | 52 | 31.656 | 8.932 | 7.086 | 134.777 | 30.023 | 28.378 | 28.414 | 603.269 | 26.15 | 27.117 | 1317.136 | 27.208 | 27.447 | 36.747 | 28.001 | 3.1 | 3.3 | 0.6 | 0.5 | 0.3
3064 | 30/07/2025 10:41:53.612 | 98.184 | 81 | 100 | 70 | 52 | 28.567 | 9.217 | 7.086 | 134.598 | 30.02 | 28.41 | 28.427 | 602.184 | 26.144 | 27.1 | 1315.684 | 27.204 | 27.422 | 36.487 | 31.001 | 3.7 | 2.5 | 2 | 0 | 0.2
3065 | 30/07/2025 10:41:55.248 | 98.136 | 81 | 100 | 70 | 52 | 28.504 | 9.207 | 7.088 | 134.612 | 29.999 | 28.401 | 28.404 | 601.931 | 26.15 | 27.125 | 1323.869 | 27.204 | 27.46 | 36.688 | 27.001 | 4.2 | 2.5 | 1.1 | 0.8 | 0.2
3066 | 30/07/2025 10:41:56.885 | 98.688 | 83 | 100 | 70 | 52 | 31.542 | 9.284 | 7.087 | 134.822 | 30.028 | 28.407 | 28.41 | 603.013 | 26.147 | 27.094 | 1320.941 | 27.185 | 27.452 | 37.931 | 27.001 | 3.1 | 2.3 | 1.2 | 0.9 | 0.2
3067 | 30/07/2025 10:41:58.519 | 98.544 | 81 | 100 | 71 | 53 | 30.905 | 9.002 | 7.085 | 134.523 | 29.999 | 28.379 | 28.422 | 603.245 | 26.144 | 27.074 | 1304.951 | 27.22 | 27.455 | 36.636 | 25.001 | 3.4 | 2.3 | 0.1 | 0.1 | 0.1
3068 | 30/07/2025 10:42:00.153 | 99 | 83 | 100 | 71 | 52 | 27.515 | 9.216 | 7.073 | 134.433 | 30.014 | 28.4 | 28.423 | 603.125 | 26.16 | 27.093 | 1306.847 | 27.211 | 27.424 | 36.65 | 25.001 | 3.4 | 2.3 | 0.1 | 0.1 | 0.1
3069 | 30/07/2025 10:42:01.789 | 98.592 | 84 | 100 | 71 | 52 | 31.661 | 9.212 | 7.07 | 134.433 | 29.999 | 28.422 | 28.418 | 603.332 | 26.149 | 27.085 | 1307.404 | 27.218 | 27.431 | 36.487 | 26.001 | 1.8 | 2.6 | 0.6 | 1 | 0.1
3070 | 30/07/2025 10:42:03.425 | 98.736 | 81 | 100 | 70 | 52 | 27.985 | 8.982 | 7.07 | 134.686 | 30.01 | 28.401 | 28.417 | 603.034 | 26.16 | 27.121 | 1307.105 | 27.175 | 27.469 | 36.825 | 25.001 | 2 | 2.6 | 0.6 | 0.5 | 0.2
3071 | 30/07/2025 10:42:05.060 | 98.76 | 83 | 100 | 70 | 52 | 29.238 | 9.134 | 7.069 | 134.703 | 30.004 | 28.397 | 28.412 | 603.253 | 26.167 | 27.114 | 1306.802 | 27.197 | 27.457 | 36.574 | 27.001 | 2.7 | 2.5 | 0.3 | 0.6 | 0.1
3072 | 30/07/2025 10:42:06.697 | 98.256 | 80 | 100 | 70 | 52 | 31.588 | 9.296 | 7.069 | 134.6 | 29.993 | 28.368 | 28.416 | 603.232 | 26.154 | 27.14 | 1317.041 | 27.232 | 27.453 | 36.723 | 28.001 | 2.5 | 2.5 | 1.2 | 1.1 | 0.1
3073 | 30/07/2025 10:42:08.332 | 97.992 | 80 | 100 | 70 | 53 | 30.461 | 9.212 | 7.069 | 134.565 | 30.003 | 28.409 | 28.424 | 603.197 | 26.172 | 27.124 | 1320.663 | 27.204 | 27.423 | 36.456 | 28.001 | 2.5 | 2.5 | 1.2 | 1.1 | 0.1
3074 | 30/07/2025 10:42:09.966 | 97.56 | 80 | 100 | 71 | 52 | 31.375 | 9.135 | 7.072 | 134.371 | 29.977 | 28.401 | 28.414 | 603.085 | 26.156 | 27.13 | 1319.493 | 27.209 | 27.445 | 36.618 | 28.001 | 4.3 | 2.4 | 0.9 | 0.7 | 0.2
3075 | 30/07/2025 10:42:11.601 | 97.872 | 81 | 100 | 71 | 52 | 31.371 | 9.375 | 7.071 | 134.683 | 30.003 | 28.401 | 28.557 | 603.242 | 26.17 | 27.115 | 1314.859 | 27.168 | 27.464 | 36.566 | 24.001 | 2.3 | 2.4 | 1.1 | 0.3 | 0.2
3076 | 30/07/2025 10:42:13.237 | 97.68 | 80 | 100 | 70 | 53 | 27.757 | 9.238 | 7.069 | 134.611 | 29.978 | 28.399 | 28.54 | 603.26 | 26.155 | 27.125 | 1305.374 | 27.221 | 27.461 | 36.51 | 23.001 | 2.7 | 1 | 1.1 | 0.5 | 0.2
3077 | 30/07/2025 10:42:14.873 | 97.608 | 81 | 100 | 70 | 52 | 29.822 | 9.284 | 7.085 | 134.407 | 29.994 | 28.378 | 28.432 | 603.149 | 26.16 | 27.118 | 1295.251 | 27.22 | 27.438 | 36.593 | 30.001 | 2 | 1 | 0.7 | 0.5 | 0.2
3078 | 30/07/2025 10:42:16.508 | 97.776 | 82 | 100 | 70 | 52 | 31.693 | 9.434 | 7.088 | 134.569 | 30.006 | 28.404 | 28.567 | 603.322 | 26.16 | 27.106 | 1297.259 | 27.203 | 27.444 | 36.381 | 34.001 | 2.5 | 2.4 | 0.3 | 0.5 | 0.2
3079 | 30/07/2025 10:42:18.144 | 97.512 | 81 | 100 | 70 | 52 | 28.643 | 9.327 | 7.122 | 134.831 | 30.011 | 28.397 | 28.443 | 603.293 | 26.169 | 27.118 | 1296.955 | 27.196 | 27.444 | 36.558 | 34.001 | 2.5 | 2.4 | 0.3 | 0.5 | 0.2
3080 | 30/07/2025 10:42:19.778 | 97.392 | 82 | 100 | 70 | 52 | 31.583 | 9.434 | 7.099 | 134.772 | 30.024 | 28.404 | 28.55 | 603.252 | 26.153 | 27.111 | 1308.186 | 27.181 | 27.457 | 36.637 | 34.001 | 3.9 | 2.4 | 0 | 0.1 | 0.2
3081 | 30/07/2025 10:42:21.415 | 97.464 | 79 | 100 | 70 | 52 | 30.955 | 9.431 | 7.088 | 134.473 | 30.011 | 28.378 | 28.542 | 603.117 | 26.14 | 27.129 | 1311.466 | 27.219 | 27.449 | 38.442 | 29.001 | 3.4 | 2.8 | 0.6 | 0.8 | 0.2
3082 | 30/07/2025 10:42:23.053 | 96.84 | 80 | 100 | 70 | 52 | 27.493 | 9.215 | 7.121 | 134.492 | 30.035 | 28.401 | 28.583 | 603.119 | 26.152 | 27.107 | 1317.022 | 27.202 | 27.444 | 38.366 | 24.001 | 1.5 | 2.8 | 0.6 | 0.5 | 0.3
3083 | 30/07/2025 10:42:24.687 | 97.272 | 81 | 100 | 71 | 52 | 30.253 | 9.174 | 7.122 | 134.442 | 30.004 | 28.413 | 28.57 | 603.191 | 26.156 | 27.112 | 1317.157 | 27.223 | 27.45 | 38.333 | 24.001 | 3.2 | 3.1 | 0.6 | 0.8 | 0.3
3084 | 30/07/2025 10:42:26.323 | 97.176 | 79 | 100 | 71 | 52 | 31.751 | 9.205 | 7.123 | 134.674 | 30.027 | 28.396 | 28.553 | 603.082 | 26.152 | 27.108 | 1316.989 | 27.179 | 27.451 | 38.463 | 24.001 | 3.2 | 3.1 | 0.6 | 0.8 | 0.3
3085 | 30/07/2025 10:42:27.961 | 96.888 | 80 | 100 | 70 | 52 | 29.953 | 9.138 | 7.123 | 134.571 | 30.014 | 28.4 | 28.539 | 603.16 | 26.144 | 27.094 | 1319.099 | 27.199 | 27.456 | 38.524 | 24.001 | 2.6 | 3.1 | 0.7 | 0.5 | 0.3
3086 | 30/07/2025 10:42:29.596 | 96.816 | 80 | 100 | 70 | 52 | 31.619 | 9.427 | 7.122 | 134.671 | 30.021 | 28.38 | 28.554 | 603.228 | 26.143 | 27.118 | 1325.195 | 27.22 | 27.448 | 38.25 | 29.001 | 1.8 | 2.4 | 1.1 | 0.8 | 0.3
3087 | 30/07/2025 10:42:31.231 | 97.248 | 79 | 100 | 70 | 52 | 30.396 | 9.291 | 7.133 | 134.445 | 29.999 | 28.407 | 28.562 | 603.15 | 26.127 | 27.085 | 1317.359 | 27.211 | 27.438 | 36.36 | 27.001 | 1.7 | 2.4 | 0.7 | 0.1 | 0.3
3088 | 30/07/2025 10:42:32.867 | 97.848 | 83 | 100 | 71 | 52 | 27.551 | 9.131 | 7.136 | 134.564 | 29.997 | 28.404 | 28.561 | 603.115 | 26.15 | 27.083 | 1307.266 | 27.192 | 27.451 | 36.558 | 23.001 | 0.7 | 2.7 | 0.6 | 0 | 0.2
3089 | 30/07/2025 10:42:34.502 | 97.344 | 81 | 100 | 70 | 52 | 30.857 | 9.125 | 7.136 | 134.78 | 30.023 | 28.396 | 28.576 | 603.307 | 26.168 | 27.099 | 1299.362 | 27.182 | 27.456 | 36.641 | 23.001 | 2.9 | 2.7 | 1.9 | 0 | 0.2
3090 | 30/07/2025 10:42:36.135 | 97.632 | 82 | 100 | 70 | 52 | 27.689 | 9.361 | 7.136 | 134.592 | 30 | 28.389 | 28.531 | 603.035 | 26.154 | 27.103 | 1301.313 | 27.206 | 27.451 | 36.835 | 23.001 | 2.9 | 2.7 | 1.9 | 0 | 0.2
3091 | 30/07/2025 10:42:37.769 | 97.776 | 82 | 100 | 70 | 52 | 29.793 | 9.295 | 7.133 | 134.613 | 30 | 28.386 | 28.593 | 603.371 | 26.162 | 27.095 | 1306.832 | 27.21 | 27.442 | 36.597 | 27.001 | 2.7 | 2.5 | 2.1 | 0.6 | 0.2
3092 | 30/07/2025 10:42:39.406 | 97.992 | 81 | 100 | 70 | 52 | 31.733 | 9.13 | 7.136 | 134.557 | 30.126 | 28.423 | 28.557 | 603.206 | 26.155 | 27.121 | 1312.264 | 27.232 | 27.429 | 36.284 | 26.001 | 4.4 | 2.5 | 1.4 | 0.6 | 0.2
3093 | 30/07/2025 10:42:41.043 | 97.536 | 81 | 100 | 70 | 52 | 29.828 | 9.133 | 7.136 | 134.785 | 30.143 | 28.399 | 28.561 | 603.171 | 26.177 | 27.133 | 1314.423 | 27.183 | 27.457 | 36.813 | 26.001 | 2.7 | 1.3 | 0.9 | 0.1 | 0.1
3094 | 30/07/2025 10:42:42.678 | 97.176 | 82 | 100 | 70 | 52 | 27.709 | 9.199 | 7.135 | 134.707 | 30.162 | 28.398 | 28.539 | 603.215 | 26.169 | 27.118 | 1306.467 | 27.196 | 27.464 | 36.746 | 25.001 | 2.7 | 1.3 | 0.8 | 1.1 | 0.2
3095 | 30/07/2025 10:42:44.311 | 96.6 | 81 | 100 | 71 | 53 | 31.156 | 9.286 | 7.15 | 134.677 | 30.122 | 28.372 | 28.568 | 601.888 | 26.152 | 27.129 | 1304.175 | 27.207 | 27.449 | 36.559 | 25.001 | 2.7 | 1.3 | 0.8 | 1.1 | 0.2
3096 | 30/07/2025 10:42:45.949 | 96.216 | 79 | 100 | 70 | 52 | 27.539 | 9.304 | 7.151 | 134.74 | 30.136 | 28.382 | 28.571 | 602.04 | 26.166 | 27.123 | 1306.758 | 27.224 | 27.454 | 36.498 | 25.001 | 2.2 | 2.6 | 0.6 | 0.8 | 0.2
3097 | 30/07/2025 10:42:47.585 | 96.072 | 80 | 100 | 70 | 52 | 30.278 | 9.26 | 7.156 | 134.539 | 30.132 | 28.406 | 28.56 | 601.843 | 26.159 | 27.131 | 1306.881 | 27.201 | 27.449 | 36.376 | 31.001 | 3.6 | 2.6 | 2 | 0.5 | 0.2
3098 | 30/07/2025 10:42:49.220 | 95.496 | 77 | 100 | 70 | 52 | 31.707 | 9.129 | 7.151 | 134.759 | 30.145 | 28.403 | 28.566 | 602.044 | 26.153 | 27.104 | 1298.527 | 27.171 | 27.467 | 36.733 | 25.001 | 2.7 | 1.7 | 2.2 | 0.5 | 0.2
3099 | 30/07/2025 10:42:50.855 | 95.688 | 78 | 100 | 70 | 52 | 29.318 | 9.29 | 7.152 | 134.732 | 30.147 | 28.402 | 28.528 | 602.041 | 26.166 | 27.122 | 1288.053 | 27.227 | 27.453 | 36.709 | 26.001 | 2.2 | 1.7 | 0.4 | 0.2 | 0.2
3100 | 30/07/2025 10:42:52.493 | 95.568 | 79 | 100 | 70 | 52 | 28.213 | 9.291 | 7.136 | 134.616 | 30.173 | 28.381 | 28.571 | 602.134 | 26.168 | 27.126 | 1287.152 | 27.205 | 27.437 | 37.587 | 24.001 | 2.2 | 2.5 | 1.7 | 0.5 | 0.2
3101 | 30/07/2025 10:42:54.129 | 96 | 80 | 100 | 69 | 52 | 30.426 | 9.34 | 7.135 | 134.291 | 30.163 | 28.399 | 28.553 | 603.239 | 26.155 | 27.117 | 1289.684 | 27.225 | 27.432 | 38.346 | 24.001 | 2.2 | 2.5 | 1.7 | 0.5 | 0.2
3102 | 30/07/2025 10:42:55.766 | 95.256 | 78 | 100 | 71 | 53 | 27.557 | 9.028 | 7.147 | 134.768 | 30.178 | 28.401 | 28.569 | 602.254 | 26.177 | 27.116 | 1285.378 | 27.203 | 27.435 | 38.371 | 28.001 | 2.7 | 2.5 | 1.9 | 0.5 | 0.2
3103 | 30/07/2025 10:42:57.401 | 95.496 | 78 | 100 | 70 | 52 | 30.845 | 8.911 | 7.151 | 134.767 | 30.164 | 28.404 | 28.561 | 603.195 | 26.148 | 27.105 | 1277.091 | 27.193 | 27.46 | 36.647 | 28.001 | 3 | 2.3 | 1.5 | 0.2 | 0.1
3104 | 30/07/2025 10:42:59.033 | 95.568 | 79 | 100 | 70 | 52 | 31.763 | 9.041 | 7.152 | 134.671 | 30.152 | 28.369 | 28.532 | 603.08 | 26.138 | 27.11 | 1268.14 | 27.218 | 27.45 | 36.668 | 23.001 | 2 | 2.3 | 0.6 | 1.1 | 0.1
3105 | 30/07/2025 10:43:00.667 | 95.568 | 80 | 100 | 70 | 52 | 28.654 | 9.226 | 7.133 | 134.49 | 30.169 | 28.395 | 28.588 | 603.138 | 26.137 | 27.11 | 1273.46 | 27.203 | 27.435 | 37.474 | 24.001 | 4.3 | 2 | 0.9 | 0.5 | 0.2
3106 | 30/07/2025 10:43:02.303 | 95.52 | 77 | 100 | 71 | 52 | 28.67 | 9.289 | 7.135 | 134.489 | 30.15 | 28.42 | 28.577 | 603.243 | 26.146 | 27.099 | 1276.148 | 27.212 | 27.452 | 36.538 | 24.001 | 4.3 | 2 | 0.9 | 0.5 | 0.2
3107 | 30/07/2025 10:43:03.937 | 95.352 | 79 | 100 | 70 | 52 | 29.9 | 9.132 | 7.166 | 134.689 | 30.152 | 28.4 | 28.565 | 603.241 | 26.147 | 27.096 | 1267.343 | 27.193 | 27.45 | 36.613 | 27.001 | 2.7 | 2 | 0.4 | 0.1 | 0.1
3108 | 30/07/2025 10:43:05.575 | 95.52 | 79 | 99 | 70 | 52 | 27.784 | 9.031 | 7.181 | 134.632 | 30.139 | 28.395 | 28.55 | 601.891 | 26.139 | 27.098 | 1259.514 | 27.204 | 27.461 | 36.641 | 30.001 | 4.4 | 2.4 | 0.6 | 0 | 0.2
3109 | 30/07/2025 10:43:07.211 | 95.088 | 79 | 100 | 71 | 53 | 31.181 | 9.272 | 7.169 | 134.92 | 30.173 | 28.388 | 28.556 | 601.856 | 26.146 | 27.095 | 1267.428 | 27.215 | 27.444 | 36.754 | 29.001 | 1.9 | 2.4 | 0.6 | 0.8 | 0.2
3110 | 30/07/2025 10:43:08.846 | 95.184 | 80 | 100 | 70 | 53 | 31.686 | 9.289 | 7.124 | 134.602 | 30.159 | 28.55 | 28.578 | 603.261 | 26.153 | 27.097 | 1274.611 | 27.21 | 27.439 | 36.348 | 26.001 | 1.5 | 1.6 | 0.3 | 0.7 | 0.2
3111 | 30/07/2025 10:43:10.482 | 94.632 | 78 | 100 | 71 | 52 | 28.046 | 9.161 | 7.123 | 134.613 | 30.157 | 28.538 | 28.573 | 603.143 | 26.164 | 27.116 | 1274.45 | 27.198 | 27.445 | 36.667 | 22.001 | 3.8 | 1.6 | 1.2 | 0 | 0.2
3112 | 30/07/2025 10:43:12.117 | 95.208 | 79 | 100 | 70 | 52 | 31.738 | 9.228 | 7.123 | 134.762 | 30.151 | 28.455 | 28.57 | 603.345 | 26.159 | 27.099 | 1274.525 | 27.2 | 27.465 | 36.818 | 22.001 | 3.8 | 1.6 | 1.2 | 0 | 0.2
3113 | 30/07/2025 10:43:13.752 | 95.4 | 79 | 100 | 71 | 51 | 29.173 | 9.28 | 7.125 | 134.599 | 30.152 | 28.398 | 28.536 | 603.254 | 26.168 | 27.114 | 1268.661 | 27.202 | 27.449 | 36.755 | 27.001 | 1.5 | 1.4 | 1.2 | 1.6 | 0.1
3114 | 30/07/2025 10:43:15.388 | 95.688 | 81 | 100 | 70 | 53 | 28.061 | 9.29 | 7.12 | 134.659 | 30.145 | 28.386 | 28.588 | 602.149 | 26.166 | 27.122 | 1280.306 | 27.21 | 27.448 | 36.472 | 24.001 | 1.9 | 1.4 | 0.6 | 0.4 | 0.1
3115 | 30/07/2025 10:43:17.021 | 95.64 | 78 | 100 | 70 | 52 | 31.359 | 9.503 | 7.124 | 134.45 | 30.122 | 28.41 | 28.567 | 602.047 | 26.154 | 27.135 | 1276.622 | 27.225 | 27.436 | 36.504 | 24.001 | 3.2 | 3.5 | 0 | 0.8 | 0.2
3116 | 30/07/2025 10:43:18.659 | 95.112 | 78 | 100 | 71 | 52 | 31.326 | 9.394 | 7.136 | 134.933 | 30.132 | 28.403 | 28.558 | 602.044 | 26.169 | 27.136 | 1290.213 | 27.181 | 27.452 | 36.802 | 29.001 | 2.2 | 3.5 | 0 | 0.6 | 0.2
3117 | 30/07/2025 10:43:20.293 | 95.088 | 78 | 100 | 70 | 51 | 27.704 | 9.172 | 7.135 | 134.666 | 30.125 | 28.554 | 28.547 | 602.028 | 26.157 | 27.111 | 1288.591 | 27.202 | 27.463 | 36.634 | 29.001 | 2.2 | 3.5 | 0 | 0.6 | 0.2
3118 | 30/07/2025 10:43:21.931 | 95.856 | 80 | 100 | 71 | 52 | 31.671 | 9.208 | 7.133 | 134.86 | 30.149 | 28.537 | 28.539 | 601.998 | 26.173 | 27.1 | 1287.459 | 27.207 | 27.443 | 36.773 | 33.001 | 1.4 | 1.9 | 1.2 | 0 | 0.1
3119 | 30/07/2025 10:43:23.566 | 95.76 | 82 | 100 | 70 | 53 | 28.579 | 9.511 | 7.133 | 134.609 | 30.141 | 28.393 | 28.584 | 601.992 | 26.165 | 27.113 | 1282.604 | 27.226 | 27.467 | 36.634 | 27.001 | 1 | 1.9 | 0.4 | 0.5 | 0.1
3120 | 30/07/2025 10:43:25.202 | 96.024 | 81 | 100 | 70 | 52 | 28.66 | 9.264 | 7.154 | 134.374 | 30.152 | 28.429 | 28.54 | 601.781 | 26.149 | 27.107 | 1284.765 | 27.204 | 27.421 | 36.724 | 22.001 | 2.1 | 3.4 | 0 | 0.9 | 0.1
3121 | 30/07/2025 10:43:26.836 | 96.12 | 80 | 100 | 70 | 52 | 31.565 | 9.293 | 7.17 | 134.718 | 30.166 | 28.407 | 28.57 | 602.189 | 26.154 | 27.109 | 1287.863 | 27.182 | 27.467 | 36.757 | 28.001 | 2.5 | 3.4 | 0.6 | 0.6 | 0.1
3122 | 30/07/2025 10:43:28.471 | 95.376 | 78 | 100 | 71 | 52 | 30.96 | 9.433 | 7.188 | 134.562 | 30.16 | 28.394 | 28.545 | 602.073 | 26.157 | 27.122 | 1277.092 | 27.218 | 27.448 | 36.778 | 27.001 | 2.7 | 4 | 1.2 | 0.1 | 0.2
3123 | 30/07/2025 10:43:30.107 | 95.136 | 79 | 100 | 71 | 52 | 31.156 | 9.273 | 7.169 | 134.776 | 30.167 | 28.383 | 28.554 | 602.369 | 26.146 | 27.086 | 1277.425 | 27.214 | 27.449 | 36.656 | 27.001 | 2.7 | 4 | 1.2 | 0.1 | 0.2
3124 | 30/07/2025 10:43:31.743 | 95.016 | 79 | 100 | 71 | 52 | 31.674 | 9.38 | 7.153 | 134.367 | 30.15 | 28.424 | 28.556 | 601.761 | 26.152 | 27.131 | 1287.077 | 27.221 | 27.441 | 36.393 | 26.001 | 1.5 | 4 | 1.4 | 0.5 | 0.3
3125 | 30/07/2025 10:43:33.377 | 94.416 | 77 | 100 | 70 | 52 | 28.171 | 9.43 | 7.154 | 134.643 | 30.178 | 28.405 | 28.564 | 601.976 | 26.151 | 27.097 | 1293.077 | 27.197 | 27.441 | 36.588 | 34.001 | 2.4 | 3.3 | 1.3 | 0.5 | 0.3
3126 | 30/07/2025 10:43:35.013 | 94.944 | 80 | 100 | 70 | 52 | 29.209 | 9.483 | 7.152 | 134.786 | 30.161 | 28.405 | 28.562 | 603.299 | 26.133 | 27.1 | 1298.851 | 27.192 | 27.476 | 36.678 | 27.001 | 2.1 | 3.3 | 0.7 | 0.5 | 0.3
3127 | 30/07/2025 10:43:36.668 | 95.52 | 80 | 100 | 70 | 52 | 31.641 | 9.203 | 7.137 | 134.449 | 30.159 | 28.538 | 28.526 | 602.9 | 26.143 | 27.104 | 1301.159 | 27.216 | 27.444 | 36.595 | 21.001 | 2.6 | 3.3 | 1.3 | 0.6 | 0.2
3128 | 30/07/2025 10:43:38.301 | 95.352 | 81 | 100 | 70 | 52 | 30.552 | 9.435 | 7.119 | 134.706 | 30.169 | 28.528 | 28.581 | 603.296 | 26.149 | 27.079 | 1292.586 | 27.21 | 27.432 | 36.443 | 21.001 | 2.6 | 3.3 | 1.3 | 0.6 | 0.2
3129 | 30/07/2025 10:43:39.936 | 95.88 | 80 | 100 | 71 | 52 | 31.505 | 9.505 | 7.124 | 134.467 | 30.161 | 28.443 | 28.574 | 602.562 | 26.156 | 27.094 | 1290.973 | 27.209 | 27.425 | 36.4 | 26.001 | 3.1 | 3.3 | 0.6 | 0.5 | 0.2
3130 | 30/07/2025 10:43:41.572 | 95.76 | 78 | 100 | 70 | 54 | 31.508 | 9.402 | 7.121 | 134.757 | 30.16 | 28.548 | 28.576 | 602.136 | 26.158 | 27.079 | 1286.455 | 27.196 | 27.454 | 36.616 | 26.001 | 2.3 | 1.1 | 0.9 | 0.6 | 0.2
3131 | 30/07/2025 10:43:43.208 | 95.688 | 81 | 100 | 70 | 52 | 27.772 | 9.137 | 7.137 | 134.761 | 30.14 | 28.441 | 28.552 | 601.964 | 26.156 | 27.098 | 1298.626 | 27.193 | 27.466 | 36.663 | 24.001 | 2.2 | 1.1 | 2.4 | 0.6 | 0.1
3132 | 30/07/2025 10:43:44.842 | 96.048 | 79 | 100 | 71 | 52 | 29.826 | 9.177 | 7.135 | 134.711 | 30.171 | 28.389 | 28.564 | 602.132 | 26.159 | 27.103 | 1302.657 | 27.207 | 27.449 | 36.407 | 23.001 | 2.4 | 2.3 | 1.5 | 0.5 | 0.1
3133 | 30/07/2025 10:43:46.476 | 96.576 | 82 | 100 | 69 | 52 | 31.739 | 9.29 | 7.133 | 134.484 | 30.155 | 28.537 | 28.562 | 602.011 | 26.155 | 27.117 | 1297.572 | 27.211 | 27.436 | 36.529 | 23.001 | 2.4 | 2.3 | 1.9 | 0.8 | 0.1
3134 | 30/07/2025 10:43:48.111 | 97.056 | 82 | 100 | 71 | 52 | 28.593 | 9.152 | 7.153 | 133.019 | 30.161 | 28.408 | 28.577 | 601.94 | 26.167 | 27.108 | 1294.905 | 27.203 | 27.428 | 36.532 | 23.001 | 2.4 | 2.3 | 1.9 | 0.8 | 0.1
3135 | 30/07/2025 10:43:49.746 | 97.296 | 82 | 100 | 70 | 52 | 31.597 | 9.13 | 7.153 | 133.197 | 30.127 | 28.407 | 28.568 | 603.12 | 26.168 | 27.123 | 1296.939 | 27.196 | 27.464 | 36.82 | 28.001 | 1.6 | 1.2 | 1 | 0.2 | 0.2
3136 | 30/07/2025 10:43:51.379 | 97.176 | 82 | 100 | 69 | 52 | 30.997 | 9.132 | 7.187 | 133.253 | 30.149 | 28.4 | 28.538 | 603.032 | 26.169 | 27.123 | 1291.006 | 27.198 | 27.437 | 36.593 | 27.001 | 1.2 | 1.2 | 1.1 | 1.1 | 0.2
3137 | 30/07/2025 10:43:53.012 | 97.152 | 82 | 100 | 70 | 52 | 27.542 | 9.208 | 7.151 | 133.117 | 30.137 | 28.386 | 28.567 | 603.144 | 26.142 | 27.106 | 1284.655 | 27.223 | 27.44 | 36.403 | 24.001 | 2.4 | 2.2 | 1 | 0.7 | 0.2
3138 | 30/07/2025 10:43:54.646 | 97.56 | 82 | 100 | 70 | 53 | 30.221 | 9.572 | 7.153 | 132.841 | 30.13 | 28.407 | 28.555 | 603.141 | 26.154 | 27.121 | 1295.988 | 27.212 | 27.429 | 38.139 | 30.001 | 2.7 | 2.2 | 1.1 | 0.5 | 0.3
3139 | 30/07/2025 10:43:56.282 | 97.536 | 81 | 100 | 70 | 52 | 31.703 | 9.314 | 7.153 | 134.65 | 30.152 | 28.406 | 28.563 | 603.334 | 26.18 | 27.12 | 1290.912 | 27.186 | 27.458 | 37.119 | 30.001 | 2.7 | 2.2 | 1.1 | 0.5 | 0.3
3140 | 30/07/2025 10:43:57.916 | 97.344 | 82 | 100 | 70 | 52 | 29.129 | 9.387 | 7.137 | 134.554 | 30.138 | 28.4 | 28.537 | 603.152 | 26.143 | 27.128 | 1287.013 | 27.181 | 27.45 | 38.643 | 30.001 | 2 | 0.8 | 0.8 | 0.7 | 0.3
3141 | 30/07/2025 10:43:59.556 | 97.296 | 82 | 100 | 70 | 52 | 31.617 | 9.284 | 7.134 | 134.63 | 30.16 | 28.544 | 28.552 | 603.204 | 26.16 | 27.107 | 1282.135 | 27.197 | 27.453 | 38.298 | 26.001 | 1.1 | 0.8 | 0 | 1.1 | 0.3
3142 | 30/07/2025 10:44:01.189 | 97.464 | 83 | 100 | 70 | 52 | 30.409 | 9.481 | 7.133 | 134.467 | 30.157 | 28.505 | 28.563 | 603.212 | 26.158 | 27.118 | 1283.992 | 27.225 | 27.449 | 38.194 | 29.001 | 2.7 | 2.4 | 0.9 | 0.5 | 0.3
3143 | 30/07/2025 10:44:02.823 | 97.416 | 81 | 100 | 70 | 52 | 27.533 | 9.29 | 7.136 | 134.549 | 30.161 | 28.529 | 28.557 | 603.06 | 26.157 | 27.127 | 1277.322 | 27.207 | 27.423 | 36.429 | 27.001 | 2.9 | 2.4 | 1.8 | 0.7 | 0.3
3144 | 30/07/2025 10:44:04.457 | 97.08 | 81 | 100 | 70 | 51 | 30.748 | 9.288 | 7.135 | 134.75 | 30.172 | 28.401 | 28.568 | 603.34 | 26.162 | 27.106 | 1278.816 | 27.186 | 27.456 | 36.608 | 31.001 | 1.5 | 3 | 1 | 0.5 | 0.4
3145 | 30/07/2025 10:44:06.090 | 96.984 | 81 | 100 | 71 | 52 | 27.675 | 9.269 | 7.136 | 134.789 | 30.176 | 28.463 | 28.545 | 603.209 | 26.163 | 27.114 | 1279.552 | 27.177 | 27.432 | 36.841 | 31.001 | 1.5 | 3 | 1 | 0.5 | 0.4
3146 | 30/07/2025 10:44:07.727 | 97.008 | 82 | 100 | 70 | 52 | 29.706 | 9.147 | 7.134 | 134.674 | 30.169 | 28.532 | 28.561 | 603.298 | 26.142 | 27.101 | 1286.804 | 27.211 | 27.449 | 36.841 | 27.001 | 3.8 | 3 | 0.8 | 0.8 | 0.4
3147 | 30/07/2025 10:44:09.362 | 97.08 | 81 | 100 | 70 | 52 | 31.699 | 9.584 | 7.122 | 134.471 | 30.161 | 28.391 | 28.57 | 603.073 | 26.145 | 27.119 | 1281.514 | 27.214 | 27.438 | 36.563 | 27.001 | 3.1 | 2.3 | 1.5 | 0.6 | 0.4
3148 | 30/07/2025 10:44:10.996 | 97.008 | 79 | 100 | 70 | 51 | 29.901 | 9.207 | 7.096 | 134.638 | 30.157 | 28.397 | 28.578 | 603.353 | 26.156 | 27.086 | 1285.117 | 27.199 | 27.434 | 36.544 | 29.001 | 3.8 | 2.3 | 1.3 | 0.7 | 0.4
3149 | 30/07/2025 10:44:12.632 | 96.744 | 82 | 100 | 70 | 52 | 27.853 | 9.216 | 7.088 | 134.624 | 30.143 | 28.399 | 28.548 | 603.248 | 26.15 | 27.093 | 1287.192 | 27.19 | 27.473 | 36.744 | 24.001 | 2.6 | 3.7 | 2.2 | 0.6 | 0.3
3150 | 30/07/2025 10:44:14.268 | 96.504 | 81 | 100 | 71 | 53 | 31.251 | 9.029 | 7.134 | 134.645 | 30.157 | 28.386 | 28.537 | 603.064 | 26.157 | 27.088 | 1294.289 | 27.204 | 27.461 | 36.672 | 24.001 | 2.6 | 3.7 | 2.2 | 0.6 | 0.3
3151 | 30/07/2025 10:44:15.930 | 96.84 | 82 | 100 | 71 | 52 | 27.574 | 9.2 | 7.134 | 134.576 | 30.151 | 28.517 | 28.557 | 603.159 | 26.146 | 27.097 | 1290.648 | 27.234 | 27.455 | 36.66 | 27.001 | 1.2 | 3.7 | 1.1 | 1.3 | 0.3
3152 | 30/07/2025 10:44:17.566 | 96.48 | 82 | 100 | 70 | 52 | 30.367 | 9.434 | 7.135 | 134.424 | 30.159 | 28.402 | 28.567 | 603.024 | 26.162 | 27.111 | 1285.876 | 27.211 | 27.428 | 36.565 | 25.001 | 1.8 | 1.1 | 2.2 | 0.7 | 0.3
3153 | 30/07/2025 10:44:19.200 | 96.624 | 81 | 100 | 70 | 52 | 31.746 | 9.287 | 7.124 | 134.627 | 30.149 | 28.552 | 28.56 | 602.095 | 26.165 | 27.097 | 1287.26 | 27.199 | 27.459 | 36.625 | 30.001 | 3.1 | 1.1 | 1.7 | 1.1 | 0.3
3154 | 30/07/2025 10:44:20.836 | 96.504 | 82 | 100 | 70 | 54 | 29.383 | 9.436 | 7.122 | 134.71 | 30.145 | 28.543 | 28.545 | 601.954 | 26.162 | 27.12 | 1296.918 | 27.181 | 27.442 | 36.704 | 27.001 | 2.9 | 1.6 | 1.3 | 0.2 | 0.4
3155 | 30/07/2025 10:44:22.471 | 96.336 | 81 | 100 | 71 | 53 | 28.034 | 9.287 | 7.122 | 134.692 | 30.161 | 28.53 | 28.557 | 602.078 | 26.167 | 27.113 | 1310.526 | 27.208 | 27.444 | 36.578 | 26.001 | 2.9 | 1.6 | 1.3 | 0.8 | 0.4
3156 | 30/07/2025 10:44:24.106 | 96.48 | 80 | 100 | 70 | 52 | 31.451 | 9.315 | 7.101 | 134.45 | 30.131 | 28.396 | 28.579 | 602.592 | 26.16 | 27.126 | 1306.671 | 27.225 | 27.448 | 36.529 | 26.001 | 2.9 | 1.6 | 1.3 | 0.8 | 0.4
3157 | 30/07/2025 10:44:25.743 | 96.336 | 79 | 100 | 71 | 52 | 27.547 | 9.336 | 7.088 | 134.402 | 30.147 | 28.547 | 28.567 | 603.327 | 26.155 | 27.124 | 1304.06 | 27.207 | 27.434 | 36.393 | 24.001 | 4.1 | 3.1 | 1.5 | 0.8 | 0.4
3158 | 30/07/2025 10:44:27.383 | 96.504 | 81 | 100 | 70 | 52 | 30.734 | 9.434 | 7.089 | 134.589 | 30.122 | 28.547 | 28.559 | 603.234 | 26.154 | 27.125 | 1295.098 | 27.205 | 27.446 | 36.676 | 24.001 | 3.4 | 3.1 | 1.2 | 0.6 | 0.4
3159 | 30/07/2025 10:44:29.018 | 96.672 | 83 | 100 | 70 | 52 | 31.693 | 9.397 | 7.124 | 134.927 | 30.135 | 28.544 | 28.53 | 603.152 | 26.168 | 27.131 | 1287.304 | 27.184 | 27.444 | 37.703 | 26.001 | 2.8 | 2.1 | 1.8 | 0 | 0.4
3160 | 30/07/2025 10:44:30.653 | 95.976 | 78 | 100 | 70 | 52 | 28.651 | 9.269 | 7.133 | 134.64 | 30.155 | 28.388 | 28.559 | 603.127 | 26.157 | 27.1 | 1287.867 | 27.208 | 27.448 | 38.471 | 30.001 | 1.5 | 2.1 | 1 | 0 | 0.4
3161 | 30/07/2025 10:44:32.291 | 95.784 | 79 | 100 | 70 | 52 | 28.543 | 9.527 | 7.136 | 134.346 | 30.139 | 28.401 | 28.548 | 603.025 | 26.152 | 27.121 | 1292.048 | 27.211 | 27.428 | 38.235 | 30.001 | 1.5 | 2.1 | 1 | 0 | 0.4
3162 | 30/07/2025 10:44:33.926 | 95.832 | 79 | 100 | 70 | 52 | 29.777 | 9.295 | 7.135 | 134.344 | 30.142 | 28.415 | 28.575 | 603.174 | 26.16 | 27.121 | 1287.215 | 27.215 | 27.447 | 38.283 | 29.001 | 2.5 | 3.3 | 1.2 | 0.5 | 0.4
3163 | 30/07/2025 10:44:35.562 | 95.28 | 79 | 100 | 70 | 52 | 27.712 | 9.397 | 7.137 | 134.627 | 30.168 | 28.408 | 28.558 | 603.023 | 26.151 | 27.113 | 1286.937 | 27.174 | 27.449 | 36.681 | 27.001 | 3 | 3.3 | 1.3 | 0.5 | 0.3
3164 | 30/07/2025 10:44:37.197 | 94.92 | 79 | 100 | 70 | 52 | 31.072 | 9.137 | 7.134 | 134.622 | 30.164 | 28.389 | 28.563 | 603.243 | 26.149 | 27.107 | 1287.402 | 27.201 | 27.446 | 36.505 | 24.001 | 1.6 | 3.1 | 0.1 | 0.1 | 0.3
3165 | 30/07/2025 10:44:38.833 | 95.016 | 78 | 100 | 71 | 52 | 31.634 | 9.145 | 7.133 | 134.489 | 30.167 | 28.392 | 28.568 | 603.203 | 26.142 | 27.118 | 1282.645 | 27.229 | 27.456 | 38.471 | 29.001 | 1.9 | 3.1 | 1.8 | 0 | 0.3
3166 | 30/07/2025 10:44:40.468 | 95.328 | 78 | 100 | 70 | 52 | 28.057 | 9.438 | 7.135 | 134.512 | 30.164 | 28.554 | 28.564 | 603.262 | 26.172 | 27.117 | 1277.161 | 27.206 | 27.424 | 38.208 | 26.001 | 3.4 | 2.6 | 0.6 | 0.5 | 0.3
3167 | 30/07/2025 10:44:42.102 | 95.928 | 80 | 100 | 70 | 51 | 31.744 | 9.287 | 7.136 | 134.547 | 30.151 | 28.518 | 28.553 | 603.267 | 26.151 | 27.122 | 1277.082 | 27.214 | 27.451 | 38.404 | 26.001 | 3.4 | 2.6 | 0.6 | 0.5 | 0.3
3168 | 30/07/2025 10:44:43.735 | 95.376 | 78 | 100 | 71 | 52 | 29.317 | 9.353 | 7.135 | 134.821 | 30.171 | 28.396 | 28.553 | 603.13 | 26.158 | 27.105 | 1295.532 | 27.17 | 27.436 | 38.61 | 28.001 | 3.3 | 2.6 | 1.2 | 0.2 | 0.3
3169 | 30/07/2025 10:44:45.369 | 95.52 | 78 | 100 | 70 | 53 | 28.215 | 9.251 | 7.134 | 134.627 | 30.147 | 28.384 | 28.554 | 603.298 | 26.136 | 27.082 | 1284.776 | 27.216 | 27.449 | 38.676 | 25.001 | 1.9 | 3.2 | 1.6 | 0 | 0.3
3170 | 30/07/2025 10:44:47.006 | 95.496 | 79 | 100 | 70 | 52 | 31.431 | 9.526 | 7.135 | 134.461 | 30.152 | 28.393 | 28.561 | 603.166 | 26.143 | 27.09 | 1296.74 | 27.204 | 27.438 | 36.901 | 24.001 | 2.9 | 3.2 | 2 | 0.5 | 0.3
3171 | 30/07/2025 10:44:48.641 | 95.496 | 81 | 100 | 70 | 52 | 31.506 | 9.221 | 7.136 | 134.577 | 30.164 | 28.405 | 28.574 | 603.388 | 26.147 | 27.083 | 1300.709 | 27.201 | 27.429 | 38.247 | 24.001 | 2.6 | 1.5 | 0.7 | 0.7 | 0.3
3172 | 30/07/2025 10:44:50.277 | 95.568 | 82 | 100 | 70 | 51 | 27.785 | 9.292 | 7.135 | 134.684 | 30.15 | 28.514 | 28.564 | 603.134 | 26.159 | 27.104 | 1301.962 | 27.187 | 27.461 | 36.6 | 24.001 | 2.6 | 1.5 | 0.7 | 0.7 | 0.3
3173 | 30/07/2025 10:44:51.913 | 95.904 | 80 | 100 | 71 | 52 | 31.739 | 9.397 | 7.134 | 134.734 | 30.157 | 28.424 | 28.556 | 603.243 | 26.144 | 27.091 | 1307.358 | 27.191 | 27.463 | 36.663 | 28.001 | 4.2 | 1.5 | 1.8 | 0.3 | 0.2
3174 | 30/07/2025 10:44:53.549 | 96.24 | 80 | 100 | 70 | 50 | 28.732 | 9.189 | 7.135 | 134.556 | 30.156 | 28.415 | 28.56 | 603.091 | 26.161 | 27.118 | 1307.615 | 27.225 | 27.458 | 36.488 | 29.001 | 3.2 | 3.1 | 1.4 | 0 | 0.3
3175 | 30/07/2025 10:44:55.187 | 96.696 | 81 | 100 | 70 | 52 | 28.633 | 9.135 | 7.135 | 134.526 | 30.161 | 28.546 | 28.578 | 603.253 | 26.186 | 27.122 | 1305.26 | 27.203 | 27.44 | 38.301 | 21.001 | 2.5 | 3.1 | 0.9 | 0.5 | 0.4
3176 | 30/07/2025 10:44:56.823 | 96.096 | 81 | 100 | 71 | 52 | 31.583 | 9.163 | 7.135 | 134.588 | 30.139 | 28.507 | 28.567 | 603.282 | 26.154 | 27.117 | 1297.493 | 27.2 | 27.469 | 36.574 | 24.001 | 2.4 | 3.5 | 1.6 | 1.1 | 0.4
3177 | 30/07/2025 10:44:58.458 | 95.448 | 79 | 100 | 70 | 52 | 31.101 | 9.407 | 7.136 | 134.788 | 30.14 | 28.401 | 28.546 | 603.106 | 26.163 | 27.143 | 1294.9 | 27.173 | 27.458 | 36.792 | 27.001 | 2.4 | 3.5 | 0.6 | 0.5 | 0.3
3178 | 30/07/2025 10:45:00.092 | 96.24 | 80 | 100 | 70 | 51 | 31.237 | 9.166 | 7.135 | 134.64 | 30.119 | 28.546 | 28.541 | 603.244 | 26.157 | 27.126 | 1297.497 | 27.216 | 27.459 | 36.776 | 27.001 | 2.4 | 3.5 | 0.6 | 0.5 | 0.3
3179 | 30/07/2025 10:45:01.727 | 96.216 | 79 | 100 | 71 | 52 | 31.642 | 9.287 | 7.135 | 133.166 | 30.125 | 28.384 | 28.559 | 603.144 | 26.167 | 27.131 | 1299.261 | 27.218 | 27.448 | 36.522 | 34.001 | 2.3 | 2 | 1.1 | 0.5 | 0.3
3180 | 30/07/2025 10:45:03.364 | 95.928 | 79 | 100 | 70 | 52 | 28.227 | 9.421 | 7.121 | 132.948 | 30.135 | 28.546 | 28.573 | 603.058 | 26.156 | 27.104 | 1297.183 | 27.197 | 27.421 | 36.42 | 30.001 | 3.2 | 2 | 0.5 | 0.5 | 0.2
3181 | 30/07/2025 10:45:04.999 | 95.952 | 81 | 100 | 70 | 51 | 29.155 | 9.136 | 7.122 | 133.055 | 30.148 | 28.416 | 28.561 | 603.119 | 26.162 | 27.125 | 1296.949 | 27.208 | 27.462 | 36.629 | 31.001 | 1.4 | 3.9 | 0.6 | 0.8 | 0.2
3182 | 30/07/2025 10:45:06.637 | 95.496 | 81 | 100 | 71 | 52 | 31.617 | 9.114 | 7.123 | 133.403 | 30.167 | 28.478 | 28.547 | 603.225 | 26.159 | 27.11 | 1285.001 | 27.185 | 27.449 | 38.222 | 26.001 | 1.8 | 3.9 | 0 | 0 | 0.3
3183 | 30/07/2025 10:45:08.272 | 96.72 | 80 | 100 | 70 | 52 | 30.392 | 9.286 | 7.12 | 133.16 | 30.155 | 28.385 | 28.572 | 603.272 | 26.151 | 27.107 | 1272.119 | 27.215 | 27.46 | 38.424 | 26.001 | 1.8 | 3.9 | 0 | 0 | 0.3
3184 | 30/07/2025 10:45:09.907 | 96.288 | 82 | 100 | 71 | 51 | 31.377 | 9.339 | 7.118 | 133.23 | 30.164 | 28.386 | 28.586 | 603.206 | 26.166 | 27.118 | 1269.928 | 27.206 | 27.446 | 37.646 | 23.001 | 2.2 | 2.4 | 1.8 | 0.8 | 0.2
3185 | 30/07/2025 10:45:11.541 | 96.888 | 79 | 100 | 70 | 50 | 31.418 | 9.288 | 7.121 | 132.905 | 30.168 | 28.51 | 28.565 | 603.186 | 26.159 | 27.098 | 1272.345 | 27.215 | 27.449 | 36.345 | 29.001 | 2.4 | 2.4 | 0.8 | 0.4 | 0.2
3186 | 30/07/2025 10:45:13.178 | 97.848 | 81 | 100 | 70 | 52 | 27.701 | 9.284 | 7.123 | 133.197 | 30.162 | 28.549 | 28.562 | 602.033 | 26.15 | 27.121 | 1269.333 | 27.168 | 27.45 | 38.583 | 31.001 | 3.2 | 1.8 | 1.5 | 0.5 | 0.2
3187 | 30/07/2025 10:45:14.810 | 98.304 | 83 | 98 | 70 | 52 | 29.612 | 9.407 | 7.085 | 133.136 | 30.163 | 28.539 | 28.552 | 603.286 | 26.146 | 27.107 | 1278.97 | 27.201 | 27.45 | 36.606 | 29.001 | 2.9 | 1.8 | 1.5 | 0.9 | 0.2
3188 | 30/07/2025 10:45:16.446 | 98.4 | 84 | 100 | 70 | 50 | 31.705 | 9.288 | 7.117 | 133.029 | 30.147 | 28.536 | 28.563 | 603.162 | 26.158 | 27.114 | 1282.546 | 27.23 | 27.45 | 36.676 | 26.001 | 3.1 | 2.9 | 0.6 | 0.4 | 0.2
3189 | 30/07/2025 10:45:18.082 | 98.496 | 84 | 100 | 70 | 53 | 28.607 | 9.288 | 7.133 | 133.089 | 30.158 | 28.546 | 28.576 | 603.256 | 26.148 | 27.086 | 1287.56 | 27.204 | 27.448 | 36.526 | 26.001 | 3.1 | 2.9 | 0.6 | 0.4 | 0.2
3190 | 30/07/2025 10:45:19.802 | 98.688 | 83 | 100 | 71 | 52 | 31.604 | 9.132 | 7.136 | 133.031 | 30.16 | 28.556 | 28.564 | 603.141 | 26.136 | 27.103 | 1294.725 | 27.216 | 27.446 | 36.589 | 22.001 | 1.6 | 2.9 | 0.6 | 0.5 | 0.2
3191 | 30/07/2025 10:45:21.446 | 98.232 | 83 | 100 | 70 | 52 | 31.097 | 9.228 | 7.134 | 133.199 | 30.165 | 28.547 | 28.56 | 603.273 | 26.159 | 27.084 | 1306.659 | 27.167 | 27.451 | 36.747 | 22.001 | 2 | 2.2 | 0.3 | 0.2 | 0.2
3192 | 30/07/2025 10:45:23.080 | 98.64 | 82 | 100 | 71 | 52 | 27.507 | 9.131 | 7.187 | 133.043 | 30.146 | 28.54 | 28.561 | 603.3 | 26.147 | 27.095 | 1306.547 | 27.224 | 27.459 | 36.68 | 24.001 | 3.8 | 2.2 | 1.2 | 0.5 | 0.2
3193 | 30/07/2025 10:45:24.713 | 98.856 | 82 | 100 | 70 | 52 | 30.373 | 9.145 | 7.13 | 133.028 | 30.15 | 28.536 | 28.57 | 603.159 | 26.16 | 27.106 | 1296.044 | 27.202 | 27.44 | 36.54 | 24.001 | 2.7 | 3.3 | 0.1 | 0.2 | 0.2
3194 | 30/07/2025 10:45:26.348 | 98.928 | 83 | 100 | 70 | 52 | 31.726 | 9.43 | 7.124 | 132.939 | 30.164 | 28.552 | 28.586 | 603.389 | 26.155 | 27.093 | 1287.642 | 27.199 | 27.44 | 36.516 | 24.001 | 2.7 | 3.3 | 0.1 | 0.2 | 0.2
3195 | 30/07/2025 10:45:27.982 | 98.52 | 83 | 100 | 71 | 52 | 29.25 | 9.29 | 7.123 | 132.89 | 30.168 | 28.546 | 28.558 | 603.251 | 26.17 | 27.116 | 1286.586 | 27.195 | 27.444 | 36.924 | 30.001 | 3.2 | 3.3 | 0.6 | 0 | 0.2
3196 | 30/07/2025 10:45:29.617 | 98.88 | 83 | 100 | 71 | 52 | 31.665 | 9.212 | 7.135 | 133.254 | 30.153 | 28.556 | 28.545 | 603.357 | 26.156 | 27.107 | 1297.472 | 27.178 | 27.45 | 36.729 | 28.001 | 3.2 | 2.4 | 1 | 1.2 | 0.1
3197 | 30/07/2025 10:45:31.255 | 100.08 | 84 | 100 | 70 | 52 | 30.584 | 9.138 | 7.136 | 133.032 | 30.144 | 28.526 | 28.545 | 603.196 | 26.166 | 27.123 | 1306.776 | 27.226 | 27.452 | 36.77 | 28.001 | 3.7 | 2.4 | 0.9 | 0.3 | 0.1
3198 | 30/07/2025 10:45:32.890 | 100.224 | 84 | 100 | 70 | 52 | 27.592 | 9.506 | 7.134 | 132.921 | 30.151 | 28.548 | 28.576 | 603.23 | 26.166 | 27.11 | 1304.981 | 27.204 | 27.43 | 36.695 | 25.001 | 2.7 | 2.4 | 1.3 | 1 | 0.1
3199 | 30/07/2025 10:45:34.524 | 99.672 | 83 | 100 | 71 | 52 | 30.909 | 9.505 | 7.135 | 133.166 | 30.13 | 28.563 | 28.573 | 603.182 | 26.165 | 27.123 | 1309.144 | 27.215 | 27.475 | 36.492 | 29.001 | 3.5 | 2.4 | 0.9 | 1 | 0.1
3200 | 30/07/2025 10:45:36.158 | 100.128 | 83 | 100 | 70 | 52 | 31.8 | 9.474 | 7.138 | 133.337 | 30.136 | 28.547 | 28.554 | 603.105 | 26.159 | 27.12 | 1311.545 | 27.173 | 27.455 | 36.757 | 29.001 | 3.5 | 2.4 | 0.9 | 1 | 0.1
3201 | 30/07/2025 10:45:37.793 | 100.728 | 83 | 100 | 70 | 52 | 29.816 | 9.293 | 7.135 | 133.151 | 30.12 | 28.548 | 28.546 | 603.145 | 26.146 | 27.116 | 1311.548 | 27.211 | 27.454 | 36.687 | 28.001 | 3.9 | 1.3 | 0.6 | 1.4 | 0.1
3202 | 30/07/2025 10:45:39.428 | 101.04 | 83 | 100 | 70 | 52 | 31.738 | 9.288 | 7.134 | 133.094 | 30.135 | 28.53 | 28.569 | 602.961 | 26.158 | 27.123 | 1306.763 | 27.215 | 27.437 | 36.645 | 24.001 | 3.7 | 1.3 | 0.3 | 0.6 | 0.1
3203 | 30/07/2025 10:45:41.064 | 101.112 | 85 | 100 | 70 | 52 | 29.973 | 9.313 | 7.094 | 133.136 | 30.149 | 28.551 | 28.569 | 603.32 | 26.141 | 27.101 | 1307.191 | 27.197 | 27.432 | 36.554 | 26.001 | 3 | 2 | 1.2 | 0.3 | 0.1
3204 | 30/07/2025 10:45:42.698 | 101.256 | 84 | 100 | 70 | 53 | 27.768 | 9.539 | 7.087 | 133.177 | 30.141 | 28.552 | 28.547 | 603.295 | 26.161 | 27.129 | 1314.824 | 27.202 | 27.457 | 36.598 | 28.001 | 3.6 | 2 | 1.6 | 0.5 | 0.1
3205 | 30/07/2025 10:45:44.331 | 101.088 | 83 | 100 | 70 | 51 | 31.133 | 9.211 | 7.086 | 133.312 | 30.188 | 28.549 | 28.55 | 603.2 | 26.17 | 27.113 | 1326.797 | 27.176 | 27.453 | 36.783 | 28.001 | 3.6 | 2 | 1.6 | 0.5 | 0.1
3206 | 30/07/2025 10:45:45.966 | 101.304 | 84 | 100 | 71 | 52 | 27.568 | 9.224 | 7.088 | 133.139 | 30.169 | 28.541 | 28.534 | 603.127 | 26.141 | 27.131 | 1331.504 | 27.21 | 27.457 | 36.727 | 25.001 | 2.4 | 1.7 | 0.7 | 0 | 0.1
3207 | 30/07/2025 10:45:47.602 | 101.352 | 86 | 100 | 70 | 52 | 30.227 | 9.432 | 7.118 | 133.112 | 30.154 | 28.529 | 28.583 | 603.356 | 26.162 | 27.102 | 1327.489 | 27.211 | 27.436 | 36.7 | 25.001 | 4.8 | 1.7 | 0 | 0 | 0.2
3208 | 30/07/2025 10:45:49.240 | 100.344 | 85 | 100 | 71 | 52 | 31.783 | 9.261 | 7.122 | 132.931 | 30.139 | 28.572 | 28.573 | 603.273 | 26.142 | 27.101 | 1326.042 | 27.227 | 27.443 | 36.521 | 22.001 | 3.6 | 2.4 | 1.8 | 0 | 0.2
3209 | 30/07/2025 10:45:50.880 | 100.536 | 85 | 100 | 71 | 52 | 29.37 | 9.504 | 7.136 | 134.055 | 30.163 | 28.536 | 28.569 | 602.932 | 26.133 | 27.11 | 1320.006 | 27.178 | 27.454 | 36.656 | 25.001 | 4.6 | 2.4 | 1.5 | 0.8 | 0.2
3210 | 30/07/2025 10:45:52.516 | 99.984 | 84 | 100 | 70 | 52 | 28.146 | 9.225 | 7.135 | 134.756 | 30.16 | 28.546 | 28.553 | 603.321 | 26.141 | 27.094 | 1309.252 | 27.197 | 27.446 | 38.355 | 30.001 | 3.6 | 2.6 | 0.6 | 0.8 | 0.2
3211 | 30/07/2025 10:45:54.152 | 100.2 | 84 | 100 | 70 | 53 | 30.55 | 8.919 | 7.135 | 134.613 | 30.156 | 28.523 | 28.55 | 603.066 | 26.158 | 27.109 | 1304.824 | 27.207 | 27.443 | 38.471 | 30.001 | 3.6 | 2.6 | 0.6 | 0.8 | 0.2
3212 | 30/07/2025 10:45:55.788 | 99.936 | 83 | 100 | 71 | 52 | 27.579 | 9.208 | 7.087 | 134.544 | 30.156 | 28.398 | 28.579 | 603.241 | 26.146 | 27.067 | 1297.4 | 27.21 | 27.445 | 38.286 | 27.001 | 2.7 | 2.6 | 0.6 | 0.4 | 0.3
3213 | 30/07/2025 10:45:57.424 | 99.816 | 84 | 100 | 71 | 52 | 30.835 | 9.482 | 7.09 | 134.367 | 30.158 | 28.556 | 28.566 | 603.147 | 26.149 | 27.116 | 1296.668 | 27.21 | 27.449 | 36.573 | 29.001 | 2.3 | 3.5 | 0.9 | 0.5 | 0.3
3214 | 30/07/2025 10:45:59.068 | 99.984 | 84 | 100 | 70 | 52 | 31.709 | 9.155 | 7.086 | 134.765 | 30.157 | 28.548 | 28.566 | 603.137 | 26.154 | 27.1 | 1295.134 | 27.175 | 27.455 | 38.545 | 29.001 | 3.5 | 3.5 | 0.3 | 0.5 | 0.3
3215 | 30/07/2025 10:46:00.709 | 100.128 | 84 | 100 | 71 | 52 | 28.73 | 8.893 | 7.087 | 134.515 | 30.148 | 28.547 | 28.548 | 603.259 | 26.162 | 27.104 | 1291.29 | 27.223 | 27.452 | 38.571 | 27.001 | 2.8 | 1.9 | 1.5 | 0.5 | 0.2
3216 | 30/07/2025 10:46:02.348 | 100.08 | 82 | 100 | 71 | 52 | 28.634 | 9.231 | 7.085 | 134.459 | 30.146 | 28.532 | 28.572 | 603.199 | 26.175 | 27.125 | 1287.304 | 27.205 | 27.445 | 38.295 | 27.001 | 2.8 | 1.9 | 1.5 | 0.5 | 0.2
3217 | 30/07/2025 10:46:03.985 | 100.2 | 83 | 99 | 71 | 52 | 29.972 | 9.134 | 7.089 | 134.513 | 30.137 | 28.562 | 28.571 | 603.297 | 26.154 | 27.125 | 1283.522 | 27.234 | 27.443 | 38.144 | 27.001 | 1.8 | 1.9 | 0.9 | 0.2 | 0.2
3218 | 30/07/2025 10:46:05.622 | 99.984 | 84 | 100 | 70 | 52 | 27.712 | 9.436 | 7.088 | 134.915 | 30.151 | 28.543 | 28.555 | 603.23 | 26.173 | 27.128 | 1287.005 | 27.193 | 27.449 | 38.536 | 28.001 | 3.2 | 2.2 | 1 | 0 | 0.2
3219 | 30/07/2025 10:46:07.255 | 100.176 | 84 | 100 | 70 | 53 | 31.212 | 9.159 | 7.088 | 134.724 | 30.13 | 28.549 | 28.56 | 603.259 | 26.151 | 27.112 | 1287.531 | 27.18 | 27.606 | 38.507 | 25.001 | 2.9 | 2.2 | 0.5 | 0 | 0.2
3220 | 30/07/2025 10:46:08.891 | 100.224 | 83 | 100 | 70 | 52 | 31.744 | 9.283 | 7.088 | 134.637 | 30.114 | 28.519 | 28.541 | 603.203 | 26.16 | 27.137 | 1294.725 | 27.216 | 27.448 | 36.927 | 25.001 | 3.4 | 3.6 | 0.6 | 0.5 | 0.2
3221 | 30/07/2025 10:46:10.527 | 99.984 | 82 | 100 | 70 | 52 | 28.243 | 9.288 | 7.089 | 134.686 | 30.14 | 28.433 | 28.574 | 603.268 | 26.152 | 27.116 | 1299.917 | 27.206 | 27.435 | 36.575 | 24.001 | 2.4 | 3.6 | 0.9 | 1.1 | 0.2
3222 | 30/07/2025 10:46:12.165 | 99.624 | 82 | 100 | 70 | 52 | 31.762 | 9.284 | 7.123 | 134.446 | 30.129 | 28.548 | 28.57 | 602.947 | 26.161 | 27.131 | 1307.256 | 27.212 | 27.576 | 36.569 | 24.001 | 2.4 | 3.6 | 0.9 | 1.1 | 0.2
3223 | 30/07/2025 10:46:13.799 | 99.216 | 82 | 100 | 70 | 52 | 29.433 | 9.134 | 7.124 | 134.741 | 30.156 | 28.556 | 28.578 | 603.122 | 26.167 | 27.113 | 1306.977 | 27.192 | 27.468 | 36.698 | 29.001 | 2.2 | 2.6 | 1.3 | 0.5 | 0.2
3224 | 30/07/2025 10:46:15.434 | 99 | 83 | 100 | 71 | 52 | 28.172 | 9.211 | 7.122 | 134.549 | 30.151 | 28.556 | 28.54 | 603.123 | 26.156 | 27.126 | 1286.906 | 27.203 | 27.595 | 36.6 | 24.001 | 3 | 2.6 | 0.6 | 1.3 | 0.3
3225 | 30/07/2025 10:46:17.071 | 98.544 | 81 | 100 | 70 | 52 | 31.426 | 9.207 | 7.134 | 134.696 | 30.168 | 28.527 | 28.568 | 603.225 | 26.168 | 27.13 | 1287.206 | 27.222 | 27.543 | 36.78 | 22.001 | 1.3 | 1.2 | 0.3 | 0.3 | 0.3
3226 | 30/07/2025 10:46:18.706 | 98.424 | 82 | 100 | 70 | 52 | 31.447 | 9.133 | 7.123 | 134.44 | 30.162 | 28.544 | 28.57 | 603.211 | 26.15 | 27.107 | 1296.543 | 27.208 | 27.448 | 36.442 | 31.001 | 2.3 | 1.2 | 0 | 0.6 | 0.3
3227 | 30/07/2025 10:46:20.341 | 98.112 | 81 | 100 | 70 | 52 | 27.812 | 9.128 | 7.124 | 134.619 | 30.166 | 28.544 | 28.561 | 603.225 | 26.15 | 27.127 | 1296.628 | 27.19 | 27.449 | 36.571 | 31.001 | 2.3 | 1.2 | 0 | 0.6 | 0.3
3228 | 30/07/2025 10:46:21.978 | 98.928 | 83 | 100 | 71 | 52 | 31.755 | 9.211 | 7.121 | 134.758 | 30.156 | 28.55 | 28.566 | 603.154 | 26.145 | 27.099 | 1292.291 | 27.19 | 27.469 | 36.807 | 29.001 | 2.7 | 2.6 | 1 | 0.1 | 0.2
3229 | 30/07/2025 10:46:23.614 | 98.28 | 80 | 100 | 70 | 52 | 28.72 | 9.279 | 7.124 | 134.522 | 30.157 | 28.536 | 28.524 | 603.005 | 26.151 | 27.119 | 1283.169 | 27.199 | 27.443 | 36.613 | 30.001 | 2.7 | 2.6 | 0.6 | 1.1 | 0.3
3230 | 30/07/2025 10:46:25.250 | 98.904 | 82 | 100 | 70 | 52 | 28.574 | 9.128 | 7.118 | 134.776 | 30.166 | 28.535 | 28.582 | 603.352 | 26.156 | 27.103 | 1274.765 | 27.207 | 27.457 | 36.574 | 30.001 | 2.5 | 4.1 | 0.3 | 0 | 0.3
3231 | 30/07/2025 10:46:26.886 | 99.192 | 82 | 100 | 70 | 53 | 31.601 | 9.41 | 7.124 | 134.318 | 30.153 | 28.573 | 28.576 | 603.091 | 26.14 | 27.098 | 1279.058 | 27.228 | 27.435 | 36.54 | 32.001 | 3.4 | 4.1 | 0.6 | 0 | 0.3
3232 | 30/07/2025 10:46:28.521 | 99.264 | 81 | 100 | 70 | 52 | 31.053 | 9.308 | 7.123 | 134.767 | 30.153 | 28.546 | 28.559 | 603.052 | 26.143 | 27.099 | 1283.175 | 27.188 | 27.44 | 36.668 | 26.001 | 3.4 | 2.4 | 0 | 0.5 | 0.3
3233 | 30/07/2025 10:46:30.158 | 100.152 | 83 | 100 | 70 | 52 | 27.533 | 9.13 | 7.07 | 134.659 | 30.154 | 28.548 | 28.547 | 603.29 | 26.138 | 27.082 | 1287.27 | 27.197 | 27.599 | 36.564 | 26.001 | 3.4 | 2.4 | 0 | 0.5 | 0.3
3234 | 30/07/2025 10:46:31.794 | 99.864 | 83 | 100 | 70 | 52 | 31.671 | 9.222 | 7.068 | 134.786 | 30.153 | 28.529 | 28.554 | 603.317 | 26.169 | 27.097 | 1284.695 | 27.199 | 27.598 | 36.72 | 25.001 | 1.9 | 2.4 | 1.8 | 0.7 | 0.3
3235 | 30/07/2025 10:46:33.429 | 100.032 | 82 | 100 | 70 | 52 | 28.207 | 9.299 | 7.085 | 134.654 | 30.153 | 28.538 | 28.588 | 603.373 | 26.163 | 27.089 | 1297.151 | 27.215 | 27.447 | 36.628 | 27.001 | 2.7 | 1.5 | 0.7 | 0.9 | 0.3
3236 | 30/07/2025 10:46:35.478 | 99.768 | 82 | 100 | 71 | 52 | 29.104 | 9.15 | 7.089 | 134.415 | 30.149 | 28.553 | 28.57 | 603.247 | 26.16 | 27.121 | 1294.754 | 27.202 | 27.46 | 36.521 | 28.001 | 1.8 | 1.5 | 0.9 | 0 | 0.2
3237 | 30/07/2025 10:46:37.114 | 100.272 | 83 | 100 | 70 | 52 | 31.654 | 9.124 | 7.088 | 134.777 | 30.157 | 28.546 | 28.567 | 603.269 | 26.168 | 27.108 | 1287.844 | 27.174 | 27.465 | 38.436 | 31.001 | 1.9 | 0.9 | 0.7 | 0.6 | 0.2
3238 | 30/07/2025 10:46:38.751 | 100.968 | 84 | 100 | 71 | 52 | 30.509 | 9.128 | 7.118 | 134.367 | 30.131 | 28.547 | 28.546 | 603.155 | 26.15 | 27.116 | 1293.072 | 27.226 | 27.45 | 36.68 | 30.001 | 4.1 | 0.9 | 0.3 | 0.6 | 0.2
3239 | 30/07/2025 10:46:40.386 | 100.848 | 83 | 100 | 70 | 52 | 27.512 | 9.299 | 7.121 | 134.709 | 30.146 | 28.528 | 28.574 | 603.213 | 26.164 | 27.14 | 1295.409 | 27.204 | 27.44 | 36.668 | 30.001 | 4.1 | 0.9 | 0.3 | 0.6 | 0.2
3240 | 30/07/2025 10:46:42.022 | 100.704 | 83 | 100 | 70 | 52 | 30.809 | 9.217 | 7.122 | 134.45 | 30.123 | 28.551 | 28.561 | 603.162 | 26.159 | 27.114 | 1287.6 | 27.208 | 27.435 | 36.341 | 27.001 | 1.2 | 2.3 | 0.6 | 0.5 | 0.2
3241 | 30/07/2025 10:46:43.656 | 100.872 | 84 | 100 | 70 | 53 | 31.769 | 9.299 | 7.088 | 134.631 | 30.14 | 28.55 | 28.561 | 603.051 | 26.153 | 27.132 | 1290.459 | 27.192 | 27.458 | 36.771 | 30.001 | 2.4 | 2.3 | 1 | 0.2 | 0.3
3242 | 30/07/2025 10:46:45.290 | 100.344 | 82 | 100 | 71 | 52 | 29.782 | 9.238 | 7.088 | 134.59 | 30.133 | 28.55 | 28.548 | 603.237 | 26.161 | 27.111 | 1294.31 | 27.189 | 27.47 | 36.613 | 27.001 | 3.6 | 2.5 | 0.7 | 0 | 0.3
3243 | 30/07/2025 10:46:46.925 | 99.96 | 83 | 100 | 70 | 52 | 31.687 | 9.205 | 7.087 | 134.61 | 30.139 | 28.525 | 28.552 | 603.266 | 26.153 | 27.111 | 1296.834 | 27.212 | 27.606 | 36.684 | 28.001 | 3.4 | 2.5 | 0.6 | 1 | 0.2
3244 | 30/07/2025 10:46:48.559 | 100.44 | 84 | 100 | 70 | 52 | 29.999 | 8.988 | 7.085 | 134.51 | 30.157 | 28.543 | 28.593 | 603.256 | 26.152 | 27.117 | 1301.691 | 27.203 | 27.574 | 36.488 | 30.001 | 2.5 | 2.5 | 0.6 | 0.7 | 0.3
3245 | 30/07/2025 10:46:50.194 | 100.248 | 86 | 100 | 71 | 52 | 27.763 | 9.204 | 7.136 | 134.358 | 30.155 | 28.56 | 28.568 | 603.25 | 26.153 | 27.125 | 1306.694 | 27.226 | 27.447 | 38.317 | 30.001 | 2.5 | 2.5 | 0.6 | 0.7 | 0.3
3246 | 30/07/2025 10:46:51.829 | 99.528 | 83 | 100 | 70 | 52 | 31.195 | 9.374 | 7.148 | 134.904 | 30.175 | 28.544 | 28.558 | 603.2 | 26.167 | 27.123 | 1308.749 | 27.181 | 27.455 | 38.564 | 25.001 | 2.7 | 2.5 | 0.7 | 0.5 | 0.3
3247 | 30/07/2025 10:46:53.467 | 99.072 | 82 | 100 | 70 | 51 | 27.608 | 9.141 | 7.152 | 134.641 | 30.173 | 28.555 | 28.54 | 603.24 | 26.154 | 27.12 | 1312.638 | 27.195 | 27.454 | 38.423 | 32.001 | 2.5 | 1.9 | 0.1 | 0.6 | 0.3
3248 | 30/07/2025 10:46:55.102 | 98.832 | 83 | 100 | 70 | 52 | 30.303 | 9.283 | 7.152 | 134.829 | 30.174 | 28.526 | 28.556 | 603.111 | 26.166 | 27.118 | 1308.27 | 27.207 | 27.455 | 38.319 | 27.001 | 1.9 | 1.9 | 0 | 0.1 | 0.2
3249 | 30/07/2025 10:46:56.737 | 99.096 | 82 | 100 | 70 | 52 | 31.757 | 9.292 | 7.151 | 134.541 | 30.17 | 28.559 | 28.575 | 602.02 | 26.132 | 27.106 | 1294.399 | 27.214 | 27.444 | 38.278 | 28.001 | 3.2 | 2.3 | 0.6 | 0.5 | 0.2
3250 | 30/07/2025 10:46:58.373 | 98.376 | 81 | 100 | 70 | 54 | 29.476 | 9.429 | 7.189 | 134.538 | 30.161 | 28.551 | 28.558 | 601.755 | 26.154 | 27.114 | 1277.372 | 27.203 | 27.536 | 38.465 | 28.001 | 3.2 | 2.3 | 0.6 | 0.5 | 0.2
3251 | 30/07/2025 10:47:00.012 | 98.568 | 82 | 100 | 71 | 53 | 28.137 | 9.291 | 7.187 | 134.83 | 30.156 | 28.548 | 28.556 | 601.914 | 26.153 | 27.088 | 1274.632 | 27.179 | 27.59 | 38.544 | 28.001 | 3.5 | 2.3 | 1.2 | 0.8 | 0.2
3252 | 30/07/2025 10:47:01.649 | 99.432 | 84 | 99 | 71 | 53 | 30.591 | 9.285 | 7.189 | 134.532 | 30.164 | 28.54 | 28.54 | 601.907 | 26.148 | 27.093 | 1274.286 | 27.202 | 27.598 | 38.469 | 26.001 | 2.8 | 2 | 0.6 | 0.7 | 0.2
3253 | 30/07/2025 10:47:03.282 | 100.128 | 84 | 100 | 71 | 52 | 27.559 | 9.214 | 7.184 | 134.57 | 30.154 | 28.521 | 28.576 | 602.025 | 26.124 | 27.067 | 1286.373 | 27.21 | 27.597 | 38.212 | 24.001 | 3 | 2 | 2.2 | 0 | 0.2
3254 | 30/07/2025 10:47:04.918 | 100.248 | 83 | 100 | 70 | 52 | 30.779 | 9.289 | 7.179 | 134.39 | 30.141 | 28.558 | 28.567 | 602.171 | 26.147 | 27.097 | 1284.806 | 27.225 | 27.596 | 37.806 | 28.001 | 2.5 | 1.6 | 2.3 | 0.5 | 0.2
3255 | 30/07/2025 10:47:06.552 | 99.72 | 84 | 100 | 70 | 52 | 31.757 | 9.29 | 7.153 | 134.868 | 30.167 | 28.546 | 28.565 | 601.966 | 26.185 | 27.107 | 1277.871 | 27.188 | 27.598 | 36.754 | 22.001 | 3 | 1.6 | 2 | 0.5 | 0.2
3256 | 30/07/2025 10:47:08.189 | 98.472 | 82 | 100 | 70 | 52 | 28.722 | 8.994 | 7.135 | 134.767 | 30.141 | 28.544 | 28.547 | 602.057 | 26.151 | 27.107 | 1281.648 | 27.19 | 27.588 | 38.536 | 22.001 | 3 | 1.6 | 2 | 0.5 | 0.2
3257 | 30/07/2025 10:47:09.820 | 98.736 | 81 | 100 | 70 | 52 | 28.584 | 8.989 | 7.135 | 134.462 | 30.145 | 28.521 | 28.564 | 601.89 | 26.17 | 27.125 | 1281.288 | 27.215 | 27.605 | 38.578 | 19 | 2 | 2.1 | 1.4 | 0.8 | 0.2
3258 | 30/07/2025 10:47:11.455 | 98.064 | 81 | 100 | 71 | 52 | 29.86 | 9.138 | 7.133 | 134.73 | 30.139 | 28.53 | 28.573 | 602.065 | 26.173 | 27.118 | 1287.407 | 27.221 | 27.533 | 38.324 | 24.001 | 2.2 | 2.1 | 0.7 | 0.8 | 0.2
3259 | 30/07/2025 10:47:13.093 | 98.136 | 80 | 100 | 70 | 52 | 27.698 | 9.13 | 7.138 | 134.515 | 30.144 | 28.554 | 28.565 | 601.826 | 26.166 | 27.128 | 1282.354 | 27.202 | 27.442 | 38.241 | 25.001 | 3.6 | 2.3 | 2.1 | 0.4 | 0.2
3260 | 30/07/2025 10:47:14.727 | 98.376 | 82 | 100 | 71 | 52 | 31.206 | 9.13 | 7.134 | 134.641 | 30.143 | 28.548 | 28.569 | 602.16 | 26.148 | 27.121 | 1287.176 | 27.184 | 27.473 | 38.441 | 27.001 | 2.1 | 2.3 | 0.8 | 0 | 0.1
3261 | 30/07/2025 10:47:16.362 | 98.376 | 82 | 100 | 70 | 52 | 31.728 | 9.209 | 7.136 | 134.571 | 30.122 | 28.548 | 28.533 | 602.081 | 26.148 | 27.127 | 1286.996 | 27.214 | 27.456 | 36.852 | 27.001 | 2.1 | 2.3 | 0.8 | 0 | 0.1
3262 | 30/07/2025 10:47:17.997 | 98.256 | 81 | 100 | 69 | 52 | 28.2 | 9.218 | 7.134 | 134.684 | 30.156 | 28.523 | 28.584 | 602.103 | 26.182 | 27.116 | 1278.199 | 27.204 | 27.59 | 36.722 | 25.001 | 2 | 2.3 | 0 | 0.5 | 0.1
3263 | 30/07/2025 10:47:19.632 | 98.256 | 83 | 100 | 70 | 51 | 31.75 | 9.254 | 7.136 | 134.314 | 30.128 | 28.542 | 28.559 | 601.928 | 26.145 | 27.122 | 1274.657 | 27.211 | 27.589 | 36.591 | 26.001 | 2.8 | 2.3 | 0.6 | 0.8 | 0.1
3264 | 30/07/2025 10:47:21.267 | 99.336 | 83 | 100 | 70 | 52 | 29.336 | 9.285 | 7.135 | 134.787 | 30.159 | 28.545 | 28.572 | 601.84 | 26.171 | 27.116 | 1277.202 | 27.201 | 27.438 | 38.289 | 29.001 | 1.6 | 3 | 1.2 | 0.6 | 0.2
3265 | 30/07/2025 10:47:22.904 | 98.952 | 82 | 100 | 69 | 52 | 28.182 | 9.147 | 7.152 | 134.641 | 30.139 | 28.547 | 28.554 | 601.948 | 26.166 | 27.117 | 1282.39 | 27.194 | 27.475 | 38.494 | 26.001 | 2 | 3 | 0.3 | 0 | 0.2
3266 | 30/07/2025 10:47:24.538 | 98.904 | 83 | 100 | 71 | 52 | 31.434 | 9.128 | 7.087 | 134.585 | 30.155 | 28.536 | 28.543 | 601.974 | 26.161 | 27.136 | 1276.801 | 27.218 | 27.548 | 38.503 | 27.001 | 1 | 3.2 | 0 | 0.6 | 0.2
3267 | 30/07/2025 10:47:26.181 | 98.76 | 83 | 100 | 69 | 52 | 31.48 | 9.425 | 7.067 | 134.552 | 30.159 | 28.539 | 28.562 | 602.148 | 26.161 | 27.105 | 1278.678 | 27.209 | 27.578 | 38.365 | 27.001 | 1 | 3.2 | 0 | 0.6 | 0.2
3268 | 30/07/2025 10:47:27.817 | 99.456 | 82 | 100 | 70 | 52 | 27.824 | 9.136 | 7.072 | 134.344 | 30.169 | 28.566 | 28.564 | 602.104 | 26.143 | 27.111 | 1287.303 | 27.226 | 27.445 | 38.298 | 27.001 | 2.9 | 3.2 | 0.9 | 1.4 | 0.1
3269 | 30/07/2025 10:47:29.457 | 99.336 | 82 | 100 | 71 | 50 | 31.792 | 8.984 | 7.07 | 134.776 | 30.168 | 28.551 | 28.568 | 602.123 | 26.151 | 27.106 | 1285.919 | 27.199 | 27.459 | 38.523 | 31.001 | 2.5 | 2.5 | 1.6 | 1.3 | 0.1
3270 | 30/07/2025 10:47:31.095 | 99.288 | 84 | 100 | 70 | 52 | 28.911 | 9.133 | 7.071 | 134.558 | 30.146 | 28.545 | 28.541 | 601.943 | 26.137 | 27.122 | 1269.321 | 27.193 | 27.454 | 38.513 | 29.001 | 4.9 | 2.5 | 1 | 0.3 | 0.2
3271 | 30/07/2025 10:47:32.744 | 99.552 | 83 | 100 | 70 | 53 | 28.633 | 9.205 | 7.058 | 134.733 | 30.176 | 28.534 | 28.567 | 601.976 | 26.161 | 27.113 | 1270.247 | 27.208 | 27.488 | 38.455 | 26.001 | 4.2 | 1.8 | 1.3 | 0.8 | 0.2
3272 | 30/07/2025 10:47:34.380 | 99.648 | 85 | 100 | 70 | 52 | 31.666 | 9.123 | 7.059 | 134.426 | 30.153 | 28.552 | 28.579 | 601.999 | 26.135 | 27.088 | 1277.129 | 27.216 | 27.598 | 38.282 | 26.001 | 4.2 | 1.8 | 1.3 | 0.8 | 0.2
3273 | 30/07/2025 10:47:36.019 | 100.104 | 85 | 100 | 70 | 52 | 31.145 | 9.43 | 7.063 | 133.012 | 30.147 | 28.555 | 28.566 | 601.796 | 26.137 | 27.099 | 1279.339 | 27.2 | 27.584 | 38.384 | 29.001 | 3.2 | 1.8 | 0.6 | 0.4 | 0.2
3274 | 30/07/2025 10:47:37.656 | 100.464 | 84 | 100 | 70 | 52 | 27.647 | 9.287 | 7.06 | 133.178 | 30.166 | 28.542 | 28.574 | 602.107 | 26.153 | 27.084 | 1282.326 | 27.183 | 27.598 | 38.473 | 24.001 | 2.2 | 2.3 | 1 | 0 | 0.1
3275 | 30/07/2025 10:47:39.291 | 100.608 | 84 | 100 | 70 | 52 | 31.718 | 9.133 | 7.061 | 133.202 | 30.157 | 28.54 | 28.511 | 601.915 | 26.161 | 27.103 | 1285.829 | 27.186 | 27.596 | 38.411 | 25.001 | 2.4 | 2.3 | 1.3 | 0.5 | 0.1
3276 | 30/07/2025 10:47:40.927 | 100.992 | 84 | 100 | 71 | 53 | 28.294 | 9.15 | 7.057 | 133.079 | 30.151 | 28.527 | 28.571 | 602.008 | 26.153 | 27.085 | 1302.14 | 27.209 | 27.592 | 38.559 | 25.001 | 4.8 | 1.4 | 0.8 | 0.8 | 0.1
3277 | 30/07/2025 10:47:42.568 | 100.728 | 84 | 100 | 70 | 52 | 29.104 | 8.998 | 7.06 | 132.905 | 30.144 | 28.559 | 28.563 | 603.149 | 26.158 | 27.111 | 1296.443 | 27.212 | 27.582 | 38.207 | 22.001 | 3.3 | 1.4 | 0.7 | 0.3 | 0.1
3278 | 30/07/2025 10:47:44.204 | 101.016 | 86 | 100 | 70 | 53 | 31.722 | 9.223 | 7.121 | 133.243 | 30.166 | 28.551 | 28.571 | 602.151 | 26.183 | 27.107 | 1290.729 | 27.192 | 27.599 | 38.58 | 22.001 | 3.3 | 1.4 | 0.7 | 0.3 | 0.1
3279 | 30/07/2025 10:47:45.843 | 101.28 | 84 | 100 | 70 | 52 | 30.583 | 9.218 | 7.023 | 134.731 | 30.143 | 28.55 | 28.566 | 603.097 | 26.166 | 27.12 | 1292.751 | 27.198 | 27.615 | 38.63 | 30.001 | 2.7 | 3.2 | 0 | 0 | 0.1
3280 | 30/07/2025 10:47:47.480 | 101.472 | 84 | 100 | 71 | 52 | 31.488 | 9.159 | 6.933 | 134.681 | 30.139 | 28.535 | 28.549 | 603.273 | 26.152 | 27.128 | 1292.347 | 27.201 | 27.599 | 38.522 | 25.001 | 2 | 3.2 | 1.2 | 0.5 | 0.1
3281 | 30/07/2025 10:47:49.118 | 101.256 | 84 | 100 | 70 | 52 | 31.568 | 9.288 | 6.956 | 134.81 | 30.121 | 28.53 | 28.578 | 603.275 | 26.164 | 27.118 | 1281.267 | 27.225 | 27.6 | 38.64 | 34.001 | 2 | 2.8 | 0.3 | 0.8 | 0.1
3282 | 30/07/2025 10:47:50.757 | 101.208 | 85 | 100 | 71 | 52 | 27.828 | 9.287 | 7.005 | 134.416 | 30.13 | 28.554 | 28.559 | 603.048 | 26.161 | 27.126 | 1283.6 | 27.211 | 27.434 | 38.232 | 30.001 | 2.2 | 2.8 | 0.6 | 1.1 | 0.1
3283 | 30/07/2025 10:47:52.391 | 100.512 | 83 | 100 | 69 | 52 | 29.671 | 9.288 | 7.004 | 134.705 | 30.141 | 28.558 | 28.58 | 603.255 | 26.147 | 27.119 | 1279.709 | 27.192 | 27.611 | 38.42 | 30.001 | 2.2 | 2.8 | 0.6 | 1.1 | 0.1
3284 | 30/07/2025 10:47:54.026 | 100.392 | 84 | 100 | 70 | 52 | 31.764 | 9.294 | 6.95 | 134.535 | 30.136 | 28.55 | 28.536 | 603.16 | 26.155 | 27.13 | 1276.837 | 27.208 | 27.46 | 38.425 | 27.001 | 1.6 | 2 | 1.2 | 0.1 | 0.1
3285 | 30/07/2025 10:47:55.665 | 100.128 | 83 | 100 | 70 | 52 | 30.02 | 8.849 | 6.916 | 134.839 | 30.156 | 28.527 | 28.575 | 603.255 | 26.165 | 27.113 | 1287.313 | 27.208 | 27.598 | 36.551 | 29.001 | 2.4 | 2 | 2.4 | 0.5 | 0.1
3286 | 30/07/2025 10:47:57.301 | 99.936 | 83 | 100 | 70 | 53 | 31.576 | 9.128 | 6.937 | 134.488 | 30.155 | 28.545 | 28.558 | 603.036 | 26.153 | 27.139 | 1287.224 | 27.223 | 27.584 | 36.502 | 27.001 | 4.5 | 3 | 1.9 | 0.9 | 0.1
3287 | 30/07/2025 10:47:58.945 | 99.648 | 82 | 100 | 71 | 52 | 31.164 | 9.283 | 7.004 | 134.485 | 30.179 | 28.549 | 28.57 | 603.407 | 26.161 | 27.108 | 1282.588 | 27.199 | 27.593 | 37.586 | 27.001 | 2.2 | 3 | 2 | 0.6 | 0.1
3288 | 30/07/2025 10:48:00.587 | 99.72 | 85 | 100 | 70 | 52 | 27.58 | 9.481 | 7.004 | 134.59 | 30.158 | 28.553 | 28.549 | 603.29 | 26.149 | 27.113 | 1282.593 | 27.191 | 27.621 | 38.432 | 25.001 | 2.5 | 3.2 | 1.1 | 0.8 | 0.1
3289 | 30/07/2025 10:48:02.226 | 99.504 | 83 | 100 | 71 | 52 | 30.267 | 9.131 | 7.018 | 134.779 | 30.162 | 28.536 | 28.534 | 603.116 | 26.157 | 27.12 | 1277.568 | 27.208 | 27.6 | 38.531 | 25.001 | 2.5 | 3.2 | 1.1 | 0.8 | 0.1
3290 | 30/07/2025 10:48:03.861 | 99.744 | 83 | 100 | 70 | 52 | 31.767 | 8.983 | 7.069 | 134.596 | 30.164 | 28.532 | 28.593 | 603.28 | 26.154 | 27.1 | 1274.832 | 27.212 | 27.592 | 36.691 | 28.001 | 1.7 | 3.2 | 0.2 | 0.6 | 0
3291 | 30/07/2025 10:48:05.499 | 99.168 | 81 | 100 | 70 | 52 | 29.257 | 9.135 | 7.075 | 134.376 | 30.164 | 28.551 | 28.572 | 603.127 | 26.16 | 27.115 | 1270.073 | 27.209 | 27.582 | 36.583 | 26.001 | 1.8 | 2.7 | 1.2 | 1.7 | 0
3292 | 30/07/2025 10:48:07.133 | 98.568 | 82 | 100 | 71 | 52 | 31.74 | 9.397 | 7.135 | 134.671 | 30.16 | 28.56 | 28.563 | 603.156 | 26.141 | 27.105 | 1268.37 | 27.196 | 27.6 | 36.582 | 26.001 | 2 | 2.7 | 0.3 | 0.2 | 0.1
3293 | 30/07/2025 10:48:08.781 | 98.64 | 82 | 100 | 71 | 52 | 30.696 | 9.471 | 7.123 | 134.764 | 30.154 | 28.541 | 28.536 | 603.105 | 26.128 | 27.111 | 1259.996 | 27.192 | 27.602 | 36.777 | 22.001 | 3 | 3.3 | 0.6 | 0.5 | 0
3294 | 30/07/2025 10:48:10.417 | 98.472 | 82 | 100 | 70 | 52 | 27.673 | 9.149 | 7.121 | 134.649 | 30.163 | 28.535 | 28.545 | 603.36 | 26.146 | 27.096 | 1265.343 | 27.208 | 27.599 | 36.681 | 23.001 | 3.1 | 3.3 | 0.7 | 0 | 0
3295 | 30/07/2025 10:48:12.068 | 98.448 | 81 | 100 | 70 | 52 | 30.878 | 9.297 | 7.133 | 134.414 | 30.146 | 28.547 | 28.582 | 603.215 | 26.142 | 27.074 | 1269.022 | 27.227 | 27.595 | 36.474 | 23.001 | 3.1 | 3.3 | 0.7 | 0 | 0
3296 | 30/07/2025 10:48:13.704 | 98.904 | 81 | 100 | 71 | 52 | 31.861 | 9.152 | 7.154 | 134.549 | 30.153 | 28.551 | 28.564 | 603.222 | 26.156 | 27.106 | 1267.096 | 27.28 | 27.587 | 36.431 | 25.001 | 3.3 | 2.1 | 1 | 0 | 0.1
3297 | 30/07/2025 10:48:15.342 | 99.336 | 82 | 100 | 70 | 52 | 29.764 | 9.283 | 7.152 | 134.718 | 30.147 | 28.56 | 28.555 | 603.267 | 26.148 | 27.246 | 1267.25 | 27.208 | 27.605 | 36.597 | 30.001 | 4 | 2.1 | 0.6 | 0.6 | 0
3298 | 30/07/2025 10:48:16.977 | 99.672 | 82 | 99 | 70 | 52 | 31.768 | 9.133 | 7.172 | 134.65 | 30.154 | 28.54 | 28.529 | 603.174 | 26.17 | 27.259 | 1268.421 | 27.187 | 27.594 | 36.585 | 25.001 | 3.1 | 0.6 | 1 | 0.8 | 0
3299 | 30/07/2025 10:48:18.612 | 99.144 | 82 | 100 | 71 | 53 | 30.086 | 9.288 | 7.186 | 134.689 | 30.151 | 28.533 | 28.556 | 603.258 | 26.15 | 27.248 | 1287.257 | 27.212 | 27.604 | 36.633 | 30.001 | 2.6 | 0.6 | 1.5 | 0 | 0.1
3300 | 30/07/2025 10:48:20.247 | 99.48 | 83 | 100 | 70 | 52 | 27.833 | 9.2 | 7.187 | 134.42 | 30.134 | 28.549 | 28.566 | 601.847 | 26.155 | 27.269 | 1289.31 | 27.213 | 27.594 | 36.457 | 30.001 | 2.6 | 0.6 | 1.5 | 0 | 0.1
3301 | 30/07/2025 10:48:21.885 | 99.336 | 82 | 100 | 70 | 51 | 31.202 | 9.423 | 7.186 | 134.82 | 30.153 | 28.55 | 28.57 | 602.022 | 26.16 | 27.263 | 1285.098 | 27.188 | 27.6 | 36.568 | 22.001 | 1.8 | 2 | 0.9 | 0 | 0.1
3302 | 30/07/2025 10:48:23.522 | 99.744 | 81 | 99 | 70 | 52 | 27.74 | 9.431 | 7.189 | 134.718 | 30.13 | 28.547 | 28.547 | 601.904 | 26.153 | 27.282 | 1287.108 | 27.186 | 27.61 | 36.854 | 24.001 | 2.6 | 2 | 1.1 | 0.5 | 0.1
3303 | 30/07/2025 10:48:25.392 | 99.936 | 82 | 100 | 70 | 52 | 28.312 | 9.185 | 7.205 | 134.827 | 30.136 | 28.522 | 28.557 | 601.962 | 26.163 | 27.272 | 1284.657 | 27.213 | 27.602 | 36.738 | 22.001 | 2.3 | 2.3 | 0.6 | 1.3 | 0.1
3304 | 30/07/2025 10:48:27.029 | 99.744 | 82 | 100 | 70 | 52 | 31.821 | 9.216 | 7.197 | 134.616 | 30.131 | 28.535 | 28.573 | 601.969 | 26.156 | 27.264 | 1282.434 | 27.232 | 27.605 | 36.571 | 25.001 | 0.9 | 2.3 | 0.6 | 0.5 | 0.1
3305 | 30/07/2025 10:48:28.666 | 99.312 | 83 | 100 | 70 | 52 | 29.413 | 9.163 | 7.154 | 134.733 | 30.141 | 28.548 | 28.559 | 602.038 | 26.161 | 27.261 | 1279.18 | 27.313 | 27.565 | 36.606 | 26.001 | 1.7 | 2.7 | 1.2 | 0 | 0.1
3306 | 30/07/2025 10:48:30.302 | 99.552 | 82 | 100 | 70 | 52 | 28.047 | 9.155 | 7.151 | 134.664 | 30.15 | 28.559 | 28.571 | 601.967 | 26.161 | 27.254 | 1286.961 | 27.193 | 27.62 | 36.654 | 26.001 | 1.7 | 2.7 | 1.2 | 0 | 0.1
3307 | 30/07/2025 10:48:31.941 | 98.592 | 82 | 100 | 70 | 52 | 31.41 | 9.189 | 7.152 | 134.628 | 30.144 | 28.548 | 28.536 | 601.868 | 26.143 | 27.283 | 1285.704 | 27.233 | 27.601 | 36.655 | 27.001 | 2.4 | 2.7 | 0.6 | 0 | 0.1
3308 | 30/07/2025 10:48:33.576 | 98.424 | 82 | 100 | 70 | 52 | 31.532 | 9.286 | 7.151 | 134.754 | 30.175 | 28.531 | 28.572 | 601.885 | 26.184 | 27.259 | 1277.518 | 27.206 | 27.6 | 36.837 | 28.001 | 3.9 | 1.6 | 0.7 | 0 | 0.2
3309 | 30/07/2025 10:48:35.211 | 98.16 | 81 | 100 | 71 | 52 | 30.731 | 9.151 | 7.152 | 134.463 | 30.164 | 28.538 | 28.564 | 601.78 | 26.151 | 27.266 | 1277.416 | 27.211 | 27.587 | 36.703 | 26.001 | 3.3 | 1.6 | 2.5 | 0.5 | 0.2
3310 | 30/07/2025 10:48:36.845 | 97.896 | 81 | 100 | 71 | 52 | 31.826 | 9.284 | 7.187 | 134.597 | 30.165 | 28.556 | 28.581 | 602.175 | 26.159 | 27.252 | 1289.202 | 27.205 | 27.586 | 38.384 | 25.001 | 3.4 | 2.9 | 1.2 | 0.9 | 0.1
3311 | 30/07/2025 10:48:38.480 | 98.184 | 81 | 100 | 71 | 52 | 28.771 | 9.41 | 7.231 | 134.657 | 30.16 | 28.559 | 28.555 | 602.136 | 26.144 | 27.248 | 1294.474 | 27.197 | 27.613 | 38.424 | 32.001 | 3.8 | 2.9 | 0.7 | 1.1 | 0.1
3312 | 30/07/2025 10:48:40.114 | 98.496 | 81 | 100 | 71 | 52 | 28.674 | 9.171 | 7.222 | 134.503 | 30.156 | 28.532 | 28.545 | 602.022 | 26.156 | 27.257 | 1306.361 | 27.206 | 27.594 | 36.753 | 32.001 | 3.8 | 2.9 | 0.7 | 1.1 | 0.1
3313 | 30/07/2025 10:48:41.750 | 97.776 | 81 | 100 | 71 | 51 | 31.641 | 9.214 | 7.133 | 134.635 | 30.166 | 28.536 | 28.587 | 602.088 | 26.139 | 27.243 | 1302.488 | 27.216 | 27.6 | 36.658 | 30.001 | 2.1 | 3.2 | 0.6 | 0.6 | 0.1
3314 | 30/07/2025 10:48:43.386 | 98.184 | 81 | 100 | 70 | 52 | 31.158 | 9.217 | 7.137 | 134.455 | 30.155 | 28.547 | 28.563 | 601.709 | 26.142 | 27.25 | 1300.486 | 27.219 | 27.582 | 36.535 | 25.001 | 2.4 | 3.2 | 0.9 | 0.5 | 0.2
3315 | 30/07/2025 10:48:45.021 | 98.376 | 82 | 100 | 71 | 51 | 31.293 | 9.392 | 7.135 | 134.574 | 30.153 | 28.557 | 28.572 | 602.181 | 26.144 | 27.224 | 1297.628 | 27.203 | 27.608 | 37.038 | 25.001 | 2.1 | 2.2 | 0.7 | 0.9 | 0.2
3316 | 30/07/2025 10:48:46.654 | 98.76 | 82 | 100 | 70 | 52 | 31.775 | 9.295 | 7.137 | 134.685 | 30.155 | 28.546 | 28.544 | 601.9 | 26.155 | 27.243 | 1294.696 | 27.187 | 27.614 | 38.675 | 26.001 | 3.5 | 2.2 | 1.2 | 0.4 | 0.2
3317 | 30/07/2025 10:48:48.286 | 98.592 | 82 | 100 | 71 | 52 | 28.342 | 9.156 | 7.133 | 134.597 | 30.164 | 28.539 | 28.554 | 602.044 | 26.147 | 27.237 | 1297.087 | 27.21 | 27.599 | 38.506 | 26.001 | 3.5 | 2.2 | 1.2 | 0.4 | 0.2
3318 | 30/07/2025 10:48:49.921 | 98.208 | 82 | 100 | 71 | 52 | 29.193 | 9.144 | 7.151 | 134.538 | 30.146 | 28.552 | 28.587 | 602.02 | 26.155 | 27.258 | 1287.42 | 27.233 | 27.599 | 38.386 | 25.001 | 2.7 | 2 | 1.5 | 0.5 | 0.3
3319 | 30/07/2025 10:48:51.553 | 99.072 | 82 | 100 | 70 | 52 | 31.727 | 9.136 | 7.135 | 134.701 | 30.157 | 28.553 | 28.562 | 601.859 | 26.183 | 27.275 | 1296.915 | 27.206 | 27.581 | 38.372 | 23.001 | 3.3 | 2 | 1.6 | 1 | 0.3
3320 | 30/07/2025 10:48:53.190 | 99.12 | 82 | 100 | 70 | 52 | 28.069 | 9.13 | 7.135 | 134.627 | 30.138 | 28.553 | 28.557 | 601.903 | 26.16 | 27.274 | 1305.184 | 27.344 | 27.617 | 38.552 | 27.001 | 2.2 | 2.6 | 1.2 | 0.8 | 0.4
3321 | 30/07/2025 10:48:54.825 | 99.24 | 81 | 100 | 70 | 52 | 31.546 | 9.288 | 7.202 | 134.851 | 30.145 | 28.542 | 28.549 | 601.995 | 26.168 | 27.252 | 1306.832 | 27.181 | 27.591 | 38.439 | 24.001 | 1.7 | 2.6 | 1 | 0.7 | 0.4
3322 | 30/07/2025 10:48:56.460 | 99.768 | 83 | 100 | 70 | 52 | 31.59 | 9.237 | 7.207 | 134.517 | 30.167 | 28.523 | 28.553 | 602.099 | 26.159 | 27.265 | 1308.006 | 27.252 | 27.615 | 38.503 | 23.001 | 2.2 | 3 | 1.3 | 0.5 | 0.3
3323 | 30/07/2025 10:48:58.100 | 99.648 | 84 | 100 | 70 | 52 | 27.988 | 9.286 | 7.088 | 134.35 | 30.142 | 28.545 | 28.561 | 602.029 | 26.151 | 27.29 | 1307.475 | 27.209 | 27.588 | 38.422 | 23.001 | 2.2 | 3 | 1.3 | 0.5 | 0.3
3324 | 30/07/2025 10:48:59.732 | 99.552 | 83 | 100 | 72 | 52 | 29.703 | 9.285 | 7.107 | 134.695 | 30.133 | 28.547 | 28.562 | 602.099 | 26.158 | 27.252 | 1301.384 | 27.329 | 27.594 | 38.372 | 29.001 | 2.9 | 3 | 1.2 | 0.5 | 0.3
3325 | 30/07/2025 10:49:01.365 | 99.792 | 83 | 100 | 70 | 52 | 28.821 | 9.333 | 7.126 | 134.817 | 30.127 | 28.551 | 28.553 | 601.869 | 26.157 | 27.267 | 1306.866 | 27.185 | 27.615 | 38.705 | 29.001 | 2.7 | 2.9 | 1.3 | 0.5 | 0.3
3326 | 30/07/2025 10:49:02.997 | 99.504 | 84 | 100 | 71 | 51 | 28.541 | 9.285 | 7.087 | 134.81 | 30.146 | 28.541 | 28.56 | 602.071 | 26.148 | 27.261 | 1299.403 | 27.201 | 27.602 | 38.577 | 24.001 | 1.3 | 2.9 | 1.5 | 0.5 | 0.3
3327 | 30/07/2025 10:49:04.635 | 98.952 | 83 | 100 | 69 | 52 | 31.604 | 9.202 | 7.082 | 134.542 | 30.272 | 28.527 | 28.564 | 601.808 | 26.162 | 27.272 | 1295.47 | 27.368 | 27.602 | 38.542 | 28.001 | 1.9 | 1.1 | 1.3 | 0.8 | 0.3
3328 | 30/07/2025 10:49:06.266 | 98.904 | 82 | 100 | 70 | 53 | 31.123 | 8.856 | 7.072 | 134.505 | 30.181 | 28.556 | 28.568 | 602.064 | 26.16 | 27.266 | 1284.502 | 27.343 | 27.578 | 38.481 | 28.001 | 1.9 | 1.1 | 1.3 | 0.8 | 0.3
3329 | 30/07/2025 10:49:07.900 | 99.096 | 83 | 100 | 70 | 51 | 27.589 | 9.157 | 7.058 | 134.522 | 30.303 | 28.561 | 28.569 | 602.154 | 26.16 | 27.255 | 1285.477 | 27.201 | 27.627 | 38.696 | 28.001 | 2.4 | 1.1 | 0.9 | 0.3 | 0.2
3330 | 30/07/2025 10:49:09.635 | 98.784 | 84 | 100 | 70 | 52 | 30.235 | 9.131 | 7.06 | 134.519 | 30.164 | 28.544 | 28.546 | 601.841 | 26.162 | 27.27 | 1289.243 | 27.206 | 27.608 | 38.504 | 23.001 | 3.9 | 3 | 1.3 | 0.5 | 0.2
3331 | 30/07/2025 10:49:11.268 | 99.12 | 82 | 100 | 71 | 52 | 31.761 | 9.101 | 7.058 | 134.757 | 30.174 | 28.532 | 28.58 | 602.059 | 26.152 | 27.242 | 1296.117 | 27.353 | 27.601 | 38.336 | 27.001 | 2.7 | 3 | 1.5 | 0.8 | 0.2
3332 | 30/07/2025 10:49:12.898 | 99.696 | 83 | 100 | 70 | 53 | 29.172 | 9.059 | 7.06 | 134.506 | 30.168 | 28.534 | 28.563 | 601.821 | 26.147 | 27.268 | 1303.383 | 27.31 | 27.583 | 38.325 | 30.001 | 2 | 1.9 | 1.1 | 0.7 | 0.1
3333 | 30/07/2025 10:49:14.533 | 99.12 | 82 | 100 | 71 | 53 | 31.742 | 9.289 | 7.059 | 134.561 | 30.297 | 28.56 | 28.572 | 600.96 | 26.127 | 27.231 | 1311.807 | 27.339 | 27.579 | 38.292 | 25.001 | 1.7 | 1.9 | 0.8 | 0.3 | 0.2
3334 | 30/07/2025 10:49:16.168 | 98.688 | 82 | 100 | 70 | 52 | 30.649 | 9.28 | 7.092 | 134.561 | 30.299 | 28.557 | 28.545 | 600.525 | 26.136 | 27.256 | 1307.353 | 27.228 | 27.618 | 38.489 | 25.001 | 1.7 | 1.9 | 0.8 | 0.3 | 0.2
3335 | 30/07/2025 10:49:17.811 | 98.856 | 82 | 100 | 71 | 52 | 27.65 | 9.137 | 7.122 | 134.589 | 30.307 | 28.536 | 28.532 | 600.573 | 26.148 | 27.238 | 1314.451 | 27.199 | 27.596 | 38.668 | 28.001 | 3 | 3.4 | 1.6 | 0 | 0.2
3336 | 30/07/2025 10:49:19.446 | 98.88 | 84 | 100 | 70 | 52 | 30.824 | 9.173 | 7.119 | 134.686 | 30.295 | 28.527 | 28.572 | 602.045 | 26.153 | 27.225 | 1315.298 | 27.225 | 27.598 | 38.446 | 29.001 | 3.5 | 3.4 | 0.7 | 0.5 | 0.3
3337 | 30/07/2025 10:49:21.084 | 98.832 | 82 | 100 | 71 | 51 | 27.812 | 9.259 | 7.123 | 134.569 | 30.31 | 28.547 | 28.558 | 601.839 | 26.168 | 27.24 | 1309.893 | 27.348 | 27.575 | 38.459 | 27.001 | 5.1 | 3.3 | 0.1 | 0.6 | 0.4
3338 | 30/07/2025 10:49:22.720 | 99.096 | 83 | 100 | 70 | 52 | 29.79 | 9.134 | 7.122 | 134.697 | 30.282 | 28.562 | 28.553 | 601.796 | 26.163 | 27.237 | 1306.67 | 27.352 | 27.603 | 38.513 | 25.001 | 4.4 | 3.3 | 0.7 | 0.8 | 0.4
3339 | 30/07/2025 10:49:24.357 | 99.168 | 82 | 100 | 70 | 52 | 31.766 | 9.132 | 7.075 | 134.734 | 30.295 | 28.547 | 28.547 | 602.09 | 26.156 | 27.263 | 1299.684 | 27.307 | 27.605 | 38.696 | 25.001 | 4.4 | 3.3 | 0.7 | 0.8 | 0.4
3340 | 30/07/2025 10:49:25.997 | 99.144 | 82 | 100 | 70 | 51 | 30.131 | 9.289 | 7.069 | 134.835 | 30.291 | 28.536 | 28.558 | 602.131 | 26.16 | 27.253 | 1307.18 | 27.346 | 27.598 | 38.216 | 29.001 | 2.5 | 3.8 | 2.2 | 0.5 | 0.4
3341 | 30/07/2025 10:49:27.633 | 98.832 | 82 | 100 | 70 | 52 | 27.867 | 9.472 | 7.085 | 134.418 | 30.265 | 28.543 | 28.568 | 600.559 | 26.158 | 27.273 | 1299.32 | 27.369 | 27.595 | 38.293 | 24.001 | 2.6 | 3.8 | 1.1 | 0.6 | 0.3
3342 | 30/07/2025 10:49:29.267 | 98.544 | 83 | 100 | 70 | 52 | 31.32 | 9.389 | 7.098 | 134.564 | 30.294 | 28.55 | 28.565 | 600.569 | 26.169 | 27.271 | 1296.98 | 27.338 | 27.582 | 38.323 | 23.001 | 3.1 | 2.2 | 0.3 | 0.8 | 0.3
3343 | 30/07/2025 10:49:30.902 | 98.4 | 81 | 100 | 70 | 52 | 27.754 | 9.376 | 7.123 | 134.6 | 30.267 | 28.549 | 28.567 | 600.446 | 26.158 | 27.27 | 1296.926 | 27.344 | 27.596 | 38.521 | 26.001 | 2.6 | 2.2 | 0.9 | 0.9 | 0.3
3344 | 30/07/2025 10:49:32.535 | 98.952 | 82 | 100 | 70 | 52 | 30.324 | 9.211 | 7.12 | 134.793 | 30.289 | 28.552 | 28.552 | 601.923 | 26.171 | 27.265 | 1295.074 | 27.329 | 27.603 | 38.476 | 27.001 | 3.4 | 2.3 | 0.1 | 0.2 | 0.4
3345 | 30/07/2025 10:49:34.170 | 98.952 | 84 | 100 | 71 | 52 | 31.8 | 9.312 | 7.121 | 134.684 | 30.266 | 28.535 | 28.567 | 600.593 | 26.152 | 27.256 | 1278.155 | 27.371 | 27.614 | 38.667 | 27.001 | 3.4 | 2.3 | 0.1 | 0.2 | 0.4
3346 | 30/07/2025 10:49:35.805 | 98.256 | 82 | 100 | 71 | 52 | 29.549 | 9.139 | 7.137 | 134.433 | 30.295 | 28.546 | 28.565 | 600.606 | 26.152 | 27.271 | 1283.609 | 27.341 | 27.583 | 38.583 | 32.001 | 3.1 | 2.3 | 1.3 | 0.5 | 0.4
3347 | 30/07/2025 10:49:37.441 | 98.328 | 82 | 100 | 70 | 51 | 28.101 | 9.285 | 7.134 | 134.623 | 30.305 | 28.546 | 28.576 | 600.702 | 26.162 | 27.253 | 1274.705 | 27.339 | 27.596 | 38.496 | 29.001 | 2 | 4.2 | 1.2 | 0.1 | 0.3
3348 | 30/07/2025 10:49:39.076 | 98.328 | 83 | 100 | 70 | 52 | 30.704 | 9.475 | 7.153 | 134.828 | 30.315 | 28.539 | 28.561 | 600.614 | 26.168 | 27.263 | 1277.033 | 27.332 | 27.599 | 38.595 | 28.001 | 3.3 | 4.2 | 1.5 | 0 | 0.3
3349 | 30/07/2025 10:49:40.711 | 98.52 | 82 | 100 | 69 | 51 | 27.618 | 9.292 | 7.152 | 134.678 | 30.319 | 28.542 | 28.562 | 600.654 | 26.147 | 27.235 | 1272.466 | 27.334 | 27.594 | 36.759 | 25.001 | 1.9 | 2.7 | 0.6 | 0.5 | 0.3
3350 | 30/07/2025 10:49:42.347 | 98.28 | 81 | 100 | 70 | 51 | 30.737 | 9.13 | 7.153 | 134.494 | 30.305 | 28.526 | 28.554 | 600.314 | 26.148 | 27.259 | 1272.759 | 27.361 | 27.602 | 36.852 | 25.001 | 1.9 | 2.7 | 0.6 | 0.5 | 0.3
3351 | 30/07/2025 10:49:43.983 | 98.376 | 82 | 100 | 70 | 52 | 31.837 | 9.256 | 7.184 | 134.545 | 30.324 | 28.546 | 28.575 | 600.46 | 26.165 | 27.259 | 1269.751 | 27.336 | 27.583 | 36.415 | 26.001 | 1.7 | 2.7 | 0.6 | 0 | 0.3
3352 | 30/07/2025 10:49:45.619 | 98.808 | 80 | 100 | 70 | 52 | 28.948 | 9.129 | 7.143 | 134.691 | 30.298 | 28.554 | 28.567 | 600.524 | 26.15 | 27.259 | 1273.148 | 27.344 | 27.622 | 36.631 | 28.001 | 4.4 | 3.6 | 0.9 | 0.8 | 0.3
3353 | 30/07/2025 10:49:47.254 | 98.76 | 82 | 100 | 70 | 52 | 28.614 | 9.432 | 7.137 | 134.646 | 30.286 | 28.548 | 28.532 | 600.482 | 26.144 | 27.259 | 1276.853 | 27.177 | 27.61 | 36.567 | 20.001 | 3.2 | 3.6 | 1 | 2 | 0.3
3354 | 30/07/2025 10:49:48.887 | 99.192 | 82 | 100 | 70 | 51 | 30.082 | 9.222 | 7.136 | 134.679 | 30.293 | 28.543 | 28.549 | 600.598 | 26.14 | 27.248 | 1276.818 | 27.374 | 27.599 | 38.538 | 23.001 | 3.1 | 2.2 | 0.8 | 0.8 | 0.2
3355 | 30/07/2025 10:49:50.523 | 98.688 | 82 | 100 | 70 | 52 | 27.781 | 9.473 | 7.185 | 134.427 | 30.288 | 28.536 | 28.559 | 600.33 | 26.148 | 27.241 | 1287.138 | 27.351 | 27.586 | 38.322 | 26.001 | 2.8 | 2.2 | 0.1 | 0.6 | 0.2
3356 | 30/07/2025 10:49:52.158 | 98.568 | 82 | 100 | 71 | 52 | 31.24 | 9.171 | 7.276 | 134.612 | 30.3 | 28.556 | 28.563 | 600.733 | 26.129 | 27.226 | 1297.13 | 27.343 | 27.575 | 38.104 | 26.001 | 2.8 | 2.2 | 0.1 | 0.6 | 0.2
3357 | 30/07/2025 10:49:53.793 | 98.616 | 82 | 100 | 70 | 52 | 31.839 | 8.988 | 7.277 | 134.706 | 30.303 | 28.548 | 28.561 | 600.397 | 26.15 | 27.246 | 1310.76 | 27.325 | 27.625 | 38.636 | 23.001 | 2.2 | 1.1 | 0.7 | 0 | 0.2
3358 | 30/07/2025 10:49:55.427 | 99.168 | 82 | 100 | 72 | 52 | 28.297 | 8.986 | 7.276 | 134.819 | 30.303 | 28.538 | 28.554 | 600.577 | 26.173 | 27.239 | 1313.538 | 27.329 | 27.603 | 38.479 | 24.001 | 1.6 | 1.1 | 0.7 | 0.5 | 0.2
3359 | 30/07/2025 10:49:57.063 | 99.024 | 83 | 100 | 70 | 51 | 31.827 | 9.158 | 7.224 | 134.478 | 30.294 | 28.524 | 28.559 | 600.463 | 26.158 | 27.256 | 1316.849 | 27.362 | 27.605 | 38.627 | 28.001 | 1.2 | 1.8 | 0.9 | 0.8 | 0.2
3360 | 30/07/2025 10:49:58.697 | 99.12 | 83 | 100 | 70 | 52 | 29.52 | 9.128 | 7.184 | 134.576 | 30.302 | 28.539 | 28.568 | 600.58 | 26.172 | 27.248 | 1310.132 | 27.197 | 27.584 | 38.384 | 27.001 | 2.7 | 1.8 | 0 | 0.5 | 0.2
3361 | 30/07/2025 10:50:00.329 | 99.096 | 82 | 100 | 71 | 52 | 28.189 | 9.181 | 7.188 | 134.472 | 30.281 | 28.561 | 28.554 | 600.473 | 26.159 | 27.255 | 1307.16 | 27.362 | 27.591 | 38.328 | 27.001 | 2.7 | 1.8 | 0 | 0.5 | 0.2
3362 | 30/07/2025 10:50:01.964 | 99.288 | 82 | 100 | 70 | 52 | 31.523 | 9.478 | 7.15 | 134.591 | 30.287 | 28.55 | 28.546 | 600.438 | 26.16 | 27.276 | 1298.263 | 27.176 | 27.609 | 38.653 | 22.001 | 2.6 | 2.4 | 0.6 | 0.6 | 0.2
3363 | 30/07/2025 10:50:03.599 | 99.048 | 83 | 100 | 69 | 52 | 31.69 | 9.435 | 7.123 | 134.71 | 30.287 | 28.533 | 28.549 | 600.809 | 26.158 | 27.263 | 1285.175 | 27.352 | 27.596 | 38.527 | 24.001 | 1.9 | 2.4 | 1 | 0 | 0.2
3364 | 30/07/2025 10:50:05.234 | 99.288 | 83 | 100 | 70 | 52 | 28.007 | 9.259 | 7.134 | 134.588 | 30.271 | 28.529 | 28.58 | 600.583 | 26.152 | 27.283 | 1279.87 | 27.368 | 27.59 | 38.469 | 26.001 | 3.2 | 2.3 | 2 | 0.5 | 0.2
3365 | 30/07/2025 10:50:06.869 | 99.192 | 82 | 100 | 69 | 52 | 31.877 | 9.134 | 7.134 | 134.4 | 30.274 | 28.545 | 28.576 | 600.49 | 26.152 | 27.258 | 1285.01 | 27.208 | 27.599 | 38.403 | 26.001 | 3.3 | 2.3 | 0.6 | 0.5 | 0.2
3366 | 30/07/2025 10:50:08.506 | 99.192 | 83 | 100 | 70 | 52 | 28.961 | 9.205 | 7.136 | 134.666 | 30.277 | 28.549 | 28.564 | 600.569 | 26.156 | 27.284 | 1297.175 | 27.343 | 27.6 | 36.86 | 24.001 | 1.3 | 3 | 1.2 | 0.5 | 0.3
3367 | 30/07/2025 10:50:10.141 | 99.312 | 82 | 100 | 70 | 52 | 28.586 | 9.131 | 7.135 | 134.802 | 30.303 | 28.544 | 28.553 | 600.402 | 26.162 | 27.249 | 1284.783 | 27.324 | 27.597 | 36.889 | 24.001 | 1.3 | 3 | 1.2 | 0.5 | 0.3
3368 | 30/07/2025 10:50:11.776 | 99.24 | 83 | 100 | 71 | 51 | 31.686 | 9.131 | 7.185 | 134.745 | 30.286 | 28.535 | 28.551 | 600.943 | 26.159 | 27.255 | 1284.926 | 27.375 | 27.608 | 37.473 | 33.001 | 2.3 | 3 | 0.3 | 1.1 | 0.2
3369 | 30/07/2025 10:50:13.411 | 99.528 | 84 | 100 | 70 | 53 | 31.201 | 8.91 | 7.188 | 134.513 | 30.313 | 28.545 | 28.561 | 601.837 | 26.164 | 27.274 | 1284.922 | 27.346 | 27.593 | 36.509 | 26.001 | 2.3 | 1.7 | 0 | 0.5 | 0.2
3370 | 30/07/2025 10:50:15.049 | 98.952 | 84 | 100 | 71 | 52 | 31.231 | 8.84 | 7.188 | 134.437 | 30.292 | 28.565 | 28.562 | 601.956 | 26.152 | 27.266 | 1282.705 | 27.373 | 27.582 | 36.523 | 21.001 | 1.9 | 1.7 | 0.6 | 0.6 | 0.2
3371 | 30/07/2025 10:50:16.685 | 98.928 | 84 | 100 | 71 | 52 | 31.83 | 9.135 | 7.188 | 134.954 | 30.31 | 28.547 | 28.558 | 600.538 | 26.158 | 27.261 | 1282.305 | 27.327 | 27.599 | 36.79 | 30.001 | 2 | 3.1 | 1 | 0.3 | 0.2
3372 | 30/07/2025 10:50:18.322 | 98.28 | 83 | 100 | 71 | 52 | 28.497 | 9.431 | 7.186 | 134.662 | 30.315 | 28.544 | 28.547 | 600.622 | 26.147 | 27.252 | 1284.743 | 27.338 | 27.608 | 36.647 | 30.001 | 2 | 3.1 | 1 | 0.3 | 0.2
3373 | 30/07/2025 10:50:19.958 | 97.608 | 81 | 99 | 70 | 51 | 29.13 | 9.21 | 7.187 | 134.619 | 30.296 | 28.518 | 28.548 | 600.364 | 26.143 | 27.276 | 1279.244 | 27.366 | 27.599 | 38.496 | 30.001 | 3.4 | 3.1 | 1.6 | 0.8 | 0.2
3374 | 30/07/2025 10:50:21.593 | 98.376 | 82 | 100 | 70 | 52 | 31.744 | 9.203 | 7.186 | 134.491 | 30.324 | 28.559 | 28.564 | 600.6 | 26.162 | 27.248 | 1287.141 | 27.347 | 27.589 | 38.195 | 28.001 | 2.3 | 1.2 | 0.8 | 0.4 | 0.2
3375 | 30/07/2025 10:50:23.230 | 97.68 | 81 | 100 | 70 | 52 | 28.107 | 9.215 | 7.19 | 134.478 | 30.292 | 28.546 | 28.554 | 600.618 | 26.15 | 27.249 | 1289.324 | 27.349 | 27.579 | 37.975 | 28.001 | 2.7 | 1.2 | 0 | 0 | 0.2
3376 | 30/07/2025 10:50:24.867 | 98.04 | 81 | 100 | 70 | 52 | 31.502 | 9.34 | 7.204 | 134.678 | 30.295 | 28.546 | 28.57 | 602.114 | 26.135 | 27.23 | 1289.895 | 27.321 | 27.613 | 37.415 | 23.001 | 2.7 | 2 | 0 | 0 | 0.2
3377 | 30/07/2025 10:50:26.505 | 98.16 | 82 | 100 | 71 | 52 | 31.551 | 9.429 | 7.205 | 134.478 | 30.286 | 28.539 | 28.552 | 601.883 | 26.13 | 27.246 | 1304.496 | 27.361 | 27.602 | 36.673 | 31.001 | 3.2 | 2 | 1 | 0.5 | 0.2
3378 | 30/07/2025 10:50:28.138 | 98.328 | 81 | 100 | 70 | 52 | 27.861 | 9.283 | 7.204 | 134.574 | 30.301 | 28.534 | 28.568 | 601.897 | 26.157 | 27.241 | 1308.469 | 27.351 | 27.577 | 36.843 | 31.001 | 3.2 | 2 | 1 | 0.5 | 0.2
3379 | 30/07/2025 10:50:29.770 | 98.568 | 82 | 100 | 70 | 52 | 29.642 | 9.217 | 7.21 | 134.565 | 30.296 | 28.559 | 28.568 | 602.039 | 26.156 | 27.238 | 1304.733 | 27.349 | 27.572 | 36.523 | 29.001 | 2.8 | 2.3 | 0.9 | 1.1 | 0.2
3380 | 30/07/2025 10:50:31.403 | 98.088 | 82 | 100 | 71 | 52 | 31.793 | 9.284 | 7.222 | 134.667 | 30.289 | 28.552 | 28.549 | 601.834 | 26.159 | 27.269 | 1306.542 | 27.333 | 27.614 | 36.938 | 31.001 | 3.3 | 2.3 | 0.4 | 1.6 | 0.2
3381 | 30/07/2025 10:50:33.039 | 98.136 | 80 | 100 | 70 | 52 | 28.652 | 9.296 | 7.221 | 134.815 | 30.282 | 28.549 | 28.57 | 601.642 | 26.145 | 27.249 | 1306.903 | 27.329 | 27.614 | 36.631 | 25.001 | 1.7 | 3 | 2.7 | 1.1 | 0.2
3382 | 30/07/2025 10:50:34.674 | 98.952 | 82 | 100 | 71 | 52 | 31.653 | 9.284 | 7.208 | 134.746 | 30.292 | 28.527 | 28.557 | 601.961 | 26.161 | 27.28 | 1309.073 | 27.355 | 27.601 | 36.757 | 25.001 | 2.6 | 3 | 0.8 | 0.8 | 0.2
3383 | 30/07/2025 10:50:36.310 | 97.92 | 82 | 100 | 70 | 53 | 31.221 | 9.401 | 7.203 | 134.48 | 30.288 | 28.537 | 28.562 | 602.092 | 26.151 | 27.252 | 1304.22 | 27.354 | 27.579 | 36.58 | 25.001 | 2.6 | 3 | 0.8 | 0.8 | 0.2
3384 | 30/07/2025 10:50:37.944 | 98.28 | 81 | 100 | 69 | 53 | 27.663 | 9.21 | 7.188 | 134.599 | 30.276 | 28.556 | 28.569 | 602.08 | 26.158 | 27.287 | 1305.133 | 27.365 | 27.595 | 37.32 | 26.001 | 2.6 | 2.8 | 0.4 | 0.9 | 0.2
3385 | 30/07/2025 10:50:39.581 | 97.656 | 81 | 100 | 72 | 53 | 30.347 | 9.19 | 7.189 | 134.829 | 30.293 | 28.543 | 28.554 | 601.922 | 26.161 | 27.28 | 1305.307 | 27.311 | 27.615 | 38.553 | 27.001 | 2.2 | 2.8 | 0.6 | 0.4 | 0.2
3386 | 30/07/2025 10:50:41.215 | 98.256 | 81 | 100 | 70 | 52 | 28.307 | 9.289 | 7.187 | 134.637 | 30.274 | 28.551 | 28.55 | 601.861 | 26.154 | 27.27 | 1296.871 | 27.354 | 27.6 | 38.437 | 26.001 | 3.4 | 2.5 | 0.7 | 0.5 | 0.2
3387 | 30/07/2025 10:50:42.850 | 98.352 | 82 | 99 | 70 | 52 | 29.196 | 9.213 | 7.186 | 133.37 | 30.284 | 28.526 | 28.559 | 601.799 | 26.167 | 27.266 | 1291.219 | 27.347 | 27.583 | 38.608 | 29.001 | 1.7 | 2.5 | 2.1 | 0 | 0.2
3388 | 30/07/2025 10:50:44.484 | 98.256 | 82 | 100 | 70 | 52 | 31.724 | 9.135 | 7.186 | 132.904 | 30.291 | 28.546 | 28.559 | 602.01 | 26.155 | 27.253 | 1292.295 | 27.345 | 27.593 | 38.343 | 26.001 | 3.3 | 2.7 | 1.2 | 0.5 | 0.2
3389 | 30/07/2025 10:50:46.123 | 98.448 | 82 | 100 | 71 | 52 | 30.721 | 9.146 | 7.188 | 133.134 | 30.294 | 28.549 | 28.538 | 601.975 | 26.147 | 27.271 | 1283.872 | 27.338 | 27.586 | 38.354 | 26.001 | 3.3 | 2.7 | 1.2 | 0.5 | 0.2
3390 | 30/07/2025 10:50:47.758 | 98.736 | 82 | 100 | 70 | 52 | 27.635 | 9.128 | 7.186 | 133.318 | 30.316 | 28.546 | 28.56 | 602.049 | 26.158 | 27.246 | 1285.145 | 27.326 | 27.594 | 38.563 | 24.001 | 2.2 | 2.7 | 1.2 | 0.5 | 0.2
3391 | 30/07/2025 10:50:49.393 | 99.024 | 83 | 100 | 71 | 53 | 31.636 | 9.281 | 7.188 | 133.102 | 30.299 | 28.541 | 28.538 | 601.83 | 26.147 | 27.266 | 1286.585 | 27.338 | 27.605 | 38.481 | 25.001 | 2.2 | 1.5 | 0.9 | 0.8 | 0.2
3392 | 30/07/2025 10:50:51.027 | 98.76 | 84 | 100 | 71 | 52 | 27.973 | 9.215 | 7.184 | 133.156 | 30.315 | 28.528 | 28.585 | 602.084 | 26.162 | 27.252 | 1282.569 | 27.349 | 27.6 | 38.306 | 23.001 | 1.6 | 1.5 | 0.6 | 0.9 | 0.2
3393 | 30/07/2025 10:50:52.661 | 99.024 | 82 | 100 | 70 | 52 | 29.778 | 9.287 | 7.189 | 132.899 | 30.298 | 28.563 | 28.572 | 601.968 | 26.136 | 27.256 | 1284.598 | 27.363 | 27.592 | 38.244 | 25.001 | 2.5 | 3.2 | 1.2 | 0.7 | 0.2
3394 | 30/07/2025 10:50:54.294 | 99.312 | 84 | 100 | 70 | 52 | 31.777 | 9.336 | 7.137 | 133.413 | 30.31 | 28.546 | 28.56 | 601.825 | 26.154 | 27.261 | 1276.906 | 27.324 | 27.592 | 38.627 | 25.001 | 2.5 | 3.2 | 1.2 | 0.7 | 0.2
3395 | 30/07/2025 10:50:55.929 | 99.6 | 83 | 100 | 70 | 52 | 30.146 | 9.291 | 7.135 | 133.277 | 30.294 | 28.544 | 28.55 | 602.083 | 26.133 | 27.248 | 1282.453 | 27.331 | 27.616 | 38.62 | 28.001 | 2.4 | 3.2 | 0.9 | 0.9 | 0.2
3396 | 30/07/2025 10:50:57.562 | 99.816 | 84 | 100 | 70 | 53 | 27.772 | 9.252 | 7.136 | 133.106 | 30.295 | 28.531 | 28.552 | 601.793 | 26.134 | 27.248 | 1296.576 | 27.359 | 27.604 | 38.545 | 31.001 | 1.2 | 2.7 | 1.4 | 0.8 | 0.2
3397 | 30/07/2025 10:50:59.198 | 100.104 | 82 | 100 | 69 | 52 | 31.203 | 9.215 | 7.135 | 133.072 | 30.293 | 28.533 | 28.559 | 603.128 | 26.135 | 27.237 | 1298.122 | 27.357 | 27.601 | 38.491 | 25.001 | 3.4 | 2.7 | 1.9 | 0.6 | 0.3
3398 | 30/07/2025 10:51:00.832 | 100.152 | 83 | 100 | 70 | 52 | 27.617 | 9.429 | 7.137 | 132.888 | 30.301 | 28.558 | 28.551 | 601.953 | 26.154 | 27.23 | 1303.209 | 27.34 | 27.584 | 38.215 | 26.001 | 2.9 | 1.7 | 0.4 | 0.3 | 0.3
3399 | 30/07/2025 10:51:02.466 | 100.32 | 83 | 100 | 71 | 52 | 30.19 | 9.5 | 7.169 | 133.302 | 30.305 | 28.554 | 28.568 | 602.096 | 26.14 | 27.232 | 1297.11 | 27.323 | 27.614 | 38.57 | 29.001 | 2.3 | 1.7 | 0.7 | 0.5 | 0.3
3400 | 30/07/2025 10:51:04.100 | 100.008 | 83 | 100 | 71 | 52 | 31.87 | 9.266 | 7.187 | 133.078 | 30.279 | 28.534 | 28.525 | 601.918 | 26.16 | 27.243 | 1291.954 | 27.362 | 27.593 | 38.447 | 29.001 | 2.3 | 1.7 | 0.7 | 0.5 | 0.3
3401 | 30/07/2025 10:51:05.735 | 99.744 | 83 | 100 | 70 | 52 | 29.52 | 9.179 | 7.187 | 133.294 | 30.311 | 28.53 | 28.571 | 602.023 | 26.167 | 27.248 | 1292.059 | 27.35 | 27.598 | 38.437 | 28.001 | 3 | 2.5 | 1.3 | 0.6 | 0.3
3402 | 30/07/2025 10:51:07.369 | 98.808 | 82 | 100 | 70 | 52 | 28.156 | 9.213 | 7.203 | 134.592 | 30.286 | 28.561 | 28.568 | 602.005 | 26.157 | 27.256 | 1290.314 | 27.353 | 27.594 | 38.217 | 24.001 | 3.3 | 2.5 | 0.6 | 0.3 | 0.2
3403 | 30/07/2025 10:51:09.005 | 98.664 | 82 | 100 | 70 | 52 | 30.719 | 9.208 | 7.205 | 134.605 | 30.3 | 28.548 | 28.568 | 601.934 | 26.179 | 27.264 | 1287.254 | 27.333 | 27.6 | 38.233 | 27.001 | 3.6 | 2.3 | 0.6 | 0.5 | 0.2
3404 | 30/07/2025 10:51:10.639 | 98.736 | 82 | 100 | 70 | 52 | 27.638 | 9.136 | 7.205 | 134.712 | 30.268 | 28.548 | 28.556 | 603.222 | 26.162 | 27.265 | 1282.583 | 27.328 | 27.612 | 38.614 | 26.001 | 3.6 | 2.3 | 0.7 | 1.4 | 0.2
3405 | 30/07/2025 10:51:12.274 | 98.52 | 82 | 100 | 70 | 52 | 30.812 | 9.217 | 7.221 | 134.67 | 30.288 | 28.533 | 28.546 | 602.985 | 26.159 | 27.271 | 1294.858 | 27.354 | 27.607 | 38.593 | 26.001 | 3.6 | 2.3 | 0.7 | 1.4 | 0.2
3406 | 30/07/2025 10:51:13.908 | 98.4 | 82 | 100 | 71 | 53 | 31.84 | 9.199 | 7.219 | 134.634 | 30.278 | 28.541 | 28.579 | 602.169 | 26.156 | 27.262 | 1301.713 | 27.345 | 27.589 | 38.274 | 28.001 | 2.3 | 2.2 | 1.4 | 0.7 | 0.2
3407 | 30/07/2025 10:51:15.543 | 98.856 | 82 | 100 | 70 | 52 | 28.911 | 9.289 | 7.22 | 134.398 | 30.271 | 28.564 | 28.557 | 603.215 | 26.156 | 27.255 | 1295.794 | 27.369 | 27.592 | 36.479 | 26.001 | 1.5 | 2.2 | 0.6 | 0 | 0.1
3408 | 30/07/2025 10:51:17.179 | 99.072 | 83 | 100 | 71 | 52 | 31.731 | 9.341 | 7.22 | 134.535 | 30.293 | 28.551 | 28.589 | 602.088 | 26.148 | 27.252 | 1290.197 | 27.333 | 27.602 | 36.585 | 21.001 | 1.9 | 2.3 | 1.3 | 0 | 0.2
3409 | 30/07/2025 10:51:18.815 | 98.88 | 81 | 100 | 70 | 51 | 30.143 | 9.287 | 7.264 | 134.678 | 30.287 | 28.544 | 28.54 | 602.49 | 26.156 | 27.261 | 1296.877 | 27.332 | 27.592 | 38.597 | 25.001 | 1.7 | 2.3 | 1.3 | 0.6 | 0.2
3410 | 30/07/2025 10:51:20.449 | 99 | 81 | 100 | 71 | 52 | 27.779 | 9.292 | 7.275 | 134.707 | 30.307 | 28.533 | 28.574 | 603.165 | 26.166 | 27.265 | 1301.749 | 27.351 | 27.605 | 38.463 | 29.001 | 2.4 | 1.1 | 0.3 | 0.6 | 0.3
3411 | 30/07/2025 10:51:22.084 | 98.496 | 83 | 100 | 71 | 52 | 31.203 | 9.134 | 7.239 | 134.544 | 30.312 | 28.544 | 28.563 | 603.27 | 26.144 | 27.251 | 1297.103 | 27.355 | 27.596 | 38.381 | 29.001 | 2.4 | 1.1 | 0.3 | 0.6 | 0.3
3412 | 30/07/2025 10:51:23.716 | 98.88 | 83 | 100 | 71 | 52 | 31.842 | 9.284 | 7.205 | 134.536 | 30.301 | 28.547 | 28.551 | 603.078 | 26.143 | 27.257 | 1294.854 | 27.333 | 27.59 | 38.399 | 24.001 | 2.1 | 1.1 | 0.6 | 0.7 | 0.3
3413 | 30/07/2025 10:51:25.352 | 98.736 | 84 | 100 | 71 | 52 | 30.374 | 9.29 | 7.187 | 134.607 | 30.305 | 28.559 | 28.551 | 603.182 | 26.149 | 27.252 | 1292.243 | 27.34 | 27.606 | 38.655 | 25.001 | 1.3 | 2.1 | 0.6 | 0.3 | 0.2
3414 | 30/07/2025 10:51:26.987 | 97.824 | 81 | 100 | 70 | 52 | 31.818 | 9.552 | 7.189 | 134.585 | 30.308 | 28.542 | 28.532 | 603.227 | 26.16 | 27.273 | 1282.297 | 27.323 | 27.613 | 38.541 | 23.001 | 2.3 | 2.1 | 0.9 | 1.1 | 0.2
3415 | 30/07/2025 10:51:28.621 | 97.152 | 82 | 100 | 70 | 52 | 29.63 | 9.432 | 7.186 | 134.712 | 30.315 | 28.541 | 28.573 | 603.275 | 26.14 | 27.233 | 1285.288 | 27.353 | 27.602 | 36.504 | 24.001 | 3.1 | 1.4 | 0.9 | 1.5 | 0.2
3416 | 30/07/2025 10:51:30.256 | 96.768 | 81 | 100 | 71 | 52 | 28.131 | 9.237 | 7.137 | 134.271 | 30.292 | 28.553 | 28.555 | 602.021 | 26.122 | 27.257 | 1287.525 | 27.362 | 27.581 | 38.372 | 24.001 | 3.1 | 1.4 | 0.9 | 1.5 | 0.2
3417 | 30/07/2025 10:51:31.891 | 97.344 | 81 | 100 | 70 | 54 | 31.552 | 9.211 | 7.135 | 134.718 | 30.315 | 28.551 | 28.57 | 601.948 | 26.158 | 27.235 | 1285.411 | 27.331 | 27.612 | 38.48 | 26.001 | 1.5 | 1.4 | 1.2 | 0.9 | 0.2
3418 | 30/07/2025 10:51:33.527 | 97.464 | 81 | 100 | 70 | 52 | 31.643 | 9.287 | 7.153 | 134.851 | 30.293 | 28.547 | 28.55 | 602.098 | 26.15 | 27.239 | 1284.932 | 27.335 | 27.625 | 38.709 | 31.001 | 2.3 | 2.4 | 1.2 | 0.5 | 0.2
3419 | 30/07/2025 10:51:35.160 | 97.368 | 82 | 100 | 70 | 52 | 30.729 | 9.214 | 7.134 | 134.81 | 30.298 | 28.537 | 28.548 | 602.064 | 26.157 | 27.24 | 1284.485 | 27.349 | 27.598 | 38.547 | 26.001 | 2.9 | 2.4 | 0 | 0.6 | 0.2
3420 | 30/07/2025 10:51:36.795 | 97.368 | 80 | 100 | 70 | 50 | 31.934 | 9.17 | 7.134 | 134.347 | 30.28 | 28.534 | 28.573 | 602.075 | 26.144 | 27.229 | 1290.272 | 27.372 | 27.593 | 38.611 | 25.001 | 3.2 | 1.4 | 0.6 | 0.5 | 0.2
3421 | 30/07/2025 10:51:38.430 | 97.44 | 82 | 100 | 70 | 52 | 29.037 | 9.181 | 7.186 | 134.54 | 30.304 | 28.552 | 28.561 | 601.888 | 26.159 | 27.254 | 1287.217 | 27.346 | 27.573 | 38.303 | 24.001 | 4.1 | 1.4 | 1.5 | 1.1 | 0.1
3422 | 30/07/2025 10:51:40.067 | 97.992 | 81 | 100 | 71 | 52 | 28.529 | 9.071 | 7.186 | 134.869 | 30.293 | 28.548 | 28.555 | 601.89 | 26.16 | 27.251 | 1285.12 | 27.311 | 27.613 | 38.573 | 24.001 | 4.1 | 1.4 | 1.5 | 1.1 | 0.1
3423 | 30/07/2025 10:51:41.701 | 98.04 | 84 | 100 | 71 | 52 | 31.645 | 8.988 | 7.187 | 134.491 | 30.274 | 28.539 | 28.538 | 601.975 | 26.15 | 27.272 | 1280.617 | 27.336 | 27.605 | 38.41 | 28.001 | 2.8 | 2.1 | 1.2 | 0.5 | 0.2
3424 | 30/07/2025 10:51:43.337 | 98.472 | 82 | 100 | 71 | 52 | 27.833 | 9.129 | 7.186 | 134.515 | 30.287 | 28.534 | 28.563 | 602.035 | 26.163 | 27.26 | 1277.119 | 27.357 | 27.601 | 38.426 | 28.001 | 2.5 | 2.1 | 1.1 | 0.5 | 0.2
3425 | 30/07/2025 11:22:47.877 | 98.376 | 84 | 100 | 70 | 54 | 28.608 | 9.232 | 7.234 | 134.458 | 30.711 | 28.703 | 28.99 | 603.229 | 26.442 | 27.579 | 1262.333 | 27.353 | 27.612 | 38.497 | 31.001 | 2.6 | 2.8 | 1.3 | 1.1 | 0.3
3426 | 30/07/2025 11:22:49.599 | 97.44 | 82 | 100 | 70 | 52 | 31.974 | 8.878 | 7.221 | 134.791 | 30.712 | 28.676 | 28.977 | 603.068 | 26.46 | 27.567 | 1269.926 | 27.315 | 27.596 | 38.557 | 26.001 | 2.1 | 2.6 | 0.9 | 1.1 | 0.2
3427 | 30/07/2025 11:22:51.234 | 97.992 | 84 | 100 | 70 | 52 | 32.187 | 9.135 | 7.201 | 134.48 | 30.72 | 28.681 | 29.017 | 603.161 | 26.441 | 27.538 | 1274.326 | 27.35 | 27.616 | 38.467 | 26.001 | 2.1 | 2.6 | 0.9 | 1.1 | 0.2
3428 | 30/07/2025 11:22:52.869 | 96.936 | 82 | 100 | 70 | 52 | 28.466 | 9.139 | 7.205 | 134.324 | 30.719 | 28.696 | 28.987 | 603.103 | 26.45 | 27.573 | 1267.225 | 27.353 | 27.58 | 38.199 | 25.001 | 3.2 | 3 | 1.2 | 0.9 | 0.2
3429 | 30/07/2025 11:22:54.504 | 97.104 | 82 | 100 | 71 | 52 | 30.074 | 9.125 | 7.151 | 134.736 | 30.738 | 28.681 | 28.992 | 603.24 | 26.456 | 27.553 | 1264.767 | 27.324 | 27.598 | 38.44 | 24.001 | 3.4 | 1.8 | 0.9 | 0.9 | 0.2
3430 | 30/07/2025 11:22:56.139 | 97.68 | 82 | 100 | 71 | 53 | 29.556 | 9.122 | 7.153 | 134.582 | 30.741 | 28.686 | 28.979 | 603.167 | 26.438 | 27.559 | 1269.573 | 27.321 | 27.6 | 38.681 | 28.001 | 3.6 | 2.3 | 1.1 | 0 | 0.1
3431 | 30/07/2025 11:22:57.775 | 97.704 | 82 | 100 | 70 | 52 | 28.887 | 8.994 | 7.184 | 134.633 | 30.742 | 28.673 | 28.998 | 602.035 | 26.439 | 27.545 | 1279.421 | 27.339 | 27.597 | 38.234 | 25.001 | 2.5 | 2.7 | 2.2 | 0 | 0.2
3432 | 30/07/2025 11:22:59.412 | 97.992 | 82 | 100 | 70 | 53 | 32.078 | 9.136 | 7.187 | 134.578 | 30.729 | 28.699 | 29.005 | 601.922 | 26.434 | 27.56 | 1287.017 | 27.363 | 27.595 | 38.353 | 26.001 | 2.4 | 2.9 | 1.4 | 0.5 | 0.2
3433 | 30/07/2025 11:23:01.047 | 98.832 | 84 | 100 | 70 | 51 | 31.773 | 9.213 | 7.187 | 134.789 | 30.763 | 28.689 | 29 | 601.869 | 26.464 | 27.561 | 1288.827 | 27.34 | 27.588 | 38.161 | 26.001 | 2.4 | 2.9 | 1.4 | 0.5 | 0.2
3434 | 30/07/2025 11:23:02.681 | 98.64 | 83 | 100 | 70 | 52 | 28.216 | 9.205 | 7.186 | 134.586 | 30.742 | 28.689 | 28.982 | 602.096 | 26.439 | 27.546 | 1291.587 | 27.334 | 27.614 | 38.55 | 29.001 | 3 | 1.9 | 0 | 0.5 | 0.2
3435 | 30/07/2025 11:23:04.317 | 100.008 | 84 | 100 | 70 | 52 | 32.344 | 9.19 | 7.187 | 134.703 | 30.761 | 28.688 | 28.975 | 601.969 | 26.453 | 27.552 | 1295.089 | 27.312 | 27.612 | 38.422 | 25.001 | 2.7 | 3.9 | 0.7 | 0 | 0.2
3436 | 30/07/2025 11:23:05.953 | 99.912 | 85 | 100 | 70 | 52 | 28.946 | 8.976 | 7.219 | 133.101 | 30.73 | 28.672 | 29.003 | 602.09 | 26.431 | 27.536 | 1294.435 | 27.368 | 27.613 | 38.708 | 23.001 | 2.3 | 3.1 | 1.8 | 0 | 0.2
3437 | 30/07/2025 11:23:07.588 | 99.648 | 84 | 100 | 71 | 51 | 29.53 | 9.191 | 7.222 | 133.009 | 30.735 | 28.69 | 29.005 | 601.876 | 26.437 | 27.547 | 1287.236 | 27.337 | 27.581 | 38.473 | 23.001 | 2.3 | 3.2 | 0.8 | 0.5 | 0.1
3438 | 30/07/2025 11:23:09.224 | 100.008 | 84 | 100 | 70 | 52 | 32.209 | 8.84 | 7.22 | 133.46 | 30.743 | 28.689 | 29.008 | 603.191 | 26.438 | 27.533 | 1272.356 | 27.339 | 27.59 | 38.196 | 23.001 | 2.3 | 3.2 | 0.8 | 0.5 | 0.1
3439 | 30/07/2025 11:23:10.860 | 99.984 | 86 | 100 | 71 | 51 | 31.245 | 9.13 | 7.24 | 133.185 | 30.725 | 28.693 | 28.988 | 603.205 | 26.434 | 27.534 | 1276.077 | 27.34 | 27.612 | 38.505 | 24.001 | 1.8 | 2.2 | 1.4 | 0.5 | 0.2
3440 | 30/07/2025 11:23:12.497 | 100.464 | 86 | 100 | 70 | 52 | 31.917 | 8.989 | 7.239 | 133.168 | 30.753 | 28.682 | 28.988 | 603.329 | 26.434 | 27.524 | 1272.022 | 27.313 | 27.601 | 38.431 | 25.001 | 1.2 | 2.7 | 0.7 | 1 | 0.1
3441 | 30/07/2025 11:23:14.131 | 99.768 | 85 | 99 | 70 | 52 | 32.136 | 9.283 | 7.238 | 133.071 | 30.723 | 28.671 | 28.991 | 603.2 | 26.445 | 27.541 | 1257.86 | 27.362 | 27.609 | 38.524 | 25.001 | 3.3 | 3 | 0.9 | 1 | 0.1
3442 | 30/07/2025 11:23:15.767 | 100.344 | 87 | 100 | 70 | 53 | 28.443 | 8.991 | 7.205 | 133.1 | 30.746 | 28.693 | 29.013 | 603.102 | 26.462 | 27.542 | 1259.743 | 27.339 | 27.578 | 38.25 | 30.001 | 1.7 | 1.9 | 1.1 | 0.5 | 0.1
3443 | 30/07/2025 11:23:17.402 | 100.584 | 87 | 100 | 70 | 50 | 30.076 | 9.131 | 7.203 | 133.159 | 30.721 | 28.691 | 28.985 | 603.155 | 26.457 | 27.545 | 1259.646 | 27.345 | 27.611 | 38.26 | 25.001 | 2.1 | 3.5 | 0.5 | 0.5 | 0.1
3444 | 30/07/2025 11:23:19.038 | 100.968 | 87 | 100 | 70 | 52 | 32.252 | 8.99 | 7.204 | 132.972 | 30.712 | 28.685 | 28.976 | 603.17 | 26.446 | 27.569 | 1260.092 | 27.328 | 27.604 | 38.655 | 25.001 | 2.1 | 3.5 | 0.5 | 0.5 | 0.1
3445 | 30/07/2025 11:23:20.675 | 100.584 | 86 | 100 | 70 | 52 | 30.788 | 8.979 | 7.202 | 133.3 | 30.716 | 28.672 | 29.001 | 603.139 | 26.447 | 27.558 | 1262.168 | 27.351 | 27.598 | 38.384 | 27.001 | 3.1 | 5.8 | 0.6 | 1.1 | 0.1
3446 | 30/07/2025 11:23:22.311 | 100.464 | 85 | 100 | 70 | 52 | 32.092 | 8.856 | 7.221 | 133.079 | 30.7 | 28.681 | 29.001 | 603.091 | 26.442 | 27.565 | 1265.782 | 27.349 | 27.591 | 38.42 | 26.001 | 2.7 | 3.4 | 0.6 | 1.1 | 0.1
3447 | 30/07/2025 11:23:23.946 | 100.824 | 85 | 100 | 71 | 52 | 31.861 | 9.215 | 7.221 | 133.148 | 30.717 | 28.699 | 29.005 | 603.177 | 26.445 | 27.556 | 1265.517 | 27.348 | 27.57 | 38.058 | 32.001 | 3.8 | 2.9 | 0.3 | 0.5 | 0.1
3448 | 30/07/2025 11:23:25.585 | 100.848 | 86 | 100 | 70 | 52 | 28.225 | 8.918 | 7.219 | 133.106 | 30.725 | 28.686 | 28.986 | 603.16 | 26.452 | 27.569 | 1274.191 | 27.349 | 27.62 | 38.477 | 25.001 | 3.7 | 3.6 | 1 | 0.5 | 0.1
3449 | 30/07/2025 11:23:27.223 | 100.176 | 85 | 100 | 71 | 52 | 30.74 | 8.987 | 7.238 | 133.269 | 30.731 | 28.673 | 28.97 | 603.062 | 26.461 | 27.558 | 1282.548 | 27.317 | 27.6 | 38.613 | 25.001 | 3.7 | 3.6 | 1 | 0.5 | 0.1
3450 | 30/07/2025 11:23:28.858 | 100.176 | 86 | 100 | 71 | 52 | 32.322 | 8.973 | 7.237 | 134.549 | 30.734 | 28.68 | 29.013 | 603.332 | 26.442 | 27.548 | 1290.082 | 27.352 | 27.607 | 38.481 | 20.001 | 3.6 | 2.7 | 0.8 | 1 | 0.1
3451 | 30/07/2025 11:23:30.494 | 100.08 | 84 | 100 | 70 | 52 | 30.193 | 9.132 | 7.242 | 134.459 | 30.733 | 28.685 | 28.99 | 603.094 | 26.44 | 27.551 | 1276.533 | 27.335 | 27.584 | 38.252 | 24.001 | 3.8 | 2.2 | 0.6 | 1 | 0.1
3452 | 30/07/2025 11:23:32.136 | 100.128 | 86 | 100 | 70 | 52 | 32.227 | 9.193 | 7.239 | 134.734 | 30.733 | 28.697 | 28.986 | 603.156 | 26.442 | 27.542 | 1279.537 | 27.349 | 27.592 | 38.246 | 27.001 | 3.7 | 4.7 | 0.6 | 0.5 | 0.1
3453 | 30/07/2025 11:23:33.773 | 100.248 | 84 | 100 | 70 | 52 | 31.373 | 9.136 | 7.24 | 134.582 | 30.74 | 28.682 | 28.982 | 603.095 | 26.442 | 27.557 | 1282.083 | 27.32 | 27.606 | 38.51 | 26.001 | 3.8 | 3.1 | 0.9 | 0.5 | 0.1
3454 | 30/07/2025 11:23:35.409 | 100.272 | 85 | 100 | 70 | 52 | 28.131 | 9.212 | 7.274 | 134.669 | 30.749 | 28.673 | 28.992 | 603.232 | 26.441 | 27.55 | 1287.231 | 27.337 | 27.608 | 38.41 | 25.001 | 2.9 | 4.3 | 1.3 | 0 | 0.1
3455 | 30/07/2025 11:23:37.042 | 99.936 | 85 | 100 | 70 | 52 | 31.204 | 9.158 | 7.277 | 134.364 | 30.735 | 28.689 | 29.02 | 603.122 | 26.444 | 27.56 | 1278.183 | 27.355 | 27.596 | 38.448 | 25.001 | 2.9 | 4.3 | 1.3 | 0 | 0.1
3456 | 30/07/2025 11:23:38.675 | 100.104 | 85 | 100 | 70 | 53 | 32.34 | 9.055 | 7.277 | 134.508 | 30.741 | 28.691 | 28.995 | 603.15 | 26.445 | 27.545 | 1259.966 | 27.341 | 27.58 | 38.339 | 24.001 | 3.4 | 2.6 | 1.5 | 0 | 0.1
3457 | 30/07/2025 11:23:40.309 | 100.032 | 86 | 100 | 70 | 52 | 30.073 | 8.895 | 7.277 | 134.665 | 30.741 | 28.694 | 28.987 | 603.064 | 26.434 | 27.56 | 1257.319 | 27.342 | 27.613 | 38.239 | 26.001 | 3.1 | 3.3 | 0.7 | 0 | 0.1
3458 | 30/07/2025 11:23:41.943 | 100.176 | 85 | 100 | 71 | 52 | 32.275 | 8.861 | 7.276 | 134.697 | 30.74 | 28.687 | 28.973 | 603.152 | 26.429 | 27.541 | 1266.971 | 27.324 | 27.611 | 38.51 | 29.001 | 2.2 | 2.3 | 1.7 | 0 | 0.1
3459 | 30/07/2025 11:23:43.575 | 99.864 | 85 | 100 | 70 | 51 | 30.728 | 9.132 | 7.275 | 134.618 | 30.732 | 28.669 | 28.997 | 603.203 | 26.428 | 27.532 | 1276.864 | 27.36 | 27.622 | 38.515 | 30.001 | 1.7 | 0.7 | 1 | 1 | 0.1
3460 | 30/07/2025 11:23:45.208 | 100.272 | 85 | 100 | 70 | 52 | 28.27 | 8.99 | 7.278 | 134.651 | 30.736 | 28.692 | 28.991 | 603.103 | 26.448 | 27.531 | 1276.535 | 27.345 | 27.596 | 38.356 | 30.001 | 1.7 | 0.7 | 1 | 1 | 0.1
3461 | 30/07/2025 11:23:46.845 | 100.152 | 84 | 100 | 70 | 52 | 31.593 | 9.284 | 7.276 | 134.642 | 30.724 | 28.688 | 29.005 | 603.176 | 26.433 | 27.52 | 1275.746 | 27.338 | 27.593 | 38.095 | 28.001 | 2.4 | 3.3 | 0.6 | 1 | 0.1
3462 | 30/07/2025 11:23:48.480 | 100.32 | 85 | 100 | 70 | 52 | 32.3 | 9.133 | 7.276 | 134.424 | 30.722 | 28.696 | 28.97 | 603.114 | 26.447 | 27.532 | 1264.472 | 27.338 | 27.603 | 38.483 | 30.001 | 2.4 | 3.3 | 1.8 | 0 | 0.1
3463 | 30/07/2025 11:23:50.116 | 99.96 | 85 | 100 | 70 | 52 | 30.579 | 9.129 | 7.275 | 134.82 | 30.728 | 28.68 | 28.981 | 603.241 | 26.447 | 27.533 | 1265.564 | 27.309 | 27.597 | 38.577 | 27.001 | 3.6 | 3.6 | 1.6 | 0 | 0.2
3464 | 30/07/2025 11:23:51.752 | 100.056 | 84 | 100 | 70 | 53 | 32.311 | 8.985 | 7.275 | 134.551 | 30.727 | 28.669 | 28.978 | 603.092 | 26.451 | 27.574 | 1262.198 | 27.368 | 27.611 | 38.398 | 32.001 | 3 | 2.8 | 0.8 | 0.2 | 0.2
3465 | 30/07/2025 11:23:53.386 | 99.84 | 84 | 99 | 70 | 52 | 30.198 | 9.144 | 7.254 | 134.671 | 30.733 | 28.693 | 28.994 | 603.116 | 26.468 | 27.573 | 1249.684 | 27.34 | 27.585 | 38.304 | 28.001 | 5 | 2.6 | 0 | 0.2 | 0.2
3466 | 30/07/2025 11:23:55.018 | 99.864 | 84 | 100 | 71 | 51 | 28.534 | 9.211 | 7.239 | 134.683 | 30.709 | 28.694 | 28.996 | 603.176 | 26.451 | 27.563 | 1247.637 | 27.356 | 27.613 | 38.36 | 28.001 | 5 | 2.6 | 0 | 0.2 | 0.2
3467 | 30/07/2025 11:23:56.654 | 100.008 | 86 | 100 | 71 | 52 | 31.85 | 9.004 | 7.24 | 134.56 | 30.713 | 28.694 | 28.965 | 603.057 | 26.451 | 27.556 | 1253.604 | 27.318 | 27.59 | 38.441 | 28.001 | 3.5 | 1.9 | 1.5 | 1.1 | 0.2
3468 | 30/07/2025 11:23:58.292 | 100.152 | 85 | 100 | 70 | 52 | 28.117 | 9.132 | 7.238 | 134.736 | 30.71 | 28.677 | 28.997 | 603.296 | 26.439 | 27.559 | 1257.339 | 27.34 | 27.61 | 38.414 | 22.001 | 1.5 | 2.7 | 1.3 | 1.1 | 0.2
3469 | 30/07/2025 11:23:59.928 | 99.504 | 84 | 99 | 71 | 52 | 31.233 | 9.13 | 7.239 | 134.809 | 30.727 | 28.675 | 29 | 603.124 | 26.448 | 27.567 | 1257.285 | 27.349 | 27.6 | 38.47 | 23.001 | 3.1 | 3.1 | 1.2 | 0.8 | 0.2
3470 | 30/07/2025 11:24:01.564 | 99.312 | 83 | 100 | 70 | 52 | 32.301 | 9.133 | 7.243 | 134.52 | 30.733 | 28.692 | 29.008 | 603.241 | 26.439 | 27.543 | 1259.09 | 27.349 | 27.581 | 38.077 | 29.001 | 4.6 | 2.3 | 1.2 | 0.8 | 0.2
3471 | 30/07/2025 11:24:03.199 | 99.096 | 84 | 100 | 69 | 52 | 29.594 | 8.992 | 7.277 | 134.688 | 30.736 | 28.694 | 28.981 | 602.992 | 26.441 | 27.572 | 1255.085 | 27.333 | 27.607 | 38.509 | 29.001 | 4.6 | 2.3 | 1.2 | 0.8 | 0.2
3472 | 30/07/2025 11:24:04.835 | 98.304 | 83 | 100 | 70 | 51 | 28.966 | 9.126 | 7.219 | 134.662 | 30.758 | 28.68 | 28.966 | 603.187 | 26.459 | 27.549 | 1257.573 | 27.308 | 27.599 | 38.415 | 28.001 | 1.9 | 3.9 | 1.2 | 0.9 | 0.3
3473 | 30/07/2025 11:24:06.470 | 98.64 | 83 | 100 | 69 | 52 | 32.105 | 8.994 | 7.203 | 134.783 | 30.745 | 28.667 | 29.005 | 603.4 | 26.446 | 27.553 | 1262.186 | 27.363 | 27.606 | 38.393 | 28.001 | 3.1 | 4.4 | 1.3 | 0.9 | 0.3
3474 | 30/07/2025 11:24:08.105 | 98.136 | 82 | 100 | 69 | 52 | 28.235 | 9.162 | 7.186 | 134.427 | 30.74 | 28.685 | 29.004 | 603.166 | 26.455 | 27.552 | 1259.452 | 27.35 | 27.592 | 38.371 | 28.001 | 3.1 | 4.1 | 1.1 | 1.1 | 0.3
3475 | 30/07/2025 11:24:09.741 | 98.712 | 83 | 100 | 71 | 52 | 31.662 | 9.014 | 7.187 | 134.733 | 30.742 | 28.693 | 28.992 | 603.165 | 26.439 | 27.555 | 1264.714 | 27.359 | 27.59 | 38.293 | 23.001 | 3.3 | 2.4 | 0.9 | 1.1 | 0.3
3476 | 30/07/2025 11:24:11.375 | 98.928 | 84 | 100 | 70 | 51 | 32.362 | 9.125 | 7.187 | 134.725 | 30.753 | 28.693 | 28.996 | 602.929 | 26.442 | 27.552 | 1262.156 | 27.323 | 27.618 | 38.605 | 28.001 | 5.3 | 2.4 | 1 | 0.5 | 0.3
3477 | 30/07/2025 11:24:13.010 | 98.664 | 83 | 100 | 70 | 51 | 29.005 | 8.915 | 7.185 | 134.623 | 30.736 | 28.677 | 28.983 | 603.233 | 26.433 | 27.539 | 1267.651 | 27.334 | 27.601 | 38.582 | 28.001 | 5.3 | 2.4 | 1 | 0.5 | 0.3
3478 | 30/07/2025 11:24:14.645 | 99.048 | 84 | 100 | 70 | 52 | 29.451 | 9.186 | 7.168 | 134.49 | 30.721 | 28.676 | 29.001 | 603.124 | 26.428 | 27.545 | 1276.681 | 27.361 | 27.599 | 38.54 | 28.001 | 2.7 | 2.6 | 1 | 0.5 | 0.3
3479 | 30/07/2025 11:24:16.283 | 98.904 | 84 | 100 | 70 | 54 | 30.18 | 9.29 | 7.153 | 134.598 | 30.744 | 28.703 | 29.01 | 603.29 | 26.417 | 27.546 | 1277.271 | 27.358 | 27.6 | 38.448 | 27.001 | 2.9 | 2.2 | 1 | 0.5 | 0.3
3480 | 30/07/2025 11:24:17.917 | 99.168 | 83 | 100 | 70 | 52 | 28.525 | 8.987 | 7.153 | 134.534 | 30.737 | 28.682 | 28.987 | 603.317 | 26.433 | 27.531 | 1272.134 | 27.341 | 27.579 | 38.437 | 27.001 | 2.7 | 4.3 | 0.2 | 0.5 | 0.3
3481 | 30/07/2025 11:24:19.552 | 99.456 | 84 | 100 | 71 | 52 | 31.913 | 8.976 | 7.187 | 134.748 | 30.749 | 28.684 | 28.992 | 603.062 | 26.448 | 27.541 | 1266.943 | 27.314 | 27.613 | 38.425 | 27.001 | 2.4 | 3.9 | 0 | 0.5 | 0.2
3482 | 30/07/2025 11:24:21.188 | 99.168 | 83 | 100 | 70 | 52 | 32.144 | 9.123 | 7.185 | 134.671 | 30.728 | 28.675 | 28.992 | 603.207 | 26.44 | 27.539 | 1267.389 | 27.366 | 27.616 | 38.33 | 27.001 | 2.4 | 3.9 | 0 | 0.5 | 0.2
3483 | 30/07/2025 11:24:22.825 | 99 | 84 | 100 | 70 | 52 | 28.533 | 9.133 | 7.187 | 134.573 | 30.73 | 28.683 | 28.99 | 603.093 | 26.447 | 27.537 | 1271.772 | 27.353 | 27.587 | 38.401 | 30.001 | 2.1 | 5 | 1.5 | 0.5 | 0.2
3484 | 30/07/2025 11:24:24.460 | 99.72 | 83 | 100 | 71 | 52 | 32.351 | 9.059 | 7.187 | 134.308 | 30.732 | 28.707 | 29.002 | 603.262 | 26.453 | 27.555 | 1269.681 | 27.36 | 27.58 | 38.284 | 31.001 | 3.3 | 2.6 | 0.7 | 0.8 | 0.2
3485 | 30/07/2025 11:24:26.095 | 99.576 | 85 | 100 | 71 | 52 | 29.607 | 9.131 | 7.188 | 134.92 | 30.739 | 28.69 | 28.988 | 603.134 | 26.469 | 27.563 | 1260.327 | 27.337 | 27.591 | 38.389 | 27.001 | 2.9 | 3.8 | 1.3 | 0.8 | 0.2
3486 | 30/07/2025 11:24:27.729 | 99.552 | 84 | 100 | 71 | 53 | 29.012 | 8.985 | 7.186 | 134.713 | 30.723 | 28.681 | 28.981 | 603.2 | 26.447 | 27.538 | 1257.182 | 27.324 | 27.614 | 38.387 | 29.001 | 4 | 5 | 0.6 | 0.6 | 0.2
3487 | 30/07/2025 11:24:29.363 | 99.84 | 86 | 100 | 70 | 52 | 32.154 | 9.132 | 7.212 | 134.688 | 30.705 | 28.669 | 29 | 603.147 | 26.45 | 27.572 | 1254.53 | 27.355 | 27.609 | 38.483 | 28.001 | 3.8 | 2.6 | 1.2 | 0.6 | 0.2
3488 | 30/07/2025 11:24:30.998 | 100.128 | 85 | 100 | 71 | 52 | 31.806 | 9.133 | 7.219 | 134.506 | 30.723 | 28.697 | 29.013 | 603.192 | 26.462 | 27.559 | 1247.256 | 27.35 | 27.59 | 38.193 | 28.001 | 3.8 | 2.6 | 1.2 | 0.6 | 0.2
3489 | 30/07/2025 11:24:32.634 | 100.44 | 85 | 100 | 69 | 52 | 28.165 | 8.993 | 7.238 | 134.626 | 30.695 | 28.689 | 28.982 | 603.124 | 26.438 | 27.558 | 1239.808 | 27.352 | 27.6 | 38.289 | 25.001 | 3.1 | 2.8 | 0.9 | 0.5 | 0.2
3490 | 30/07/2025 11:24:34.270 | 100.824 | 85 | 100 | 72 | 52 | 32.29 | 8.962 | 7.222 | 134.819 | 30.726 | 28.685 | 28.989 | 603.129 | 26.449 | 27.552 | 1239.78 | 27.332 | 27.605 | 38.411 | 29.001 | 2.9 | 2.7 | 2 | 0.5 | 0.2
3491 | 30/07/2025 11:24:35.906 | 100.728 | 85 | 100 | 70 | 52 | 29.026 | 9.183 | 7.185 | 134.518 | 30.74 | 28.682 | 28.985 | 603.296 | 26.448 | 27.567 | 1244.834 | 27.345 | 27.604 | 38.658 | 30.001 | 3.7 | 3.7 | 0.6 | 0 | 0.3
3492 | 30/07/2025 11:24:37.543 | 100.824 | 86 | 100 | 70 | 52 | 29.496 | 9.071 | 7.071 | 134.58 | 30.731 | 28.666 | 28.999 | 603.208 | 26.454 | 27.557 | 1240.016 | 27.362 | 27.596 | 38.678 | 26.001 | 2.7 | 5 | 0.6 | 0 | 0.3
3493 | 30/07/2025 11:24:39.178 | 100.416 | 85 | 100 | 71 | 52 | 32.208 | 8.839 | 7.069 | 134.557 | 30.725 | 28.698 | 28.996 | 602.984 | 26.432 | 27.547 | 1243.354 | 27.355 | 27.568 | 38.231 | 26.001 | 2.7 | 5 | 0.6 | 0 | 0.3
3494 | 30/07/2025 11:24:40.813 | 100.488 | 84 | 100 | 71 | 52 | 31.474 | 8.914 | 7.152 | 133.502 | 30.742 | 28.69 | 28.993 | 603.084 | 26.443 | 27.567 | 1249.712 | 27.341 | 27.602 | 38.322 | 30.001 | 2.7 | 3.1 | 0.6 | 1.3 | 0.3
3495 | 30/07/2025 11:24:42.448 | 100.296 | 84 | 100 | 70 | 52 | 32.023 | 9.025 | 7.152 | 133.139 | 30.739 | 28.688 | 28.982 | 603.192 | 26.441 | 27.554 | 1238.761 | 27.329 | 27.613 | 38.647 | 21.001 | 3.8 | 2 | 0.9 | 1.3 | 0.3
3496 | 30/07/2025 11:24:44.082 | 100.632 | 84 | 100 | 70 | 52 | 32.272 | 9.264 | 7.151 | 133.071 | 30.74 | 28.67 | 28.982 | 603.223 | 26.441 | 27.555 | 1256.095 | 27.332 | 27.592 | 38.561 | 23.001 | 2 | 1.8 | 0.8 | 0.3 | 0.3
3497 | 30/07/2025 11:24:45.718 | 100.944 | 84 | 100 | 71 | 52 | 28.59 | 8.914 | 7.202 | 133.909 | 30.745 | 28.688 | 29.012 | 603.142 | 26.436 | 27.53 | 1273.568 | 27.352 | 27.584 | 38.296 | 24.001 | 2.6 | 2.5 | 1.2 | 0.3 | 0.3
3498 | 30/07/2025 11:24:47.352 | 100.344 | 85 | 100 | 71 | 52 | 30.208 | 8.989 | 7.205 | 134.552 | 30.733 | 28.699 | 28.998 | 603.183 | 26.426 | 27.562 | 1277.068 | 27.356 | 27.587 | 38.273 | 21.001 | 2.9 | 2.2 | 1.8 | 0 | 0.2
3499 | 30/07/2025 11:24:48.989 | 101.064 | 86 | 100 | 70 | 52 | 32.329 | 8.916 | 7.204 | 134.891 | 30.733 | 28.681 | 28.966 | 602.932 | 26.435 | 27.542 | 1273.047 | 27.327 | 27.601 | 38.624 | 21.001 | 2.9 | 2.2 | 1.8 | 0 | 0.2
3500 | 30/07/2025 11:24:50.625 | 100.68 | 85 | 100 | 70 | 52 | 30.904 | 8.986 | 7.202 | 134.772 | 30.74 | 28.683 | 28.983 | 603.336 | 26.431 | 27.529 | 1269.959 | 27.334 | 27.602 | 38.323 | 24.001 | 1.3 | 4.5 | 0.2 | 0 | 0.2
3501 | 30/07/2025 11:24:52.260 | 101.352 | 86 | 100 | 70 | 50 | 32.181 | 8.986 | 7.202 | 134.755 | 30.739 | 28.655 | 28.997 | 603.129 | 26.442 | 27.539 | 1269.61 | 27.337 | 27.592 | 38.502 | 27.001 | 4.4 | 2.4 | 0 | 0.8 | 0.2
3502 | 30/07/2025 11:24:53.894 | 101.232 | 88 | 100 | 70 | 53 | 31.94 | 8.991 | 7.256 | 134.338 | 30.725 | 28.688 | 28.993 | 603.148 | 26.424 | 27.537 | 1266.165 | 27.357 | 27.609 | 38.396 | 25.001 | 2.7 | 2.1 | 1 | 0.8 | 0.2
3503 | 30/07/2025 11:24:55.528 | 101.04 | 87 | 100 | 70 | 52 | 28.297 | 9.13 | 7.273 | 134.574 | 30.741 | 28.688 | 28.99 | 603.204 | 26.448 | 27.552 | 1262.02 | 27.343 | 27.577 | 38.276 | 24.001 | 3.9 | 3.1 | 0.7 | 0 | 0.2
3504 | 30/07/2025 11:24:57.163 | 100.872 | 85 | 100 | 70 | 52 | 30.606 | 9.134 | 7.239 | 134.654 | 30.741 | 28.687 | 29.006 | 603.044 | 26.434 | 27.535 | 1266.043 | 27.318 | 27.62 | 38.551 | 24.001 | 3.9 | 3.1 | 0.7 | 0 | 0.2
3505 | 30/07/2025 11:24:58.799 | 101.112 | 85 | 100 | 70 | 53 | 32.376 | 8.988 | 7.266 | 134.326 | 30.728 | 28.665 | 28.977 | 602.136 | 26.447 | 27.561 | 1260.172 | 27.354 | 27.604 | 38.617 | 28.001 | 1.9 | 2.9 | 0.9 | 0 | 0.3
3506 | 30/07/2025 11:25:00.435 | 100.776 | 84 | 100 | 70 | 52 | 29.501 | 9.12 | 7.274 | 134.567 | 30.731 | 28.671 | 29.02 | 603.336 | 26.46 | 27.557 | 1267.389 | 27.354 | 27.604 | 38.504 | 32.001 | 2.2 | 2 | 1.7 | 0.9 | 0.2
3507 | 30/07/2025 11:25:02.069 | 100.584 | 86 | 100 | 69 | 52 | 32.249 | 9.134 | 7.277 | 134.33 | 30.716 | 28.703 | 28.996 | 603.123 | 26.448 | 27.561 | 1277.048 | 27.35 | 27.586 | 38.441 | 26.001 | 2.1 | 1.7 | 1.1 | 0.9 | 0.2
3508 | 30/07/2025 11:25:03.704 | 100.248 | 84 | 100 | 71 | 52 | 31.365 | 9.154 | 7.277 | 134.805 | 30.732 | 28.687 | 28.98 | 603.14 | 26.465 | 27.55 | 1277.247 | 27.334 | 27.581 | 38.5 | 25.001 | 3.3 | 2.3 | 1.1 | 0 | 0.2
3509 | 30/07/2025 11:25:05.339 | 99.792 | 85 | 100 | 71 | 52 | 28.137 | 9.135 | 7.276 | 134.756 | 30.719 | 28.684 | 28.96 | 602.081 | 26.446 | 27.558 | 1272.243 | 27.324 | 27.611 | 38.681 | 26.001 | 2.5 | 3.1 | 1.2 | 0 | 0.2
3510 | 30/07/2025 11:25:06.973 | 99.456 | 84 | 100 | 71 | 52 | 31.12 | 9.21 | 7.276 | 134.638 | 30.726 | 28.677 | 29.008 | 601.938 | 26.451 | 27.574 | 1270.141 | 27.352 | 27.603 | 38.526 | 26.001 | 2.5 | 3.1 | 1.2 | 0 | 0.2
3511 | 30/07/2025 11:25:08.608 | 99.432 | 84 | 100 | 70 | 52 | 32.308 | 9.172 | 7.275 | 134.588 | 30.738 | 28.694 | 29.021 | 602.038 | 26.454 | 27.565 | 1279.179 | 27.349 | 27.593 | 38.222 | 26.001 | 4 | 2.6 | 1.5 | 0.6 | 0.1
3512 | 30/07/2025 11:25:10.243 | 99.408 | 85 | 100 | 70 | 52 | 29.974 | 9.137 | 7.278 | 134.303 | 30.737 | 28.69 | 28.99 | 601.775 | 26.449 | 27.562 | 1279.284 | 27.345 | 27.582 | 38.204 | 28.001 | 2.1 | 2.2 | 0.3 | 0.6 | 0.1
3513 | 30/07/2025 11:25:11.879 | 99.168 | 83 | 100 | 71 | 52 | 32.257 | 9.154 | 7.277 | 134.837 | 30.751 | 28.693 | 29.001 | 601.967 | 26.441 | 27.551 | 1286.866 | 27.33 | 27.613 | 38.409 | 27.001 | 3.4 | 1.9 | 1.8 | 0.5 | 0.2
3514 | 30/07/2025 11:25:13.515 | 98.712 | 84 | 100 | 70 | 53 | 30.807 | 9.155 | 7.277 | 134.454 | 30.741 | 28.688 | 28.966 | 601.912 | 26.449 | 27.562 | 1292.203 | 27.339 | 27.604 | 38.513 | 21.001 | 2 | 3.3 | 1.8 | 0.5 | 0.2
3515 | 30/07/2025 11:25:15.154 | 99 | 84 | 100 | 70 | 52 | 28.183 | 8.985 | 7.276 | 134.597 | 30.758 | 28.676 | 28.999 | 601.983 | 26.462 | 27.56 | 1287.194 | 27.36 | 27.601 | 38.432 | 21.001 | 2 | 3.3 | 1.8 | 0.5 | 0.2
3516 | 30/07/2025 11:25:16.788 | 98.736 | 84 | 100 | 73 | 52 | 34.582 | 9.134 | 7.293 | 134.606 | 30.732 | 28.692 | 29.003 | 601.995 | 26.438 | 27.542 | 1286.072 | 27.358 | 27.59 | 38.385 | 26.001 | 2.8 | 3.1 | 1 | 0.6 | 0.2
3517 | 30/07/2025 11:25:18.424 | 98.424 | 83 | 100 | 71 | 52 | 28.195 | 9.128 | 7.277 | 134.58 | 30.769 | 28.692 | 29.008 | 601.956 | 26.462 | 27.556 | 1276 | 27.337 | 27.583 | 38.379 | 26.001 | 3.3 | 1 | 1.9 | 0.6 | 0.3
3518 | 30/07/2025 11:25:20.061 | 98.496 | 84 | 100 | 71 | 52 | 30.763 | 9.194 | 7.276 | 134.712 | 30.745 | 28.69 | 28.993 | 602.016 | 26.44 | 27.537 | 1257.501 | 27.333 | 27.616 | 38.508 | 22.001 | 3.5 | 4.1 | 0.7 | 0 | 0.3
3519 | 30/07/2025 11:25:21.696 | 98.376 | 82 | 100 | 70 | 52 | 32.34 | 9.137 | 7.276 | 134.644 | 30.749 | 28.674 | 28.991 | 601.649 | 26.43 | 27.556 | 1277.155 | 27.333 | 27.605 | 38.527 | 25.001 | 1.7 | 3.2 | 0 | 0 | 0.3
3520 | 30/07/2025 11:25:23.330 | 97.848 | 83 | 100 | 70 | 52 | 30.253 | 8.987 | 7.276 | 134.592 | 30.741 | 28.688 | 29.017 | 602.203 | 26.43 | 27.535 | 1286.06 | 27.346 | 27.599 | 38.369 | 24.001 | 2.5 | 2.5 | 0 | 0 | 0.3
3521 | 30/07/2025 11:25:24.966 | 97.872 | 82 | 100 | 71 | 52 | 28.572 | 8.909 | 7.276 | 134.208 | 30.724 | 28.701 | 28.995 | 602.116 | 26.438 | 27.523 | 1282.639 | 27.369 | 27.583 | 38.258 | 24.001 | 2.5 | 2.5 | 0 | 0 | 0.3
3522 | 30/07/2025 11:25:26.600 | 97.296 | 83 | 100 | 70 | 52 | 32.011 | 9.129 | 7.277 | 134.771 | 30.734 | 28.684 | 28.982 | 602.006 | 26.457 | 27.541 | 1290.162 | 27.332 | 27.602 | 38.67 | 27.001 | 0.9 | 1.5 | 0.6 | 0 | 0.2
3523 | 30/07/2025 11:25:28.233 | 97.776 | 82 | 100 | 71 | 52 | 28.203 | 8.985 | 7.277 | 134.709 | 30.734 | 28.683 | 28.981 | 601.96 | 26.43 | 27.521 | 1293.591 | 27.32 | 27.589 | 38.671 | 25.001 | 3.4 | 2.3 | 1.6 | 0.9 | 0.2
3524 | 30/07/2025 11:25:29.868 | 98.16 | 83 | 100 | 70 | 53 | 31.174 | 8.971 | 7.275 | 134.737 | 30.746 | 28.667 | 29 | 601.824 | 26.453 | 27.538 | 1289.524 | 27.339 | 27.604 | 38.222 | 28.001 | 3.1 | 5.3 | 1 | 0.9 | 0.2
3525 | 30/07/2025 11:25:31.503 | 98.016 | 84 | 100 | 71 | 52 | 32.372 | 9.315 | 7.244 | 134.443 | 30.723 | 28.696 | 28.992 | 600.65 | 26.442 | 27.537 | 1287.493 | 27.357 | 27.609 | 38.378 | 25.001 | 3.4 | 3.5 | 1.8 | 0 | 0.1
3526 | 30/07/2025 11:25:33.138 | 97.704 | 84 | 100 | 70 | 52 | 29.698 | 9.243 | 7.24 | 134.489 | 30.736 | 28.691 | 28.996 | 601.873 | 26.459 | 27.553 | 1282.266 | 27.337 | 27.582 | 38.182 | 25.001 | 3.4 | 3.5 | 1.8 | 0 | 0.1
3527 | 30/07/2025 11:25:34.774 | 97.248 | 82 | 100 | 70 | 51 | 28.983 | 9.127 | 7.239 | 134.662 | 30.732 | 28.689 | 28.996 | 600.445 | 26.446 | 27.556 | 1275.508 | 27.321 | 27.6 | 38.492 | 23.001 | 2.8 | 2.3 | 1.9 | 0 | 0.1
3528 | 30/07/2025 11:25:36.410 | 97.488 | 84 | 100 | 70 | 52 | 30.876 | 9.215 | 7.24 | 134.671 | 30.709 | 28.679 | 28.971 | 600.321 | 26.459 | 27.568 | 1271.543 | 27.308 | 27.6 | 38.598 | 25.001 | 3.7 | 2.4 | 0.7 | 1.1 | 0.1
3529 | 30/07/2025 11:25:38.044 | 97.272 | 84 | 100 | 70 | 52 | 28.236 | 8.919 | 7.119 | 134.55 | 30.716 | 28.67 | 29.015 | 600.474 | 26.448 | 27.55 | 1272.065 | 27.349 | 27.606 | 38.371 | 28.001 | 3.9 | 3.7 | 1.5 | 1.1 | 0.1
3530 | 30/07/2025 11:25:39.678 | 97.032 | 82 | 100 | 70 | 52 | 31.573 | 9.137 | 7.086 | 134.316 | 30.714 | 28.7 | 28.994 | 600.41 | 26.454 | 27.577 | 1276.839 | 27.349 | 27.594 | 38.324 | 31.001 | 3 | 3.3 | 1.8 | 0.6 | 0.1
3531 | 30/07/2025 11:25:41.314 | 98.4 | 84 | 100 | 70 | 54 | 32.317 | 9.284 | 7.07 | 134.898 | 30.727 | 28.687 | 29 | 600.504 | 26.462 | 27.574 | 1276.964 | 27.343 | 27.603 | 38.2 | 26.001 | 2.7 | 4.3 | 0.9 | 0.6 | 0.1
3532 | 30/07/2025 11:25:42.949 | 98.472 | 84 | 100 | 70 | 53 | 28.955 | 9.191 | 7.059 | 134.606 | 30.723 | 28.679 | 28.977 | 600.443 | 26.447 | 27.547 | 1272.731 | 27.326 | 27.608 | 38.611 | 26.001 | 2.7 | 4.3 | 0.9 | 0.6 | 0.1
3533 | 30/07/2025 11:25:44.584 | 98.352 | 84 | 100 | 71 | 52 | 32.313 | 9.289 | 7.058 | 133.817 | 30.734 | 28.677 | 28.987 | 600.483 | 26.452 | 27.547 | 1277.011 | 27.317 | 27.599 | 38.506 | 26.001 | 1.9 | 2.4 | 2.1 | 0.8 | 0.1
3534 | 30/07/2025 11:25:46.220 | 98.16 | 83 | 100 | 71 | 52 | 30.078 | 9.018 | 7.057 | 133.057 | 30.73 | 28.685 | 29.007 | 601.375 | 26.437 | 27.543 | 1280.015 | 27.37 | 27.595 | 38.678 | 25.001 | 1.5 | 2.5 | 1.6 | 0.8 | 0.1
3535 | 30/07/2025 11:25:47.854 | 98.712 | 84 | 100 | 71 | 52 | 28.432 | 8.96 | 7.061 | 132.966 | 30.76 | 28.697 | 29.003 | 600.585 | 26.458 | 27.551 | 1269.724 | 27.343 | 27.585 | 38.194 | 28.001 | 3.1 | 3 | 1.3 | 0 | 0.2
3536 | 30/07/2025 11:25:49.489 | 99.24 | 84 | 100 | 70 | 52 | 31.937 | 9.184 | 7.058 | 133.373 | 30.737 | 28.69 | 28.99 | 600.535 | 26.438 | 27.551 | 1257.329 | 27.341 | 27.613 | 38.332 | 27.001 | 3.3 | 3.3 | 2.5 | 0 | 0.2
3537 | 30/07/2025 11:25:51.123 | 99.672 | 85 | 100 | 71 | 52 | 32.197 | 9.2 | 7.071 | 133.114 | 30.744 | 28.676 | 28.968 | 600.339 | 26.434 | 27.554 | 1264.262 | 27.323 | 27.598 | 38.459 | 27.001 | 3.3 | 3.3 | 2.5 | 0 | 0.2
3538 | 30/07/2025 11:25:52.760 | 99.792 | 86 | 100 | 71 | 52 | 28.507 | 9.007 | 7.074 | 133.321 | 30.747 | 28.671 | 28.991 | 600.552 | 26.435 | 27.552 | 1272.197 | 27.349 | 27.6 | 38.314 | 27.001 | 2.9 | 5.8 | 1.5 | 0 | 0.2
3539 | 30/07/2025 11:25:54.396 | 100.512 | 86 | 100 | 70 | 54 | 32.38 | 9.112 | 7.121 | 132.882 | 30.745 | 28.684 | 29.002 | 601.95 | 26.442 | 27.561 | 1267.645 | 27.351 | 27.602 | 38.722 | 27.001 | 3 | 2.8 | 1.3 | 0 | 0.3
3540 | 30/07/2025 11:25:56.030 | 100.584 | 87 | 100 | 70 | 52 | 29.65 | 8.841 | 7.119 | 133.05 | 30.735 | 28.696 | 29.016 | 602.007 | 26.443 | 27.547 | 1271.072 | 27.34 | 27.584 | 38.351 | 32.001 | 2.3 | 2.4 | 1 | 1.1 | 0.3
3541 | 30/07/2025 11:25:57.666 | 100.464 | 84 | 100 | 70 | 52 | 29.046 | 8.959 | 7.135 | 133.181 | 30.728 | 28.698 | 28.994 | 602.009 | 26.431 | 27.54 | 1284.982 | 27.347 | 27.618 | 38.515 | 26.001 | 2.7 | 2.8 | 1.7 | 1.1 | 0.3
3542 | 30/07/2025 11:25:59.300 | 100.608 | 87 | 100 | 70 | 52 | 32.118 | 9.13 | 7.188 | 133.187 | 30.728 | 28.674 | 28.978 | 600.403 | 26.432 | 27.533 | 1286.15 | 27.329 | 27.596 | 38.448 | 25.001 | 2 | 4 | 0.7 | 1.1 | 0.3
3543 | 30/07/2025 11:26:00.935 | 100.392 | 86 | 100 | 70 | 52 | 31.934 | 9.105 | 7.19 | 133.096 | 30.739 | 28.678 | 28.991 | 602.01 | 26.432 | 27.503 | 1275.152 | 27.354 | 27.595 | 38.26 | 25.001 | 2 | 4 | 0.7 | 1.1 | 0.3
3544 | 30/07/2025 11:26:02.570 | 100.272 | 85 | 100 | 70 | 52 | 31.684 | 8.989 | 7.205 | 133.173 | 30.745 | 28.686 | 28.998 | 601.999 | 26.466 | 27.528 | 1274.585 | 27.343 | 27.587 | 38.365 | 27.001 | 1.7 | 1.9 | 0 | 1.1 | 0.3
3545 | 30/07/2025 11:26:04.206 | 99.96 | 84 | 100 | 70 | 52 | 32.413 | 9.187 | 7.203 | 133.163 | 30.728 | 28.69 | 29.008 | 602.03 | 26.429 | 27.523 | 1288.121 | 27.345 | 27.597 | 38.215 | 28.001 | 1.9 | 2.9 | 1.2 | 0.8 | 0.2
3546 | 30/07/2025 11:26:05.841 | 99.744 | 84 | 100 | 71 | 51 | 29.182 | 8.917 | 7.221 | 132.994 | 30.732 | 28.683 | 28.981 | 601.871 | 26.445 | 27.553 | 1282.42 | 27.314 | 27.597 | 38.566 | 26.001 | 1.5 | 3.1 | 0.7 | 0.8 | 0.2
3547 | 30/07/2025 11:26:07.478 | 99.288 | 84 | 100 | 71 | 53 | 29.595 | 8.983 | 7.271 | 133.931 | 30.737 | 28.669 | 28.994 | 601.911 | 26.463 | 27.549 | 1282.763 | 27.334 | 27.597 | 38.408 | 23.001 | 3.4 | 2.7 | 0.3 | 0.5 | 0.3
3548 | 30/07/2025 11:26:09.116 | 99.432 | 84 | 100 | 70 | 52 | 32.266 | 9.023 | 7.276 | 134.402 | 30.712 | 28.696 | 29.005 | 602.002 | 26.439 | 27.556 | 1284.967 | 27.368 | 27.598 | 38.335 | 23.001 | 3.4 | 2.7 | 0.3 | 0.5 | 0.3
3549 | 30/07/2025 11:26:10.754 | 99.312 | 84 | 100 | 70 | 53 | 31.418 | 9.148 | 7.278 | 134.594 | 30.711 | 28.692 | 28.994 | 601.834 | 26.463 | 27.571 | 1285.079 | 27.338 | 27.574 | 38.125 | 24.001 | 3.7 | 2.7 | 1.2 | 0.5 | 0.3
3550 | 30/07/2025 11:26:12.390 | 99.72 | 84 | 100 | 70 | 52 | 31.973 | 9.2 | 7.275 | 134.711 | 30.713 | 28.701 | 29.008 | 601.956 | 26.459 | 27.564 | 1293.14 | 27.356 | 27.604 | 38.196 | 28.001 | 2.6 | 3.6 | 1.3 | 0 | 0.3
3551 | 30/07/2025 11:26:14.027 | 100.032 | 83 | 99 | 71 | 52 | 32.186 | 9.141 | 7.278 | 134.662 | 30.718 | 28.683 | 28.972 | 601.857 | 26.456 | 27.555 | 1291.923 | 27.31 | 27.601 | 38.505 | 25.001 | 3.6 | 3.4 | 1.5 | 0 | 0.3
3552 | 30/07/2025 11:26:15.662 | 99.24 | 85 | 100 | 70 | 52 | 28.597 | 9.087 | 7.275 | 134.539 | 30.714 | 28.675 | 29.001 | 601.917 | 26.446 | 27.555 | 1294.564 | 27.347 | 27.615 | 38.534 | 26.001 | 1.7 | 2 | 1 | 0.6 | 0.3
3553 | 30/07/2025 11:26:17.296 | 99.216 | 84 | 100 | 71 | 52 | 29.972 | 9.269 | 7.278 | 134.201 | 30.731 | 28.689 | 28.979 | 601.837 | 26.444 | 27.564 | 1289.689 | 27.348 | 27.587 | 38.466 | 29.001 | 2.2 | 2.4 | 1.4 | 0.6 | 0.2
3554 | 30/07/2025 11:26:18.933 | 98.712 | 84 | 100 | 71 | 52 | 32.329 | 9.128 | 7.276 | 134.641 | 30.757 | 28.69 | 29.007 | 602.014 | 26.446 | 27.55 | 1277.121 | 27.336 | 27.6 | 38.256 | 29.001 | 2.2 | 2.4 | 1.4 | 0.6 | 0.2
3555 | 30/07/2025 11:26:20.571 | 98.424 | 82 | 100 | 70 | 52 | 28.851 | 9.283 | 7.277 | 134.676 | 30.733 | 28.684 | 28.992 | 601.937 | 26.44 | 27.562 | 1273.004 | 27.327 | 27.596 | 38.452 | 25.001 | 2.3 | 3 | 1.6 | 0.8 | 0.3
3556 | 30/07/2025 11:26:22.206 | 98.28 | 82 | 100 | 70 | 52 | 32.132 | 9.126 | 7.275 | 134.592 | 30.737 | 28.678 | 28.983 | 602.074 | 26.444 | 27.549 | 1261.471 | 27.321 | 27.605 | 38.429 | 28.001 | 2.6 | 3.7 | 0.6 | 0.8 | 0.3
3557 | 30/07/2025 11:26:23.841 | 98.472 | 84 | 100 | 69 | 52 | 31.915 | 8.99 | 7.291 | 134.491 | 30.748 | 28.681 | 28.999 | 601.926 | 26.445 | 27.554 | 1267.348 | 27.364 | 27.607 | 38.462 | 21.001 | 3 | 4.5 | 0.7 | 0 | 0.3
3558 | 30/07/2025 11:26:25.475 | 98.112 | 83 | 100 | 71 | 52 | 28.25 | 9.132 | 7.295 | 134.491 | 30.75 | 28.698 | 29.014 | 602.057 | 26.451 | 27.554 | 1260.155 | 27.349 | 27.577 | 38.451 | 24.001 | 0.8 | 2.8 | 1.2 | 0 | 0.2
3559 | 30/07/2025 11:26:27.110 | 98.448 | 82 | 100 | 72 | 52 | 30.659 | 9.267 | 7.276 | 134.835 | 30.743 | 28.692 | 28.996 | 602.133 | 26.445 | 27.541 | 1264.512 | 27.337 | 27.614 | 38.183 | 24.001 | 0.8 | 2.8 | 1.2 | 0 | 0.2
3560 | 30/07/2025 11:26:28.745 | 98.88 | 83 | 100 | 69 | 52 | 32.362 | 9.007 | 7.276 | 134.464 | 30.739 | 28.685 | 28.979 | 601.878 | 26.434 | 27.566 | 1269.7 | 27.319 | 27.605 | 38.678 | 27.001 | 2 | 3 | 1.4 | 0 | 0.2
3561 | 30/07/2025 11:26:30.378 | 98.664 | 82 | 100 | 70 | 52 | 29.531 | 9.214 | 7.274 | 134.665 | 30.741 | 28.674 | 28.997 | 601.877 | 26.437 | 27.542 | 1266.607 | 27.341 | 27.623 | 38.399 | 29.001 | 3.3 | 3.1 | 0.9 | 0 | 0.2
3562 | 30/07/2025 11:26:32.012 | 98.832 | 84 | 100 | 70 | 51 | 32.272 | 8.986 | 7.278 | 134.563 | 30.739 | 28.684 | 28.999 | 601.784 | 26.426 | 27.542 | 1269.596 | 27.344 | 27.589 | 38.612 | 22.001 | 3.8 | 4 | 0.8 | 1.1 | 0.3
3563 | 30/07/2025 11:26:33.646 | 98.952 | 84 | 100 | 69 | 52 | 31.469 | 8.991 | 7.275 | 134.638 | 30.733 | 28.692 | 29.009 | 602.177 | 26.435 | 27.507 | 1284.653 | 27.339 | 27.589 | 38.12 | 27.001 | 2.1 | 3.2 | 1.3 | 1.1 | 0.2
3564 | 30/07/2025 11:26:35.280 | 99.264 | 84 | 100 | 71 | 52 | 28.202 | 9.13 | 7.276 | 134.59 | 30.736 | 28.698 | 28.99 | 601.972 | 26.433 | 27.533 | 1270.751 | 27.338 | 27.605 | 38.392 | 27.001 | 2.1 | 3.2 | 1.3 | 1.1 | 0.2
3565 | 30/07/2025 11:26:36.915 | 99.048 | 84 | 100 | 71 | 52 | 31.241 | 8.984 | 7.276 | 134.74 | 30.734 | 28.676 | 28.982 | 601.818 | 26.462 | 27.541 | 1258.074 | 27.326 | 27.578 | 38.502 | 25.001 | 4.2 | 5.4 | 1.2 | 0.9 | 0.2
3566 | 30/07/2025 11:26:38.549 | 98.4 | 84 | 100 | 71 | 51 | 28.697 | 8.851 | 7.275 | 134.622 | 30.72 | 28.661 | 28.981 | 601.941 | 26.447 | 27.535 | 1256.552 | 27.357 | 27.614 | 38.413 | 21.001 | 2.8 | 4.6 | 1 | 0.9 | 0.2
3567 | 30/07/2025 11:26:40.185 | 99.192 | 84 | 100 | 70 | 54 | 30.126 | 8.845 | 7.278 | 134.518 | 30.739 | 28.69 | 29.01 | 601.852 | 26.468 | 27.547 | 1255.498 | 27.342 | 27.591 | 38.342 | 25.001 | 2 | 3.6 | 2.1 | 0.9 | 0.2
3568 | 30/07/2025 11:26:41.820 | 98.712 | 84 | 100 | 72 | 52 | 32.322 | 8.986 | 7.276 | 134.731 | 30.719 | 28.697 | 29.003 | 602.041 | 26.454 | 27.561 | 1247.197 | 27.347 | 27.604 | 38.293 | 27.001 | 0.8 | 4.2 | 1.6 | 0.9 | 0.1
3569 | 30/07/2025 11:26:43.454 | 98.736 | 83 | 100 | 70 | 50 | 30.995 | 8.984 | 7.293 | 134.73 | 30.714 | 28.684 | 28.973 | 601.953 | 26.444 | 27.545 | 1249.71 | 27.307 | 27.603 | 40.262 | 27.001 | 2.5 | 1.8 | 0.7 | 0 | 0.1
3570 | 30/07/2025 11:26:45.089 | 98.832 | 83 | 100 | 70 | 52 | 28.298 | 8.988 | 7.29 | 134.678 | 30.719 | 28.671 | 29.002 | 602.002 | 26.44 | 27.555 | 1239.254 | 27.34 | 27.6 | 40.147 | 27.001 | 2.5 | 1.8 | 0.7 | 0 | 0.1
3571 | 30/07/2025 11:26:46.723 | 99.456 | 85 | 100 | 71 | 52 | 31.66 | 8.84 | 7.293 | 134.38 | 30.705 | 28.699 | 29.002 | 601.841 | 26.454 | 27.57 | 1232.353 | 27.37 | 27.595 | 40.17 | 28.001 | 2.4 | 4 | 0.6 | 0 | 0.1
3572 | 30/07/2025 11:26:48.358 | 99.384 | 84 | 100 | 72 | 52 | 28.32 | 8.981 | 7.277 | 134.417 | 30.735 | 28.697 | 29.013 | 601.843 | 26.434 | 27.564 | 1228.373 | 27.355 | 27.582 | 40.144 | 24.001 | 1.8 | 2.2 | 0.7 | 0.1 | 0.1
3573 | 30/07/2025 11:26:49.993 | 99.816 | 85 | 100 | 71 | 52 | 30.624 | 9.208 | 7.276 | 134.549 | 30.712 | 28.69 | 28.985 | 601.958 | 26.445 | 27.568 | 1229.873 | 27.365 | 27.608 | 39.989 | 27.001 | 3.3 | 3.2 | 1.2 | 0.1 | 0.1
3574 | 30/07/2025 11:26:51.627 | 99.864 | 85 | 100 | 70 | 52 | 32.365 | 9.075 | 7.277 | 134.591 | 30.737 | 28.685 | 28.953 | 601.971 | 26.464 | 27.547 | 1233.354 | 27.307 | 27.594 | 40.287 | 28.001 | 3.4 | 1.6 | 0.4 | 0 | 0.1
3575 | 30/07/2025 11:26:53.261 | 99.48 | 84 | 100 | 70 | 54 | 30.285 | 9.131 | 7.308 | 134.649 | 30.738 | 28.664 | 29.006 | 602.029 | 26.449 | 27.546 | 1257.652 | 27.358 | 27.615 | 40.243 | 28.001 | 3.4 | 1.6 | 0.4 | 0 | 0.1
3576 | 30/07/2025 11:26:54.896 | 100.008 | 84 | 100 | 70 | 52 | 28.481 | 9.133 | 7.33 | 134.293 | 30.745 | 28.687 | 29.003 | 601.835 | 26.449 | 27.549 | 1269.814 | 27.347 | 27.59 | 40.135 | 22.001 | 3.6 | 1.7 | 0.6 | 0 | 0.1
3577 | 30/07/2025 11:26:56.532 | 99.456 | 85 | 100 | 71 | 52 | 31.514 | 8.989 | 7.328 | 134.674 | 30.74 | 28.708 | 28.995 | 601.945 | 26.439 | 27.548 | 1267.206 | 27.353 | 27.583 | 39.993 | 23.001 | 3 | 3.1 | 0 | 0 | 0.1
3578 | 30/07/2025 11:26:58.167 | 99.144 | 84 | 100 | 70 | 52 | 28.145 | 9.182 | 7.329 | 134.672 | 30.76 | 28.696 | 28.985 | 601.86 | 26.449 | 27.564 | 1269.425 | 27.333 | 27.606 | 40.258 | 29.001 | 2.6 | 3.3 | 0.7 | 0 | 0.2
3579 | 30/07/2025 11:26:59.802 | 99.24 | 82 | 100 | 71 | 52 | 31.16 | 9.128 | 7.343 | 134.71 | 30.736 | 28.686 | 28.964 | 602.012 | 26.438 | 27.549 | 1257.529 | 27.319 | 27.612 | 40.279 | 27.001 | 3.7 | 3 | 0.7 | 0.5 | 0.1
3580 | 30/07/2025 11:27:01.436 | 99.168 | 83 | 100 | 70 | 52 | 32.408 | 9.137 | 7.344 | 134.526 | 30.742 | 28.673 | 29.001 | 601.953 | 26.449 | 27.561 | 1259.852 | 27.355 | 27.607 | 40.13 | 28.001 | 3 | 3.8 | 0.3 | 0.5 | 0.1
3581 | 30/07/2025 11:27:03.073 | 99.312 | 83 | 100 | 70 | 52 | 29.546 | 9.277 | 7.347 | 134.593 | 30.739 | 28.69 | 29.004 | 601.491 | 26.442 | 27.548 | 1261.504 | 27.34 | 27.584 | 40.137 | 28.001 | 3 | 3.8 | 0.3 | 0.5 | 0.1
3582 | 30/07/2025 11:27:04.709 | 99.408 | 85 | 100 | 71 | 52 | 32.353 | 9.215 | 7.292 | 134.465 | 30.738 | 28.693 | 29 | 601.904 | 26.419 | 27.568 | 1266.793 | 27.356 | 27.592 | 40.153 | 28.001 | 2.3 | 4.5 | 0.6 | 0.8 | 0.2
3583 | 30/07/2025 11:27:06.343 | 99.36 | 84 | 100 | 70 | 52 | 30.887 | 9.125 | 7.277 | 134.765 | 30.749 | 28.685 | 28.986 | 603.205 | 26.436 | 27.531 | 1275.417 | 27.313 | 27.607 | 40.296 | 21.001 | 2.7 | 3.6 | 1.3 | 0.8 | 0.2
3584 | 30/07/2025 11:27:07.978 | 99.072 | 83 | 100 | 71 | 54 | 28.285 | 9.136 | 7.274 | 134.766 | 30.726 | 28.675 | 28.99 | 603.116 | 26.431 | 27.524 | 1277.005 | 27.348 | 27.618 | 38.457 | 29.001 | 1.3 | 3.9 | 0.6 | 0.6 | 0.2
3585 | 30/07/2025 11:27:09.613 | 98.856 | 83 | 100 | 70 | 52 | 31.621 | 9.134 | 7.277 | 134.499 | 30.726 | 28.68 | 29.004 | 603.046 | 26.435 | 27.545 | 1270.153 | 27.353 | 27.597 | 38.409 | 27.001 | 3.4 | 3 | 0.3 | 0.6 | 0.1
3586 | 30/07/2025 11:27:11.260 | 98.592 | 83 | 100 | 70 | 51 | 32.399 | 8.991 | 7.294 | 134.552 | 30.724 | 28.692 | 29.01 | 603.146 | 26.433 | 27.531 | 1267.006 | 27.349 | 27.587 | 38.077 | 27.001 | 3.4 | 3 | 0.3 | 0.6 | 0.1
3587 | 30/07/2025 11:27:12.897 | 98.256 | 83 | 100 | 70 | 52 | 29.079 | 9.04 | 7.293 | 134.681 | 30.725 | 28.703 | 28.988 | 603.289 | 26.442 | 27.545 | 1268.644 | 27.339 | 27.602 | 38.442 | 27.001 | 1.9 | 2.7 | 0.6 | 0 | 0.1
3588 | 30/07/2025 11:27:14.535 | 98.376 | 84 | 99 | 70 | 52 | 32.331 | 9.223 | 7.292 | 134.603 | 30.733 | 28.697 | 29.001 | 603.274 | 26.439 | 27.534 | 1267.091 | 27.323 | 27.626 | 38.474 | 29.001 | 1.7 | 2.8 | 0.7 | 0 | 0.2
3589 | 30/07/2025 11:27:16.172 | 98.832 | 83 | 100 | 70 | 52 | 30.399 | 9.261 | 7.291 | 134.606 | 30.712 | 28.658 | 28.99 | 601.935 | 26.439 | 27.577 | 1260.168 | 27.352 | 27.614 | 38.508 | 27.001 | 1.6 | 3 | 0.7 | 0.6 | 0.2
3590 | 30/07/2025 11:27:17.808 | 99.144 | 84 | 100 | 70 | 52 | 28.581 | 9.131 | 7.277 | 134.466 | 30.741 | 28.693 | 28.987 | 601.903 | 26.454 | 27.554 | 1252.99 | 27.338 | 27.584 | 38.617 | 25.001 | 0.9 | 3.4 | 0.7 | 0.6 | 0.2
3591 | 30/07/2025 11:27:19.444 | 98.976 | 83 | 100 | 70 | 53 | 32.052 | 9.29 | 7.276 | 134.792 | 30.719 | 28.697 | 28.991 | 602.878 | 26.446 | 27.552 | 1253.879 | 27.357 | 27.589 | 38.227 | 28.001 | 1.6 | 2.3 | 1.3 | 0.5 | 0.2
3592 | 30/07/2025 11:27:21.079 | 99.144 | 84 | 100 | 70 | 52 | 32.233 | 8.988 | 7.278 | 134.849 | 30.721 | 28.687 | 28.989 | 602.032 | 26.452 | 27.562 | 1252.802 | 27.323 | 27.608 | 38.566 | 28.001 | 1.6 | 2.3 | 1.3 | 0.5 | 0.2
3593 | 30/07/2025 11:27:22.714 | 99 | 85 | 100 | 70 | 52 | 28.64 | 9.13 | 7.274 | 134.497 | 30.731 | 28.668 | 28.985 | 602.028 | 26.45 | 27.561 | 1244.762 | 27.333 | 27.612 | 38.376 | 24.001 | 1.4 | 3 | 1.2 | 0.5 | 0.2
3594 | 30/07/2025 11:27:24.348 | 99.168 | 83 | 100 | 70 | 52 | 32.417 | 8.983 | 7.294 | 134.865 | 30.725 | 28.664 | 28.997 | 601.944 | 26.46 | 27.564 | 1244.76 | 27.357 | 27.591 | 38.471 | 27.001 | 2.7 | 3.2 | 0.6 | 0.5 | 0.2
3595 | 30/07/2025 11:27:25.984 | 98.76 | 83 | 100 | 70 | 52 | 29.742 | 9.112 | 7.305 | 134.653 | 30.744 | 28.696 | 29.014 | 601.967 | 26.43 | 27.546 | 1237.581 | 27.345 | 27.587 | 38.278 | 26.001 | 1.8 | 1.6 | 2.2 | 0.5 | 0.3
3596 | 30/07/2025 11:27:27.621 | 98.592 | 83 | 100 | 70 | 52 | 28.89 | 9.007 | 7.328 | 134.442 | 30.738 | 28.687 | 28.999 | 601.878 | 26.444 | 27.566 | 1247.051 | 27.344 | 27.6 | 38.386 | 25.001 | 5.3 | 3.6 | 0.8 | 0.5 | 0.3
3597 | 30/07/2025 11:27:29.256 | 97.776 | 81 | 100 | 70 | 53 | 32.18 | 8.91 | 7.328 | 134.808 | 30.752 | 28.69 | 28.97 | 602.006 | 26.599 | 27.542 | 1253.749 | 27.319 | 27.594 | 38.552 | 25.001 | 5.3 | 3.6 | 0.8 | 0.5 | 0.3
3598 | 30/07/2025 11:27:30.891 | 97.68 | 83 | 99 | 70 | 52 | 31.951 | 8.931 | 7.326 | 134.688 | 30.744 | 28.678 | 28.998 | 601.962 | 26.598 | 27.541 | 1257.54 | 27.355 | 27.621 | 38.402 | 26.001 | 3.4 | 3.7 | 1.3 | 0.5 | 0.3
3599 | 30/07/2025 11:27:32.524 | 98.232 | 83 | 100 | 70 | 52 | 31.6 | 8.983 | 7.326 | 134.617 | 30.732 | 28.676 | 29.018 | 601.929 | 26.592 | 27.555 | 1260.282 | 27.356 | 27.595 | 38.426 | 26.001 | 3.3 | 4 | 0.6 | 0.1 | 0.2
3600 | 30/07/2025 11:27:34.160 | 97.728 | 83 | 100 | 71 | 52 | 32.422 | 9.132 | 7.31 | 134.396 | 30.733 | 28.7 | 29.006 | 601.93 | 26.584 | 27.556 | 1257.861 | 27.362 | 27.584 | 38.206 | 24.001 | 3.7 | 3.1 | 1.6 | 0.1 | 0.3
3601 | 30/07/2025 11:27:35.795 | 98.232 | 84 | 100 | 71 | 52 | 29.113 | 9.212 | 7.294 | 134.14 | 30.729 | 28.687 | 28.982 | 601.898 | 26.599 | 27.564 | 1253.915 | 27.336 | 27.601 | 38.383 | 30.001 | 1.8 | 2.8 | 1.4 | 0.5 | 0.3
3602 | 30/07/2025 11:27:37.430 | 98.688 | 82 | 100 | 71 | 52 | 29.456 | 9.135 | 7.326 | 133.172 | 30.744 | 28.686 | 28.987 | 602.078 | 26.586 | 27.536 | 1255.352 | 27.312 | 27.614 | 38.554 | 29.001 | 2 | 4 | 0 | 0.5 | 0.3
3603 | 30/07/2025 11:27:39.065 | 98.736 | 83 | 100 | 70 | 52 | 32.258 | 9.13 | 7.327 | 133.055 | 30.739 | 28.669 | 29.01 | 602.012 | 26.582 | 27.539 | 1259.63 | 27.357 | 27.602 | 38.503 | 29.001 | 2 | 4 | 0 | 0.5 | 0.3
3604 | 30/07/2025 11:27:40.700 | 98.664 | 84 | 100 | 70 | 53 | 28.516 | 9.132 | 7.327 | 133.168 | 30.743 | 28.689 | 28.995 | 602.042 | 26.584 | 27.535 | 1261.559 | 27.355 | 27.605 | 38.369 | 26.001 | 1.9 | 3.9 | 0.6 | 0 | 0.3
3605 | 30/07/2025 11:27:42.336 | 98.304 | 82 | 100 | 71 | 52 | 31.935 | 9.136 | 7.329 | 132.845 | 30.732 | 28.688 | 28.982 | 601.87 | 26.588 | 27.543 | 1272.585 | 27.338 | 27.569 | 38.353 | 26.001 | 2 | 2.8 | 2.2 | 0 | 0.3
3606 | 30/07/2025 11:27:43.971 | 98.4 | 83 | 100 | 71 | 51 | 32.26 | 9.132 | 7.328 | 133.323 | 30.743 | 28.691 | 29.003 | 602.034 | 26.592 | 27.531 | 1279.149 | 27.332 | 27.611 | 38.365 | 28.001 | 4.3 | 3.5 | 0.8 | 0.8 | 0.3
3607 | 30/07/2025 11:27:45.608 | 98.76 | 84 | 100 | 70 | 52 | 28.598 | 9.184 | 7.292 | 133.265 | 30.733 | 28.678 | 28.985 | 603.284 | 26.593 | 27.526 | 1287.857 | 27.344 | 27.602 | 38.606 | 24.001 | 2.6 | 4.3 | 1.5 | 0.8 | 0.2
3608 | 30/07/2025 11:27:47.242 | 99 | 84 | 100 | 71 | 52 | 30.038 | 9.139 | 7.296 | 133.202 | 30.729 | 28.676 | 29.012 | 603.164 | 26.618 | 27.552 | 1280.311 | 27.355 | 27.59 | 38.391 | 24.001 | 2.6 | 4.3 | 1.5 | 0.8 | 0.2
3609 | 30/07/2025 11:27:48.878 | 99.864 | 84 | 100 | 70 | 52 | 32.319 | 9.161 | 7.345 | 133.109 | 30.726 | 28.697 | 29.002 | 602.459 | 26.6 | 27.552 | 1284.087 | 27.349 | 27.594 | 38.373 | 20.001 | 3 | 3.4 | 1.8 | 1.6 | 0.2
3610 | 30/07/2025 11:27:50.515 | 99.984 | 84 | 100 | 70 | 53 | 29.047 | 9.132 | 7.33 | 133.309 | 30.718 | 28.684 | 28.992 | 601.714 | 26.604 | 27.55 | 1277.034 | 27.342 | 27.568 | 38.346 | 22.001 | 2.4 | 2.5 | 1 | 1.6 | 0.2
3611 | 30/07/2025 11:27:52.149 | 100.008 | 84 | 100 | 70 | 52 | 32.209 | 8.844 | 7.292 | 133.279 | 30.708 | 28.691 | 28.99 | 602.125 | 26.451 | 27.557 | 1267.36 | 27.321 | 27.611 | 38.548 | 29.001 | 1.9 | 2.5 | 0.8 | 1.2 | 0.2
3612 | 30/07/2025 11:27:53.785 | 100.56 | 86 | 100 | 70 | 52 | 31.99 | 9.13 | 7.292 | 133.211 | 30.716 | 28.663 | 28.98 | 601.95 | 26.6 | 27.566 | 1274.913 | 27.34 | 27.6 | 38.559 | 25.001 | 2.3 | 3.2 | 0.6 | 1.2 | 0.2
3613 | 30/07/2025 11:27:55.424 | 100.704 | 86 | 100 | 71 | 52 | 28.322 | 8.918 | 7.293 | 133.121 | 30.723 | 28.686 | 29.017 | 601.861 | 26.596 | 27.564 | 1274.825 | 27.347 | 27.59 | 38.585 | 26.001 | 1.1 | 4.3 | 0.6 | 0.1 | 0.2
3614 | 30/07/2025 11:27:57.060 | 99.984 | 85 | 100 | 72 | 50 | 30.759 | 9.099 | 7.328 | 133.033 | 30.715 | 28.692 | 28.999 | 601.895 | 26.599 | 27.56 | 1269.544 | 27.365 | 27.597 | 38.157 | 26.001 | 1.1 | 4.3 | 0.6 | 0.1 | 0.2
3615 | 30/07/2025 11:27:58.697 | 100.152 | 86 | 100 | 70 | 53 | 29.136 | 8.987 | 7.327 | 133.262 | 30.717 | 28.687 | 29.006 | 602.124 | 26.59 | 27.549 | 1257.485 | 27.338 | 27.591 | 38.189 | 27.001 | 3.3 | 4 | 0.1 | 0.1 | 0.2
3616 | 30/07/2025 11:28:00.339 | 100.392 | 87 | 100 | 70 | 52 | 29.575 | 9.135 | 7.327 | 133.177 | 30.741 | 28.693 | 28.978 | 602.002 | 26.603 | 27.554 | 1257.409 | 27.321 | 27.61 | 38.546 | 26.001 | 3 | 3.4 | 0.7 | 0.1 | 0.2
3617 | 30/07/2025 11:28:01.975 | 99.768 | 85 | 100 | 71 | 51 | 32.264 | 9.212 | 7.328 | 133.16 | 30.756 | 28.672 | 28.995 | 601.935 | 26.601 | 27.559 | 1259.692 | 27.357 | 27.595 | 38.519 | 22.001 | 3.1 | 2.9 | 0.3 | 0.1 | 0.2
3618 | 30/07/2025 11:28:03.611 | 100.152 | 85 | 100 | 70 | 51 | 31.57 | 9.251 | 7.328 | 133.195 | 30.744 | 28.7 | 29.003 | 601.875 | 26.59 | 27.54 | 1265.794 | 27.351 | 27.598 | 38.295 | 27.001 | 2.2 | 3.4 | 0.6 | 0.6 | 0.1
3619 | 30/07/2025 11:28:05.248 | 99.672 | 85 | 100 | 70 | 51 | 28.264 | 9.109 | 7.328 | 133.132 | 30.749 | 28.688 | 28.989 | 603.085 | 26.597 | 27.544 | 1271.558 | 27.337 | 27.592 | 38.298 | 27.001 | 2.2 | 3.4 | 0.6 | 0.6 | 0.1
3620 | 30/07/2025 11:28:06.888 | 99.6 | 84 | 100 | 70 | 53 | 31.322 | 9.129 | 7.295 | 133.152 | 30.744 | 28.691 | 28.987 | 603.3 | 26.598 | 27.546 | 1274.249 | 27.312 | 27.613 | 38.583 | 27.001 | 2.6 | 1.6 | 0.6 | 0.6 | 0.2
3621 | 30/07/2025 11:28:08.524 | 99.6 | 84 | 100 | 70 | 52 | 28.715 | 9.023 | 7.293 | 133.273 | 30.743 | 28.679 | 28.971 | 603.078 | 26.59 | 27.552 | 1272.49 | 27.311 | 27.605 | 38.642 | 22.001 | 2.4 | 4.1 | 0 | 0.2 | 0.2
3622 | 30/07/2025 11:28:10.159 | 99.264 | 84 | 100 | 70 | 53 | 30.115 | 9.131 | 7.291 | 133.196 | 30.743 | 28.674 | 29.025 | 603.34 | 26.585 | 27.543 | 1271.039 | 27.359 | 27.604 | 38.477 | 28.001 | 2.9 | 3.9 | 0.9 | 0.2 | 0.2
3623 | 30/07/2025 11:28:11.793 | 99.312 | 83 | 100 | 70 | 52 | 32.335 | 8.989 | 7.294 | 132.995 | 30.735 | 28.707 | 29.006 | 603.061 | 26.578 | 27.552 | 1267.557 | 27.355 | 27.585 | 38.155 | 27.001 | 2.7 | 5.1 | 1.4 | 0 | 0.3
3624 | 30/07/2025 11:28:13.451 | 99.48 | 87 | 100 | 70 | 53 | 30.94 | 9.187 | 7.294 | 133.166 | 30.742 | 28.687 | 28.991 | 603.019 | 26.589 | 27.532 | 1273.984 | 27.336 | 27.594 | 38.371 | 29.001 | 2.8 | 2.3 | 0.6 | 0 | 0.3
3625 | 30/07/2025 11:28:15.088 | 99.408 | 84 | 100 | 71 | 51 | 28.33 | 9.17 | 7.292 | 134.767 | 30.734 | 28.682 | 28.973 | 603.427 | 26.576 | 27.515 | 1274.503 | 27.319 | 27.623 | 38.299 | 29.001 | 2.8 | 2.3 | 0.6 | 0 | 0.3
3626 | 30/07/2025 11:28:16.725 | 98.952 | 84 | 100 | 71 | 52 | 31.935 | 9.166 | 7.292 | 134.75 | 30.74 | 28.675 | 28.986 | 603.156 | 26.593 | 27.539 | 1276.715 | 27.338 | 27.602 | 38.315 | 27.001 | 3.7 | 3 | 2.1 | 0.8 | 0.3
3627 | 30/07/2025 11:28:18.358 | 98.64 | 83 | 100 | 69 | 52 | 28.376 | 9.169 | 7.275 | 134.478 | 30.726 | 28.683 | 28.996 | 603.198 | 26.587 | 27.52 | 1279.808 | 27.372 | 27.596 | 38.297 | 22.001 | 1.6 | 3 | 0.9 | 0.8 | 0.2
3628 | 30/07/2025 11:28:19.992 | 98.088 | 84 | 100 | 70 | 52 | 30.591 | 9.393 | 7.272 | 134.407 | 30.733 | 28.681 | 28.992 | 603.011 | 26.588 | 27.546 | 1279.189 | 27.342 | 27.582 | 38.241 | 24.001 | 2.2 | 1.9 | 1 | 0 | 0.2
3629 | 30/07/2025 11:28:21.635 | 97.632 | 82 | 100 | 70 | 52 | 32.358 | 8.983 | 7.185 | 134.85 | 30.73 | 28.686 | 28.99 | 603.305 | 26.602 | 27.538 | 1286.816 | 27.331 | 27.617 | 38.323 | 24.001 | 2.4 | 2.8 | 1.2 | 0 | 0.2
3630 | 30/07/2025 11:28:23.269 | 98.064 | 85 | 100 | 70 | 51 | 30.313 | 9.182 | 7.184 | 134.617 | 30.723 | 28.687 | 28.962 | 603.148 | 26.613 | 27.569 | 1296.557 | 27.331 | 27.609 | 38.431 | 24.001 | 2.4 | 2.8 | 1.2 | 0 | 0.2
3631 | 30/07/2025 11:28:24.905 | 98.304 | 83 | 99 | 70 | 52 | 28.533 | 9.289 | 7.187 | 134.634 | 30.724 | 28.665 | 29.001 | 603.158 | 26.604 | 27.559 | 1299.778 | 27.342 | 27.588 | 38.585 | 28.001 | 2.9 | 2.7 | 1.2 | 0 | 0.2
3632 | 30/07/2025 11:28:26.541 | 98.016 | 83 | 100 | 70 | 53 | 31.495 | 9.123 | 7.187 | 134.195 | 30.714 | 28.694 | 28.992 | 603.155 | 26.597 | 27.571 | 1297.269 | 27.36 | 27.596 | 38.547 | 23.001 | 3 | 3 | 0.6 | 0 | 0.2
3633 | 30/07/2025 11:28:28.179 | 98.04 | 84 | 100 | 70 | 52 | 28.221 | 9.284 | 7.182 | 134.87 | 30.725 | 28.692 | 28.994 | 603.036 | 26.608 | 27.561 | 1297.161 | 27.341 | 27.573 | 38.112 | 30.001 | 2.6 | 4.1 | 1 | 0 | 0.2
3634 | 30/07/2025 11:28:29.816 | 98.112 | 84 | 100 | 71 | 52 | 31.12 | 9.168 | 7.152 | 134.837 | 30.72 | 28.698 | 28.99 | 603.185 | 26.595 | 27.559 | 1290.581 | 27.331 | 27.619 | 38.804 | 26.001 | 1.6 | 3.2 | 1.7 | 0 | 0.2
3635 | 30/07/2025 11:28:31.451 | 98.064 | 82 | 100 | 71 | 52 | 32.41 | 9.133 | 7.151 | 134.671 | 30.712 | 28.66 | 28.971 | 603.084 | 26.592 | 27.568 | 1287.079 | 27.341 | 27.604 | 38.355 | 28.001 | 1.4 | 3.4 | 1.9 | 0 | 0.3
3636 | 30/07/2025 11:28:33.087 | 97.824 | 83 | 100 | 72 | 52 | 29.636 | 9.273 | 7.152 | 134.56 | 30.735 | 28.686 | 29.008 | 603.168 | 26.599 | 27.545 | 1294.445 | 27.356 | 27.597 | 38.318 | 28.001 | 1.4 | 3.4 | 1.9 | 0 | 0.3
3637 | 30/07/2025 11:28:34.723 | 97.992 | 83 | 100 | 70 | 52 | 28.971 | 9.137 | 7.239 | 134.494 | 30.746 | 28.7 | 29.001 | 602.996 | 26.589 | 27.557 | 1282.493 | 27.366 | 27.59 | 38.037 | 28.001 | 2.5 | 4 | 2.1 | 0 | 0.3
3638 | 30/07/2025 11:28:36.360 | 98.28 | 83 | 100 | 71 | 52 | 30.992 | 9.132 | 7.239 | 134.795 | 30.75 | 28.688 | 28.997 | 603.305 | 26.585 | 27.534 | 1277.119 | 27.346 | 27.593 | 38.057 | 28.001 | 3.1 | 2.8 | 1.2 | 0.5 | 0.3
3639 | 30/07/2025 11:28:37.996 | 97.56 | 83 | 100 | 71 | 52 | 28.265 | 9.134 | 7.204 | 134.617 | 30.754 | 28.684 | 28.983 | 603.212 | 26.597 | 27.567 | 1276.848 | 27.326 | 27.614 | 38.45 | 23.001 | 2.4 | 2.2 | 1.2 | 0.5 | 0.3
3640 | 30/07/2025 11:28:39.632 | 97.992 | 83 | 100 | 72 | 52 | 31.657 | 9.189 | 7.218 | 134.758 | 30.744 | 28.674 | 28.979 | 601.975 | 26.609 | 27.556 | 1287.362 | 27.35 | 27.597 | 38.43 | 22.001 | 4 | 2.6 | 1.2 | 0 | 0.3
3641 | 30/07/2025 11:28:41.266 | 97.56 | 83 | 100 | 70 | 53 | 32.385 | 9.016 | 7.238 | 133.07 | 30.736 | 28.705 | 28.996 | 601.966 | 26.581 | 27.539 | 1279.812 | 27.355 | 27.603 | 38.4 | 22.001 | 4 | 2.6 | 1.2 | 0 | 0.3
3642 | 30/07/2025 11:28:42.901 | 97.752 | 82 | 100 | 70 | 52 | 29.168 | 8.91 | 7.277 | 133.278 | 30.728 | 28.689 | 29.006 | 601.919 | 26.592 | 27.565 | 1277.071 | 27.337 | 27.589 | 38.32 | 25.001 | 3.7 | 3.6 | 1.3 | 0 | 0.3
3643 | 30/07/2025 11:28:44.534 | 97.968 | 84 | 100 | 70 | 52 | 32.38 | 9.111 | 7.276 | 133.259 | 30.726 | 28.695 | 28.992 | 602.086 | 26.583 | 27.551 | 1276.996 | 27.343 | 27.621 | 38.254 | 20.001 | 5.5 | 3.2 | 0.7 | 0.9 | 0.2
3644 | 30/07/2025 11:28:46.169 | 97.656 | 81 | 100 | 69 | 53 | 30.402 | 9.161 | 7.276 | 133.201 | 30.726 | 28.681 | 28.958 | 601.99 | 26.586 | 27.544 | 1267.108 | 27.321 | 27.603 | 38.523 | 26.001 | 3.4 | 4.6 | 0.7 | 0.9 | 0.3
3645 | 30/07/2025 11:28:47.806 | 98.304 | 84 | 100 | 71 | 54 | 28.517 | 9.178 | 7.273 | 133.125 | 30.735 | 28.67 | 29.004 | 602.006 | 26.573 | 27.522 | 1277.358 | 27.356 | 27.6 | 38.476 | 27.001 | 2.2 | 1.6 | 0.9 | 1.3 | 0.3
3646 | 30/07/2025 11:28:49.438 | 98.688 | 84 | 100 | 70 | 51 | 32.001 | 9.134 | 7.276 | 132.95 | 30.73 | 28.702 | 29.003 | 601.903 | 26.572 | 27.537 | 1282.302 | 27.35 | 27.593 | 38.226 | 23.001 | 3 | 2.6 | 1.2 | 1.3 | 0.3
3647 | 30/07/2025 11:28:51.074 | 98.376 | 84 | 100 | 70 | 52 | 32.318 | 8.986 | 7.276 | 133.362 | 30.741 | 28.689 | 28.995 | 601.897 | 26.606 | 27.537 | 1287.229 | 27.335 | 27.6 | 38.32 | 23.001 | 3 | 2.6 | 1.2 | 1.3 | 0.3
3648 | 30/07/2025 11:28:52.711 | 98.808 | 86 | 100 | 71 | 53 | 28.668 | 8.914 | 7.275 | 133.32 | 30.729 | 28.687 | 28.961 | 602.155 | 26.6 | 27.516 | 1298.324 | 27.326 | 27.62 | 38.52 | 27.001 | 1.3 | 3.5 | 1.2 | 0.9 | 0.2
3649 | 30/07/2025 11:28:54.346 | 99.264 | 84 | 100 | 70 | 52 | 32.466 | 8.947 | 7.275 | 133.281 | 30.75 | 28.671 | 28.98 | 602 | 26.603 | 27.542 | 1297.367 | 27.33 | 27.599 | 38.571 | 28.001 | 3 | 1.7 | 1.3 | 0.9 | 0.2
3650 | 30/07/2025 11:28:55.982 | 99.624 | 84 | 100 | 70 | 52 | 29.781 | 9.108 | 7.275 | 133.092 | 30.875 | 28.675 | 28.997 | 602.019 | 26.592 | 27.54 | 1306.957 | 27.375 | 27.615 | 38.445 | 23.001 | 3.5 | 3.3 | 0.7 | 0.5 | 0.2
3651 | 30/07/2025 11:28:57.631 | 100.632 | 85 | 100 | 70 | 52 | 28.882 | 9.014 | 7.278 | 132.848 | 30.736 | 28.698 | 28.997 | 601.677 | 26.589 | 27.563 | 1307.288 | 27.35 | 27.58 | 38.238 | 25.001 | 1.5 | 4 | 1.2 | 0.5 | 0.2
3652 | 30/07/2025 11:28:59.266 | 100.8 | 85 | 100 | 70 | 51 | 32.157 | 9.428 | 7.276 | 133.205 | 30.797 | 28.685 | 29.002 | 602.173 | 26.599 | 27.561 | 1308.33 | 27.34 | 27.603 | 38.202 | 25.001 | 1.5 | 4 | 1.2 | 0.5 | 0.2
3653 | 30/07/2025 11:29:00.898 | 100.92 | 86 | 100 | 70 | 51 | 31.908 | 9.293 | 7.276 | 133.146 | 30.712 | 28.683 | 28.964 | 602.088 | 26.602 | 27.567 | 1306.888 | 27.333 | 27.611 | 38.385 | 23.001 | 3.7 | 4.1 | 1.1 | 0.6 | 0.2
3654 | 30/07/2025 11:29:02.532 | 101.376 | 88 | 100 | 71 | 51 | 31.539 | 9.215 | 7.273 | 133.346 | 30.725 | 28.67 | 28.985 | 601.944 | 26.597 | 27.544 | 1306.944 | 27.348 | 27.6 | 38.43 | 25.001 | 2.6 | 2.6 | 1.1 | 0.6 | 0.2
3655 | 30/07/2025 11:29:04.164 | 101.424 | 87 | 100 | 70 | 52 | 32.411 | 9.131 | 7.277 | 132.856 | 30.861 | 28.699 | 29 | 601.965 | 26.595 | 27.586 | 1300.539 | 27.359 | 27.602 | 38.382 | 24.001 | 1.8 | 3.1 | 0 | 0.3 | 0.2
3656 | 30/07/2025 11:29:05.798 | 101.664 | 87 | 100 | 70 | 52 | 29.051 | 8.953 | 7.294 | 133.134 | 30.876 | 28.689 | 28.996 | 601.851 | 26.591 | 27.555 | 1314.68 | 27.338 | 27.571 | 38.34 | 27.001 | 4.6 | 2.6 | 1.2 | 0.3 | 0.2
3657 | 30/07/2025 11:29:07.434 | 101.472 | 87 | 100 | 70 | 54 | 29.433 | 8.986 | 7.292 | 133.106 | 30.873 | 28.691 | 28.993 | 602.081 | 26.595 | 27.556 | 1311.957 | 27.338 | 27.615 | 38.63 | 28.001 | 2 | 1.9 | 0.7 | 0.5 | 0.2
3658 | 30/07/2025 11:29:09.070 | 101.568 | 87 | 100 | 70 | 52 | 32.269 | 9.129 | 7.278 | 133.281 | 30.896 | 28.676 | 28.988 | 601.964 | 26.598 | 27.559 | 1307.694 | 27.332 | 27.607 | 38.451 | 28.001 | 2 | 1.9 | 0.7 | 0.5 | 0.2
3659 | 30/07/2025 11:29:10.704 | 101.568 | 88 | 100 | 70 | 52 | 28.517 | 9.134 | 7.275 | 133.082 | 30.884 | 28.668 | 28.999 | 602.065 | 26.59 | 27.549 | 1306.779 | 27.363 | 27.597 | 38.383 | 25.001 | 2.2 | 3.1 | 1.2 | 0.5 | 0.2
3660 | 30/07/2025 11:29:12.338 | 101.424 | 89 | 100 | 70 | 51 | 32.026 | 9.135 | 7.278 | 132.87 | 30.886 | 28.697 | 28.999 | 601.814 | 26.576 | 27.554 | 1294.9 | 27.342 | 27.592 | 38.601 | 26.001 | 2.7 | 2.9 | 0.8 | 0.5 | 0.2
3661 | 30/07/2025 11:29:13.973 | 100.704 | 85 | 100 | 72 | 52 | 32.332 | 9.13 | 7.276 | 133.29 | 30.887 | 28.69 | 29.017 | 602.014 | 26.585 | 27.543 | 1291.965 | 27.344 | 27.598 | 38.317 | 25.001 | 3.4 | 2.1 | 1.7 | 0.5 | 0.2
3662 | 30/07/2025 11:29:15.605 | 100.248 | 85 | 100 | 70 | 52 | 28.667 | 9.287 | 7.276 | 133.136 | 30.888 | 28.686 | 28.982 | 603.138 | 26.582 | 27.543 | 1287.237 | 27.319 | 27.612 | 38.63 | 23.001 | 3 | 2.2 | 0.8 | 0.7 | 0.2
3663 | 30/07/2025 11:29:17.236 | 100.224 | 85 | 100 | 70 | 52 | 30.156 | 9.211 | 7.274 | 134.279 | 30.902 | 28.67 | 29.004 | 603.169 | 26.601 | 27.542 | 1282.613 | 27.334 | 27.609 | 38.422 | 23.001 | 3 | 2.2 | 0.8 | 0.7 | 0.2
3664 | 30/07/2025 11:29:18.868 | 99.984 | 87 | 100 | 70 | 52 | 32.366 | 9.213 | 7.277 | 134.634 | 30.885 | 28.692 | 29.005 | 602.116 | 26.591 | 27.537 | 1289.844 | 27.369 | 27.598 | 38.587 | 25.001 | 2.8 | 1.1 | 0.6 | 0.7 | 0.2
3665 | 30/07/2025 11:29:20.500 | 99.36 | 83 | 100 | 70 | 53 | 28.992 | 9.136 | 7.262 | 134.474 | 30.881 | 28.688 | 29 | 601.942 | 26.564 | 27.523 | 1289.578 | 27.343 | 27.562 | 38.161 | 27.001 | 2 | 1.8 | 0.3 | 0.1 | 0.2
3666 | 30/07/2025 11:29:22.134 | 99.264 | 86 | 100 | 71 | 52 | 32.2 | 9.042 | 7.24 | 134.76 | 30.878 | 28.692 | 28.999 | 601.901 | 26.579 | 27.542 | 1289.2 | 27.36 | 27.609 | 38.201 | 25.001 | 2.5 | 2.4 | 0.7 | 0.1 | 0.2
3667 | 30/07/2025 11:29:23.771 | 99.36 | 85 | 100 | 70 | 52 | 32.05 | 9.128 | 7.277 | 134.679 | 30.879 | 28.68 | 28.972 | 601.867 | 26.599 | 27.54 | 1296.689 | 27.322 | 27.605 | 38.467 | 26.001 | 2.7 | 2.5 | 0.6 | 0.6 | 0.2
3668 | 30/07/2025 11:29:25.406 | 99.192 | 86 | 100 | 70 | 52 | 28.426 | 9.005 | 7.274 | 134.753 | 30.888 | 28.679 | 29.009 | 603.153 | 26.58 | 27.506 | 1287.49 | 27.346 | 27.596 | 38.455 | 22.001 | 4.6 | 2.4 | 0 | 0.6 | 0.2
3669 | 30/07/2025 11:29:27.042 | 99.312 | 84 | 100 | 70 | 53 | 30.606 | 8.906 | 7.277 | 134.487 | 30.881 | 28.702 | 28.998 | 603.052 | 26.586 | 27.543 | 1287.347 | 27.353 | 27.58 | 38.399 | 22.001 | 4.6 | 2.4 | 0 | 0.6 | 0.2
3670 | 30/07/2025 11:29:28.678 | 98.664 | 83 | 100 | 71 | 52 | 32.412 | 9.127 | 7.276 | 134.908 | 30.881 | 28.686 | 28.992 | 601.906 | 26.628 | 27.549 | 1291.729 | 27.341 | 27.596 | 38.238 | 24.001 | 3.4 | 3.1 | 0.9 | 0.5 | 0.2
3671 | 30/07/2025 11:29:30.313 | 98.688 | 84 | 100 | 71 | 52 | 29.411 | 8.994 | 7.276 | 134.677 | 30.878 | 28.689 | 28.977 | 601.83 | 26.596 | 27.565 | 1296.713 | 27.328 | 27.611 | 38.451 | 24.001 | 2.4 | 5.6 | 0.6 | 0.5 | 0.2
3672 | 30/07/2025 11:29:31.947 | 98.616 | 84 | 100 | 71 | 52 | 32.28 | 9.126 | 7.274 | 134.683 | 30.863 | 28.675 | 28.978 | 602.063 | 26.588 | 27.548 | 1297.236 | 27.321 | 27.584 | 38.335 | 25.001 | 1.6 | 2.8 | 1.5 | 0 | 0.2
3673 | 30/07/2025 11:29:33.584 | 98.424 | 83 | 100 | 71 | 52 | 31.511 | 9.137 | 7.275 | 134.468 | 30.855 | 28.679 | 28.99 | 602.054 | 26.592 | 27.572 | 1283.231 | 27.372 | 27.599 | 38.425 | 26.001 | 1.8 | 3.4 | 1.5 | 0 | 0.2
3674 | 30/07/2025 11:29:35.221 | 98.064 | 84 | 100 | 70 | 52 | 28.174 | 8.99 | 7.278 | 134.217 | 30.86 | 28.697 | 28.992 | 601.839 | 26.603 | 27.57 | 1284.693 | 27.352 | 27.569 | 38.323 | 26.001 | 1.8 | 3.4 | 1.5 | 0 | 0.2
3675 | 30/07/2025 11:29:36.856 | 98.184 | 83 | 100 | 70 | 52 | 31.05 | 8.845 | 7.239 | 134.801 | 30.862 | 28.689 | 28.999 | 601.775 | 26.584 | 27.543 | 1289.171 | 27.337 | 27.606 | 38.432 | 29.001 | 1.8 | 3.1 | 1.7 | 0 | 0.2
3676 | 30/07/2025 11:29:38.494 | 97.392 | 83 | 100 | 70 | 51 | 28.616 | 8.961 | 7.24 | 134.519 | 30.876 | 28.685 | 28.975 | 601.869 | 26.61 | 27.573 | 1286.758 | 27.317 | 27.588 | 38.288 | 30.001 | 1.7 | 3.5 | 1.3 | 0 | 0.2
3677 | 30/07/2025 11:29:40.133 | 97.224 | 82 | 100 | 72 | 53 | 29.982 | 9.429 | 7.218 | 134.749 | 30.875 | 28.678 | 28.978 | 602.132 | 26.596 | 27.547 | 1294.8 | 27.336 | 27.6 | 38.473 | 28.001 | 4.4 | 2.9 | 0.6 | 0.5 | 0.2
3678 | 30/07/2025 11:29:41.770 | 96.528 | 81 | 100 | 70 | 52 | 32.327 | 9.215 | 7.221 | 134.305 | 30.881 | 28.688 | 28.99 | 601.938 | 26.587 | 27.569 | 1284.869 | 27.357 | 27.605 | 38.531 | 26.001 | 1.6 | 2.6 | 1.5 | 0.5 | 0.2
3679 | 30/07/2025 11:29:43.405 | 97.44 | 82 | 100 | 70 | 51 | 30.906 | 8.988 | 7.22 | 134.577 | 30.877 | 28.69 | 28.992 | 601.987 | 26.594 | 27.544 | 1284.781 | 27.338 | 27.571 | 38.272 | 26.001 | 2.7 | 3 | 1.2 | 0 | 0.2
3680 | 30/07/2025 11:29:45.040 | 97.2 | 82 | 100 | 71 | 52 | 28.288 | 9.282 | 7.238 | 134.644 | 30.9 | 28.691 | 29.003 | 601.97 | 26.581 | 27.554 | 1282.316 | 27.34 | 27.615 | 38.475 | 26.001 | 2.7 | 3 | 1.2 | 0 | 0.2
3681 | 30/07/2025 11:29:46.674 | 97.608 | 84 | 100 | 69 | 52 | 31.993 | 9.213 | 7.24 | 134.805 | 30.901 | 28.687 | 28.989 | 602.091 | 26.596 | 27.529 | 1280.738 | 27.32 | 27.604 | 38.665 | 30.001 | 3.1 | 2.1 | 0.7 | 0 | 0.2
3682 | 30/07/2025 11:29:48.308 | 98.184 | 82 | 100 | 70 | 52 | 28.336 | 9.171 | 7.187 | 134.54 | 30.893 | 28.678 | 29.006 | 603.231 | 26.6 | 27.555 | 1282.983 | 27.355 | 27.597 | 38.525 | 25.001 | 1.7 | 2.9 | 1.3 | 0.5 | 0.1
3683 | 30/07/2025 11:29:49.940 | 97.968 | 83 | 100 | 71 | 52 | 30.691 | 8.98 | 7.188 | 134.45 | 30.893 | 28.689 | 28.993 | 602.138 | 26.595 | 27.553 | 1272.623 | 27.341 | 27.597 | 38.433 | 30.001 | 2.5 | 2.3 | 0.6 | 0.5 | 0.1
3684 | 30/07/2025 11:29:51.574 | 97.896 | 82 | 100 | 70 | 52 | 32.359 | 9.224 | 7.239 | 134.791 | 30.891 | 28.688 | 28.995 | 601.938 | 26.589 | 27.543 | 1262.538 | 27.33 | 27.596 | 38.113 | 28.001 | 2.6 | 1.7 | 1.3 | 0 | 0.1
3685 | 30/07/2025 11:29:53.209 | 97.896 | 83 | 100 | 70 | 52 | 30.393 | 9.011 | 7.188 | 134.642 | 30.879 | 28.691 | 28.981 | 601.93 | 26.569 | 27.558 | 1261.16 | 27.312 | 27.616 | 38.708 | 28.001 | 2.6 | 1.7 | 1.3 | 0 | 0.1
3686 | 30/07/2025 11:29:54.843 | 97.896 | 84 | 100 | 70 | 52 | 28.592 | 8.987 | 7.185 | 134.658 | 30.906 | 28.672 | 29.002 | 602.152 | 26.576 | 27.535 | 1269.803 | 27.331 | 27.598 | 38.369 | 25.001 | 2.4 | 2.6 | 1.3 | 0 | 0.2
3687 | 30/07/2025 11:29:56.480 | 98.112 | 83 | 100 | 71 | 53 | 31.666 | 9.199 | 7.203 | 134.615 | 30.887 | 28.67 | 29.002 | 603.183 | 26.588 | 27.533 | 1271.19 | 27.357 | 27.604 | 38.477 | 28.001 | 2.1 | 3.9 | 0.9 | 0.5 | 0.2
3688 | 30/07/2025 11:29:58.116 | 98.232 | 82 | 100 | 71 | 52 | 28.259 | 9.131 | 7.204 | 134.444 | 30.883 | 28.693 | 29.009 | 602.4 | 26.587 | 27.525 | 1265.3 | 27.348 | 27.576 | 38.343 | 26.001 | 2.9 | 2.7 | 0.1 | 0.5 | 0.2
3689 | 30/07/2025 11:29:59.753 | 98.544 | 82 | 100 | 70 | 51 | 31.31 | 9.282 | 7.221 | 134.505 | 30.888 | 28.701 | 28.996 | 601.839 | 26.59 | 27.535 | 1266.394 | 27.357 | 27.61 | 38.211 | 29.001 | 2.8 | 3.6 | 0.6 | 0 | 0.2
3690 | 30/07/2025 11:30:01.387 | 98.76 | 84 | 100 | 71 | 53 | 32.446 | 9.223 | 7.222 | 134.779 | 30.876 | 28.686 | 28.974 | 603.167 | 26.609 | 27.531 | 1267.043 | 27.314 | 27.592 | 38.5 | 24.001 | 2.6 | 2.6 | 1.2 | 0 | 0.2
3691 | 30/07/2025 11:30:03.023 | 98.376 | 82 | 100 | 70 | 52 | 29.872 | 9.211 | 7.219 | 134.672 | 30.877 | 28.675 | 29 | 603.239 | 26.592 | 27.543 | 1269.669 | 27.357 | 27.598 | 38.541 | 24.001 | 2.6 | 2.6 | 1.2 | 0 | 0.2
3692 | 30/07/2025 11:30:04.657 | 98.712 | 85 | 100 | 69 | 52 | 32.348 | 9.136 | 7.22 | 134.704 | 30.88 | 28.68 | 29.001 | 601.998 | 26.607 | 27.555 | 1270.015 | 27.353 | 27.588 | 38.457 | 24.001 | 3.1 | 3.8 | 0.9 | 0.6 | 0.1
3693 | 30/07/2025 11:30:06.292 | 98.496 | 84 | 100 | 70 | 52 | 31.064 | 9.038 | 7.221 | 134.612 | 30.873 | 28.69 | 29.007 | 603.139 | 26.605 | 27.558 | 1273.109 | 27.353 | 27.596 | 38.286 | 27.001 | 1.9 | 2.3 | 0.7 | 0.6 | 0.1
3694 | 30/07/2025 11:30:07.925 | 98.976 | 86 | 100 | 70 | 52 | 28.319 | 8.981 | 7.241 | 133.095 | 30.852 | 28.687 | 28.987 | 602.861 | 26.595 | 27.569 | 1278.052 | 27.322 | 27.606 | 38.544 | 31.001 | 3.4 | 5.5 | 0.6 | 0.9 | 0.1
3695 | 30/07/2025 11:30:09.559 | 99.096 | 84 | 100 | 71 | 52 | 31.635 | 9.206 | 7.219 | 133.172 | 30.862 | 28.674 | 28.992 | 603.408 | 26.598 | 27.552 | 1277.779 | 27.319 | 27.593 | 38.711 | 28.001 | 4.9 | 3.2 | 1.8 | 0.9 | 0.2
3696 | 30/07/2025 11:30:11.195 | 98.976 | 85 | 100 | 71 | 52 | 32.49 | 9.131 | 7.22 | 133.165 | 30.86 | 28.686 | 29.004 | 603.242 | 26.597 | 27.567 | 1272.632 | 27.372 | 27.613 | 38.556 | 28.001 | 4.9 | 3.2 | 1.8 | 0.9 | 0.2
3697 | 30/07/2025 11:30:12.830 | 98.928 | 84 | 100 | 70 | 53 | 29.271 | 8.99 | 7.221 | 132.896 | 30.872 | 28.693 | 28.989 | 603.103 | 26.606 | 27.552 | 1268.304 | 27.339 | 27.568 | 38.328 | 26.001 | 2.2 | 3.9 | 2 | 0.9 | 0.2
3698 | 30/07/2025 11:30:14.464 | 99.216 | 83 | 100 | 70 | 52 | 32.404 | 9.136 | 7.22 | 132.997 | 30.87 | 28.702 | 28.991 | 603.209 | 26.589 | 27.564 | 1269.331 | 27.345 | 27.593 | 38.215 | 25.001 | 3.2 | 4.4 | 0.9 | 0.9 | 0.2
3699 | 30/07/2025 11:30:16.103 | 99.528 | 85 | 100 | 71 | 53 | 30.491 | 9.28 | 7.203 | 133.127 | 30.887 | 28.691 | 28.983 | 603.122 | 26.609 | 27.553 | 1272.072 | 27.311 | 27.594 | 38.451 | 26.001 | 2.6 | 2.6 | 1.2 | 0.8 | 0.2
3700 | 30/07/2025 11:30:17.739 | 99.6 | 83 | 100 | 70 | 51 | 28.572 | 9.14 | 7.186 | 133.197 | 30.896 | 28.669 | 28.987 | 603.369 | 26.585 | 27.549 | 1270.182 | 27.346 | 27.613 | 38.578 | 30.001 | 2.9 | 2.3 | 1.6 | 0.8 | 0.2
3701 | 30/07/2025 11:30:19.373 | 100.128 | 88 | 100 | 70 | 52 | 31.994 | 9.152 | 7.188 | 133.077 | 30.885 | 28.682 | 29.003 | 603.119 | 26.6 | 27.56 | 1269.716 | 27.351 | 27.604 | 38.472 | 27.001 | 3.5 | 3.3 | 1.3 | 0 | 0.3
3702 | 30/07/2025 11:30:21.007 | 99.36 | 85 | 100 | 70 | 52 | 32.288 | 9.134 | 7.203 | 133.067 | 30.895 | 28.693 | 29.012 | 603.344 | 26.591 | 27.554 | 1272.493 | 27.343 | 27.574 | 38.305 | 27.001 | 3.5 | 3.3 | 1.3 | 0 | 0.3
3703 | 30/07/2025 11:30:22.644 | 99.432 | 85 | 100 | 70 | 53 | 31.181 | 9.177 | 7.205 | 133.212 | 30.889 | 28.693 | 28.991 | 603.012 | 26.596 | 27.557 | 1271.868 | 27.354 | 27.593 | 38.328 | 25.001 | 3 | 1.4 | 0.3 | 0 | 0.3
3704 | 30/07/2025 11:30:24.280 | 99.408 | 86 | 100 | 71 | 52 | 32.451 | 9.428 | 7.203 | 133.179 | 30.887 | 28.683 | 28.978 | 603.301 | 26.594 | 27.539 | 1253.02 | 27.319 | 27.608 | 38.431 | 30.001 | 2.5 | 3.8 | 1.3 | 0 | 0.2
3705 | 30/07/2025 11:30:25.915 | 100.176 | 86 | 100 | 70 | 52 | 29.672 | 9.134 | 7.204 | 133.343 | 30.885 | 28.67 | 28.988 | 603.257 | 26.583 | 27.55 | 1246.737 | 27.351 | 27.61 | 38.297 | 28.001 | 2.5 | 3.7 | 0.6 | 0 | 0.2
3706 | 30/07/2025 11:30:27.550 | 99.528 | 84 | 100 | 70 | 52 | 28.931 | 8.913 | 7.204 | 133.115 | 30.892 | 28.686 | 29.013 | 603.241 | 26.595 | 27.549 | 1243.388 | 27.34 | 27.592 | 38.322 | 25.001 | 2.9 | 4.4 | 0.6 | 0.7 | 0.2
3707 | 30/07/2025 11:30:29.184 | 99.36 | 83 | 100 | 70 | 52 | 32.201 | 9.206 | 7.205 | 134.6 | 30.877 | 28.691 | 29.009 | 603.179 | 26.567 | 27.523 | 1247.243 | 27.338 | 27.597 | 38.157 | 25.001 | 2.9 | 4.4 | 0.6 | 0.7 | 0.2
3708 | 30/07/2025 11:30:30.821 | 99.096 | 85 | 100 | 70 | 52 | 32.096 | 9.216 | 7.22 | 134.842 | 30.888 | 28.693 | 28.97 | 602.952 | 26.569 | 27.538 | 1261.906 | 27.313 | 27.611 | 38.667 | 24.001 | 2.7 | 3.3 | 0.7 | 0.7 | 0.2
3709 | 30/07/2025 11:30:32.455 | 99.072 | 84 | 100 | 70 | 53 | 31.738 | 9.122 | 7.239 | 134.498 | 30.871 | 28.679 | 28.971 | 603.317 | 26.589 | 27.527 | 1261.698 | 27.334 | 27.616 | 38.464 | 26.001 | 2.3 | 3.1 | 1.2 | 0.5 | 0.2
3710 | 30/07/2025 11:30:34.089 | 99.144 | 84 | 100 | 72 | 52 | 32.444 | 9.06 | 7.257 | 134.652 | 30.873 | 28.669 | 29.006 | 603.158 | 26.596 | 27.538 | 1257.485 | 27.359 | 27.6 | 38.54 | 26.001 | 2.4 | 3.4 | 1 | 0.5 | 0.1
3711 | 30/07/2025 11:30:35.726 | 99.36 | 85 | 100 | 70 | 52 | 29.284 | 9.218 | 7.276 | 134.438 | 30.883 | 28.692 | 29.014 | 603.33 | 26.593 | 27.534 | 1262.351 | 27.352 | 27.579 | 38.415 | 25.001 | 2.7 | 3.3 | 0.6 | 0.5 | 0.1
3712 | 30/07/2025 11:30:37.361 | 98.856 | 84 | 100 | 70 | 52 | 29.472 | 9.134 | 7.276 | 134.51 | 30.869 | 28.681 | 28.996 | 603.142 | 26.599 | 27.561 | 1271.694 | 27.354 | 27.601 | 38.291 | 26.001 | 3 | 4.1 | 0.6 | 0.5 | 0.2
3713 | 30/07/2025 11:30:38.996 | 99.048 | 84 | 100 | 70 | 52 | 32.307 | 9.131 | 7.277 | 134.906 | 30.873 | 28.683 | 28.974 | 603.283 | 26.616 | 27.546 | 1278.073 | 27.302 | 27.596 | 38.431 | 26.001 | 3 | 4.1 | 0.6 | 0.5 | 0.2
3714 | 30/07/2025 11:30:40.631 | 98.88 | 85 | 100 | 70 | 52 | 28.533 | 9.211 | 7.276 | 134.507 | 30.861 | 28.678 | 28.981 | 603.196 | 26.602 | 27.583 | 1269.215 | 27.327 | 27.607 | 38.301 | 26.001 | 2.1 | 3 | 1.3 | 0.5 | 0.2
3715 | 30/07/2025 11:30:42.266 | 98.304 | 86 | 100 | 71 | 52 | 32.017 | 9.128 | 7.275 | 134.737 | 30.862 | 28.676 | 29.006 | 603.326 | 26.605 | 27.561 | 1267.474 | 27.348 | 27.591 | 38.37 | 24.001 | 1.5 | 2.1 | 1.5 | 0.5 | 0.2
3716 | 30/07/2025 11:30:43.901 | 98.376 | 84 | 100 | 70 | 52 | 32.369 | 9.135 | 7.277 | 134.571 | 30.844 | 28.697 | 29 | 603.236 | 26.582 | 27.557 | 1265.146 | 27.359 | 27.591 | 38.32 | 28.001 | 3.3 | 2.5 | 0.7 | 0.5 | 0.2
3717 | 30/07/2025 11:30:45.537 | 98.04 | 83 | 100 | 71 | 53 | 28.75 | 9.13 | 7.277 | 134.538 | 30.863 | 28.689 | 28.989 | 603.039 | 26.599 | 27.562 | 1266.348 | 27.344 | 27.595 | 38.479 | 24.001 | 4.4 | 2.1 | 0.6 | 0.5 | 0.2
3718 | 30/07/2025 11:30:47.172 | 97.896 | 84 | 100 | 70 | 52 | 29.982 | 9.133 | 7.273 | 134.703 | 30.876 | 28.682 | 28.99 | 603.208 | 26.588 | 27.548 | 1273.286 | 27.314 | 27.608 | 38.322 | 24.001 | 4.4 | 2.1 | 0.6 | 0.5 | 0.2
3719 | 30/07/2025 11:30:48.807 | 97.704 | 83 | 100 | 70 | 52 | 29.859 | 9.131 | 7.276 | 134.781 | 30.88 | 28.659 | 28.976 | 604.458 | 26.596 | 27.561 | 1277.108 | 27.342 | 27.605 | 38.442 | 28.001 | 3.3 | 2.4 | 0.3 | 0.5 | 0.2
3720 | 30/07/2025 11:30:50.442 | 97.92 | 83 | 100 | 70 | 52 | 28.934 | 9.133 | 7.276 | 134.577 | 30.88 | 28.691 | 29.013 | 603.226 | 26.593 | 27.543 | 1276.178 | 27.352 | 27.602 | 38.41 | 24.001 | 3.6 | 2.9 | 1.8 | 0.5 | 0.1
3721 | 30/07/2025 11:30:52.076 | 97.8 | 83 | 100 | 70 | 52 | 32.18 | 8.98 | 7.278 | 134.541 | 30.886 | 28.703 | 28.986 | 603.131 | 26.586 | 27.563 | 1263.968 | 27.338 | 27.583 | 38.435 | 24.001 | 2 | 4.1 | 0.9 | 0.5 | 0.2
3722 | 30/07/2025 11:30:53.711 | 97.488 | 83 | 99 | 70 | 52 | 32.031 | 9.274 | 7.277 | 134.78 | 30.895 | 28.689 | 28.989 | 603.032 | 26.589 | 27.55 | 1257.257 | 27.316 | 27.606 | 38.532 | 22.001 | 3 | 3.8 | 0.6 | 0.5 | 0.2
3723 | 30/07/2025 11:30:55.345 | 97.632 | 83 | 100 | 70 | 52 | 28.356 | 8.987 | 7.276 | 134.531 | 30.879 | 28.673 | 28.978 | 603.347 | 26.598 | 27.55 | 1269.867 | 27.35 | 27.603 | 38.617 | 24.001 | 2.5 | 2.6 | 0.9 | 0.5 | 0.1
3724 | 30/07/2025 11:30:56.978 | 97.104 | 84 | 100 | 70 | 54 | 30.632 | 9.132 | 7.277 | 134.411 | 30.896 | 28.68 | 29.012 | 603.319 | 26.584 | 27.553 | 1277.464 | 27.356 | 27.61 | 38.597 | 24.001 | 2.5 | 2.6 | 0.9 | 0.5 | 0.1
3725 | 30/07/2025 11:30:58.615 | 97.56 | 84 | 100 | 72 | 52 | 29.145 | 9.06 | 7.277 | 134.556 | 30.892 | 28.695 | 29.011 | 603.261 | 26.577 | 27.547 | 1277.299 | 27.373 | 27.592 | 38.625 | 23.001 | 4.7 | 2.5 | 0.8 | 0.5 | 0.2
3726 | 30/07/2025 11:31:00.251 | 97.272 | 83 | 100 | 70 | 53 | 29.463 | 9.281 | 7.277 | 134.442 | 30.888 | 28.686 | 29.01 | 603.021 | 26.599 | 27.55 | 1278.884 | 27.342 | 27.594 | 38.356 | 26.001 | 1.9 | 1.1 | 0.6 | 0.6 | 0.2
3727 | 30/07/2025 11:31:01.886 | 97.632 | 84 | 100 | 71 | 52 | 32.316 | 9.129 | 7.275 | 134.694 | 30.889 | 28.692 | 28.987 | 603.19 | 26.585 | 27.529 | 1282.588 | 27.315 | 27.628 | 38.423 | 25.001 | 3.4 | 2.9 | 1.2 | 0.6 | 0.3
3728 | 30/07/2025 11:31:03.530 | 97.944 | 83 | 100 | 69 | 52 | 31.658 | 9.134 | 7.274 | 134.471 | 30.87 | 28.664 | 28.984 | 603.263 | 26.576 | 27.547 | 1282.381 | 27.333 | 27.603 | 38.337 | 27.001 | 2 | 3.3 | 0.3 | 1 | 0.3
3729 | 30/07/2025 11:31:05.165 | 97.776 | 83 | 100 | 71 | 52 | 28.223 | 9.164 | 7.275 | 134.469 | 30.892 | 28.688 | 29.004 | 603.276 | 26.578 | 27.532 | 1287.288 | 27.35 | 27.592 | 38.337 | 27.001 | 2 | 3.3 | 0.3 | 1 | 0.3
3730 | 30/07/2025 11:31:06.799 | 97.368 | 81 | 100 | 69 | 52 | 31.229 | 8.996 | 7.325 | 134.608 | 30.876 | 28.694 | 29.002 | 603.216 | 26.592 | 27.531 | 1277.358 | 27.356 | 27.604 | 38.154 | 25.001 | 2.5 | 4.6 | 0.6 | 1 | 0.2
3731 | 30/07/2025 11:31:08.435 | 97.44 | 84 | 100 | 71 | 51 | 28.763 | 9.186 | 7.328 | 134.755 | 30.889 | 28.693 | 29.01 | 603.153 | 26.595 | 27.528 | 1276.906 | 27.34 | 27.603 | 38.195 | 29.001 | 3 | 6.2 | 1 | 0.6 | 0.2
3732 | 30/07/2025 11:31:10.070 | 98.016 | 83 | 100 | 70 | 51 | 30.06 | 9.213 | 7.328 | 134.438 | 30.87 | 28.687 | 28.979 | 603.203 | 26.602 | 27.547 | 1278.852 | 27.334 | 27.594 | 38.514 | 28.001 | 2.3 | 3.4 | 0.6 | 0.6 | 0.2
3733 | 30/07/2025 11:31:11.704 | 98.232 | 84 | 100 | 70 | 52 | 32.332 | 9.132 | 7.312 | 134.536 | 30.874 | 28.67 | 28.994 | 601.893 | 26.595 | 27.549 | 1263.683 | 27.357 | 27.586 | 38.499 | 25.001 | 1.9 | 4.1 | 1.5 | 0.5 | 0.1
3734 | 30/07/2025 11:31:13.338 | 97.704 | 83 | 100 | 71 | 52 | 31.133 | 9.13 | 7.276 | 134.408 | 30.867 | 28.696 | 29.008 | 602.096 | 26.606 | 27.557 | 1260.893 | 27.355 | 27.587 | 38.131 | 24.001 | 3.4 | 5.8 | 0.3 | 0.5 | 0.1
3735 | 30/07/2025 11:31:14.976 | 98.592 | 83 | 100 | 71 | 52 | 28.329 | 9.133 | 7.277 | 134.753 | 30.863 | 28.688 | 28.979 | 602.01 | 26.593 | 27.582 | 1272.486 | 27.352 | 27.593 | 38.261 | 24.001 | 3.4 | 5.8 | 0.3 | 0.5 | 0.1
3736 | 30/07/2025 11:31:16.613 | 98.64 | 84 | 100 | 71 | 52 | 32.101 | 9.129 | 7.276 | 134.608 | 30.876 | 28.7 | 28.996 | 602.047 | 26.595 | 27.571 | 1276.284 | 27.339 | 27.632 | 38.403 | 23.001 | 4.5 | 4.3 | 0.6 | 1.2 | 0.1
3737 | 30/07/2025 11:31:18.247 | 98.832 | 85 | 100 | 69 | 52 | 28.48 | 8.99 | 7.277 | 134.54 | 30.848 | 28.679 | 28.965 | 601.871 | 26.59 | 27.577 | 1271.865 | 27.32 | 27.609 | 38.438 | 25.001 | 2 | 2.5 | 0 | 1.2 | 0.2
3738 | 30/07/2025 11:31:19.881 | 98.952 | 84 | 100 | 71 | 52 | 30.664 | 8.982 | 7.275 | 133.052 | 30.886 | 28.679 | 29.158 | 602.065 | 26.598 | 27.56 | 1281.808 | 27.345 | 27.604 | 38.247 | 28.001 | 2 | 2.5 | 0.7 | 1.1 | 0.2
3739 | 30/07/2025 11:31:21.520 | 99.312 | 84 | 100 | 70 | 51 | 32.401 | 9.197 | 7.277 | 133.023 | 30.873 | 28.71 | 29.145 | 602.015 | 26.584 | 27.56 | 1279.395 | 27.367 | 27.593 | 38.337 | 26.001 | 1.9 | 4.2 | 0.6 | 1.1 | 0.2
3740 | 30/07/2025 11:31:23.156 | 99.048 | 85 | 100 | 70 | 52 | 30.575 | 9.205 | 7.242 | 133.238 | 30.889 | 28.687 | 28.985 | 601.89 | 26.594 | 27.55 | 1274.359 | 27.332 | 27.59 | 38.337 | 26.001 | 1.9 | 4.2 | 0.6 | 1.1 | 0.2
3741 | 30/07/2025 11:31:24.791 | 99.432 | 85 | 100 | 70 | 52 | 28.51 | 8.985 | 7.239 | 133.092 | 30.89 | 28.688 | 28.973 | 601.927 | 26.589 | 27.546 | 1271.07 | 27.325 | 27.615 | 38.427 | 26.001 | 0.7 | 2.3 | 0.7 | 0 | 0.2
3742 | 30/07/2025 11:31:26.426 | 100.032 | 86 | 100 | 70 | 52 | 31.635 | 8.902 | 7.27 | 133.244 | 30.896 | 28.668 | 28.972 | 601.893 | 26.612 | 27.562 | 1275.338 | 27.334 | 27.597 | 38.414 | 26.001 | 2 | 2.7 | 0 | 0 | 0.2
3743 | 30/07/2025 11:31:28.063 | 99.624 | 84 | 100 | 71 | 52 | 28.245 | 9.049 | 7.276 | 133.118 | 30.89 | 28.689 | 29.062 | 602.121 | 26.595 | 27.534 | 1272.853 | 27.361 | 27.616 | 38.35 | 28.001 | 1.7 | 3 | 0.9 | 0.5 | 0.2
3744 | 30/07/2025 11:31:29.698 | 99.072 | 84 | 100 | 70 | 51 | 31.172 | 8.989 | 7.277 | 133.078 | 30.886 | 28.689 | 28.988 | 601.906 | 26.588 | 27.561 | 1272.93 | 27.348 | 27.592 | 39.416 | 27.001 | 3.1 | 2.7 | 1.5 | 0.5 | 0.2
3745 | 30/07/2025 11:31:31.333 | 98.784 | 84 | 100 | 69 | 53 | 32.446 | 8.981 | 7.276 | 133.306 | 30.893 | 28.689 | 28.988 | 602.034 | 26.596 | 27.549 | 1271.911 | 27.333 | 27.611 | 38.27 | 27.001 | 2.8 | 4.8 | 1.3 | 0.6 | 0.2
3746 | 30/07/2025 11:31:32.967 | 98.832 | 85 | 100 | 71 | 53 | 29.76 | 9.135 | 7.276 | 133.049 | 30.867 | 28.685 | 28.977 | 601.932 | 26.584 | 27.545 | 1274.49 | 27.347 | 27.602 | 38.458 | 27.001 | 2.8 | 4.8 | 1.3 | 0.6 | 0.2
3747 | 30/07/2025 11:31:34.601 | 99 | 85 | 100 | 70 | 52 | 32.358 | 8.985 | 7.275 | 133.245 | 30.879 | 28.668 | 28.999 | 602.136 | 26.589 | 27.531 | 1277.512 | 27.351 | 27.594 | 38.428 | 29.001 | 3.1 | 3.4 | 1.2 | 0.6 | 0.2
3748 | 30/07/2025 11:31:36.237 | 98.664 | 83 | 99 | 70 | 52 | 30.997 | 9.138 | 7.276 | 132.992 | 30.881 | 28.707 | 29.004 | 601.998 | 26.589 | 27.538 | 1272.321 | 27.358 | 27.596 | 38.544 | 27.001 | 1.4 | 4.8 | 0.7 | 1 | 0.2
3749 | 30/07/2025 11:31:37.871 | 98.808 | 84 | 100 | 70 | 52 | 28.32 | 9.067 | 7.277 | 133.177 | 30.893 | 28.69 | 28.983 | 602.07 | 26.6 | 27.531 | 1261.733 | 27.344 | 27.579 | 38.355 | 29.001 | 3.2 | 2.7 | 1.2 | 1 | 0.2
3750 | 30/07/2025 11:31:39.505 | 99.384 | 84 | 100 | 71 | 53 | 31.626 | 9.168 | 7.276 | 133.165 | 30.882 | 28.69 | 28.987 | 602.073 | 26.58 | 27.522 | 1260.225 | 27.325 | 27.623 | 38.477 | 26.001 | 3.8 | 1.5 | 0.6 | 0.1 | 0.2
3751 | 30/07/2025 11:31:41.136 | 100.056 | 87 | 100 | 71 | 52 | 32.432 | 9.128 | 7.276 | 133.185 | 30.886 | 28.667 | 28.984 | 601.885 | 26.592 | 27.547 | 1252.514 | 27.327 | 27.601 | 38.262 | 26.001 | 3.8 | 1.5 | 0.6 | 0.1 | 0.2
3752 | 30/07/2025 11:31:42.773 | 99.288 | 84 | 100 | 70 | 53 | 30.615 | 8.862 | 7.289 | 133.199 | 30.872 | 28.667 | 28.993 | 603.376 | 26.603 | 27.531 | 1257.695 | 27.377 | 27.607 | 38.421 | 28.001 | 2.3 | 3.2 | 1.4 | 0.1 | 0.2
3753 | 30/07/2025 11:31:44.412 | 99.888 | 85 | 100 | 70 | 52 | 32.394 | 8.921 | 7.294 | 132.986 | 30.871 | 28.689 | 28.989 | 603.214 | 26.599 | 27.544 | 1264.803 | 27.339 | 27.582 | 38.373 | 27.001 | 3.6 | 3 | 0.9 | 0.6 | 0.2
3754 | 30/07/2025 11:31:46.046 | 99.648 | 84 | 100 | 71 | 53 | 30.43 | 9.209 | 7.276 | 133.104 | 30.877 | 28.683 | 29.007 | 603.286 | 26.599 | 27.549 | 1255.877 | 27.339 | 27.594 | 38.235 | 23.001 | 1.7 | 2.4 | 2 | 0.6 | 0.2
3755 | 30/07/2025 11:31:47.682 | 99.456 | 84 | 100 | 71 | 53 | 28.542 | 8.985 | 7.274 | 132.874 | 30.872 | 28.701 | 28.973 | 602.105 | 26.594 | 27.565 | 1250.458 | 27.328 | 27.609 | 38.377 | 25.001 | 1.3 | 4.7 | 1.6 | 0.3 | 0.1
3756 | 30/07/2025 11:31:49.317 | 98.544 | 85 | 100 | 70 | 52 | 31.915 | 8.981 | 7.277 | 133.279 | 30.862 | 28.677 | 28.998 | 601.9 | 26.604 | 27.555 | 1255.186 | 27.351 | 27.591 | 38.375 | 24.001 | 2.5 | 2.3 | 1.1 | 0.3 | 0.2
3757 | 30/07/2025 11:31:50.951 | 97.512 | 83 | 100 | 71 | 52 | 32.336 | 8.996 | 7.276 | 132.92 | 30.872 | 28.697 | 29.004 | 602.035 | 26.591 | 27.558 | 1252.926 | 27.348 | 27.599 | 38.288 | 24.001 | 2.5 | 2.3 | 1.1 | 0.3 | 0.2
3758 | 30/07/2025 11:31:52.584 | 97.44 | 83 | 100 | 70 | 53 | 31.165 | 8.995 | 7.278 | 133.082 | 30.875 | 28.694 | 29.007 | 601.963 | 26.61 | 27.573 | 1257.166 | 27.342 | 27.58 | 38.188 | 25.001 | 3.9 | 4.9 | 0.2 | 0.8 | 0.2
3759 | 30/07/2025 11:31:54.218 | 97.752 | 83 | 100 | 71 | 51 | 32.467 | 9.129 | 7.276 | 133.281 | 30.868 | 28.692 | 28.987 | 601.989 | 26.597 | 27.55 | 1267.028 | 27.346 | 27.623 | 38.491 | 28.001 | 3.8 | 3.2 | 1 | 0.8 | 0.2
3760 | 30/07/2025 11:31:55.853 | 97.488 | 84 | 100 | 69 | 52 | 30.045 | 8.986 | 7.277 | 133.255 | 30.875 | 28.679 | 28.96 | 601.82 | 26.595 | 27.57 | 1271.873 | 27.309 | 27.605 | 38.489 | 21.001 | 2.4 | 4.2 | 0.8 | 0 | 0.2
3761 | 30/07/2025 11:31:57.488 | 97.848 | 82 | 100 | 70 | 52 | 29.009 | 9.186 | 7.275 | 133.351 | 30.886 | 28.673 | 29.01 | 602.219 | 26.588 | 27.541 | 1274.242 | 27.348 | 27.603 | 38.449 | 28.001 | 2.2 | 4.7 | 0.3 | 0 | 0.2
3762 | 30/07/2025 11:31:59.124 | 97.2 | 83 | 100 | 70 | 51 | 32.211 | 9.209 | 7.24 | 132.811 | 30.881 | 28.697 | 29.007 | 602.023 | 26.595 | 27.561 | 1276.921 | 27.358 | 27.588 | 38.263 | 28.001 | 2.2 | 4.7 | 0.3 | 0 | 0.2
3763 | 30/07/2025 11:32:00.758 | 97.896 | 83 | 100 | 71 | 52 | 28.331 | 9.22 | 7.24 | 133.223 | 30.882 | 28.685 | 29.007 | 602.114 | 26.588 | 27.545 | 1277.103 | 27.351 | 27.583 | 38.135 | 25.001 | 2.7 | 3.5 | 0.6 | 0.4 | 0.2
3764 | 30/07/2025 11:32:02.390 | 97.872 | 83 | 100 | 70 | 51 | 31.712 | 9.074 | 7.188 | 133.086 | 30.898 | 28.684 | 29.121 | 601.991 | 26.597 | 27.561 | 1271.852 | 27.337 | 27.599 | 38.505 | 29.001 | 1.7 | 3.7 | 0 | 0.4 | 0.2
3765 | 30/07/2025 11:32:04.025 | 98.016 | 83 | 100 | 71 | 52 | 32.473 | 9.132 | 7.185 | 133.351 | 30.898 | 28.665 | 29.107 | 603.119 | 26.602 | 27.548 | 1285.374 | 27.334 | 27.598 | 38.217 | 25.001 | 3 | 3.7 | 0.7 | 0 | 0.2
3766 | 30/07/2025 11:32:05.661 | 98.664 | 84 | 100 | 70 | 52 | 29.262 | 9.145 | 7.186 | 133.197 | 30.887 | 28.69 | 29.155 | 603.237 | 26.591 | 27.546 | 1284.805 | 27.359 | 27.612 | 38.432 | 26.001 | 3.1 | 3.2 | 1 | 0 | 0.2
3767 | 30/07/2025 11:32:07.295 | 98.832 | 84 | 100 | 70 | 52 | 29.436 | 9.136 | 7.205 | 132.873 | 30.88 | 28.686 | 29.13 | 601.759 | 26.59 | 27.548 | 1296.903 | 27.348 | 27.585 | 39.978 | 29.001 | 3.3 | 3.7 | 0.2 | 0.2 | 0.4
3768 | 30/07/2025 11:32:08.951 | 98.616 | 84 | 100 | 70 | 52 | 32.298 | 9.212 | 7.204 | 133.32 | 30.887 | 28.687 | 29.141 | 603.242 | 26.574 | 27.534 | 1289.666 | 27.333 | 27.606 | 40.175 | 29.001 | 3.3 | 3.7 | 0.2 | 0.2 | 0.4
3769 | 30/07/2025 11:32:10.586 | 99.024 | 86 | 100 | 70 | 52 | 28.515 | 9.417 | 7.205 | 133.204 | 30.885 | 28.688 | 29.125 | 603.085 | 26.589 | 27.549 | 1284.668 | 27.305 | 27.6 | 40.264 | 29.001 | 1.6 | 2 | 0 | 0.2 | 0.4
3770 | 30/07/2025 11:32:12.221 | 99.288 | 84 | 100 | 70 | 51 | 31.989 | 9.134 | 7.202 | 133.173 | 30.886 | 28.668 | 29.14 | 603.241 | 26.588 | 27.533 | 1277.425 | 27.344 | 27.604 | 38.276 | 28.001 | 2.4 | 2.1 | 0.6 | 0 | 0.4
3771 | 30/07/2025 11:32:13.855 | 99.696 | 84 | 100 | 69 | 53 | 32.382 | 9.134 | 7.22 | 132.926 | 30.867 | 28.688 | 29.141 | 603.131 | 26.582 | 27.537 | 1285.718 | 27.363 | 27.592 | 38.464 | 28.001 | 3.9 | 3 | 1.2 | 0 | 0.4
3772 | 30/07/2025 11:32:15.488 | 99.96 | 84 | 100 | 70 | 52 | 28.746 | 8.987 | 7.221 | 133.239 | 30.891 | 28.688 | 29.142 | 603.192 | 26.601 | 27.535 | 1294.753 | 27.344 | 27.577 | 38.14 | 30.001 | 3.3 | 2.3 | 0.3 | 0.5 | 0.4
3773 | 30/07/2025 11:32:17.123 | 100.608 | 87 | 99 | 70 | 52 | 29.968 | 9.285 | 7.221 | 133.154 | 30.868 | 28.691 | 29.129 | 602.064 | 26.606 | 27.537 | 1290.743 | 27.34 | 27.617 | 38.529 | 30.001 | 3.3 | 2.3 | 0.3 | 0.5 | 0.4
3774 | 30/07/2025 11:32:18.754 | 100.248 | 86 | 100 | 70 | 52 | 29.799 | 9.334 | 7.237 | 133.332 | 30.875 | 28.676 | 29.122 | 601.994 | 26.6 | 27.528 | 1289.497 | 27.315 | 27.606 | 39.94 | 26.001 | 2.2 | 2.4 | 0.6 | 0.5 | 0.3
3775 | 30/07/2025 11:32:20.389 | 99.6 | 85 | 100 | 70 | 53 | 28.937 | 8.991 | 7.237 | 133.119 | 30.878 | 28.661 | 29.153 | 602.138 | 26.586 | 27.548 | 1292.391 | 27.381 | 27.608 | 38.432 | 27.001 | 2 | 4.3 | 0.6 | 0 | 0.3
3776 | 30/07/2025 11:32:22.026 | 99.96 | 85 | 99 | 71 | 52 | 32.182 | 9.134 | 7.241 | 132.988 | 30.856 | 28.686 | 29.135 | 601.975 | 26.622 | 27.573 | 1293.217 | 27.35 | 27.583 | 38.442 | 26.001 | 3.1 | 3.3 | 0.7 | 0 | 0.2
3777 | 30/07/2025 11:32:23.660 | 100.128 | 86 | 100 | 70 | 52 | 32.064 | 9.131 | 7.238 | 133.242 | 30.857 | 28.692 | 29.143 | 602.091 | 26.585 | 27.55 | 1306.97 | 27.34 | 27.599 | 38.051 | 25.001 | 2.2 | 2.8 | 1 | 0.8 | 0.2
3778 | 30/07/2025 11:32:25.296 | 100.704 | 88 | 100 | 70 | 53 | 28.365 | 9.131 | 7.239 | 133.005 | 30.861 | 28.688 | 29.111 | 601.969 | 26.597 | 27.569 | 1292.212 | 27.322 | 27.603 | 38.557 | 29.001 | 3.3 | 3 | 0.1 | 0.8 | 0.2
3779 | 30/07/2025 11:32:26.940 | 100.464 | 86 | 100 | 70 | 52 | 32.464 | 9.146 | 7.238 | 133.33 | 30.861 | 28.676 | 29.139 | 602.003 | 26.594 | 27.554 | 1289.309 | 27.321 | 27.618 | 38.356 | 29.001 | 3.3 | 3 | 0.1 | 0.8 | 0.2
3780 | 30/07/2025 11:32:28.574 | 100.608 | 86 | 100 | 70 | 53 | 29.274 | 9.11 | 7.221 | 133.097 | 30.856 | 28.669 | 29.139 | 602.127 | 26.58 | 27.572 | 1283.893 | 27.36 | 27.597 | 38.515 | 31.001 | 4.5 | 4.8 | 0 | 0.7 | 0.2
3781 | 30/07/2025 11:32:30.208 | 100.056 | 84 | 100 | 70 | 52 | 29.472 | 9.24 | 7.22 | 133.059 | 30.895 | 28.697 | 29.146 | 602.013 | 26.601 | 27.554 | 1282.075 | 27.346 | 27.573 | 38.58 | 28.001 | 3.1 | 3 | 0.7 | 0.7 | 0.2
3782 | 30/07/2025 11:32:31.847 | 100.08 | 85 | 100 | 70 | 52 | 32.287 | 9.132 | 7.24 | 133.236 | 30.881 | 28.688 | 29.139 | 602.01 | 26.595 | 27.553 | 1286.918 | 27.356 | 27.616 | 38.335 | 26.001 | 2.3 | 4.3 | 1.2 | 0.1 | 0.2
3783 | 30/07/2025 11:32:33.486 | 100.44 | 85 | 100 | 70 | 52 | 31.691 | 9.172 | 7.241 | 133.119 | 30.886 | 28.674 | 29.121 | 601.895 | 26.596 | 27.562 | 1287.214 | 27.312 | 27.602 | 38.435 | 31.001 | 3 | 3 | 0.6 | 0.1 | 0.2
3784 | 30/07/2025 11:32:35.126 | 100.488 | 86 | 100 | 69 | 53 | 28.257 | 9.228 | 7.238 | 133.121 | 30.881 | 28.668 | 29.146 | 602.1 | 26.588 | 27.526 | 1279.808 | 27.343 | 27.602 | 38.311 | 31.001 | 3 | 3 | 0.6 | 0.1 | 0.2
3785 | 30/07/2025 11:32:36.761 | 100.536 | 88 | 100 | 71 | 52 | 32.33 | 9.019 | 7.252 | 133.083 | 30.888 | 28.689 | 29.149 | 601.94 | 26.595 | 27.548 | 1276.849 | 27.354 | 27.595 | 38.323 | 24.001 | 2.4 | 3.5 | 0.7 | 0 | 0.1
3786 | 30/07/2025 11:32:38.396 | 100.248 | 86 | 100 | 70 | 53 | 28.763 | 9.209 | 7.276 | 133.131 | 30.884 | 28.69 | 29.136 | 602.177 | 26.574 | 27.543 | 1289.005 | 27.348 | 27.59 | 38.12 | 24.001 | 1.2 | 3 | 1 | 0 | 0.2
3787 | 30/07/2025 11:32:40.029 | 99.672 | 85 | 100 | 70 | 52 | 30.025 | 9.209 | 7.275 | 133.298 | 30.884 | 28.679 | 29.122 | 602.048 | 26.586 | 27.553 | 1283.694 | 27.332 | 27.608 | 38.563 | 29.001 | 0.9 | 4.1 | 1.1 | 0.6 | 0.2
3788 | 30/07/2025 11:32:41.664 | 99.888 | 85 | 100 | 70 | 52 | 32.331 | 9.204 | 7.275 | 134.669 | 30.89 | 28.672 | 29.13 | 601.882 | 26.588 | 27.538 | 1282.577 | 27.318 | 27.6 | 38.493 | 28.001 | 3.5 | 1.2 | 0.6 | 0.6 | 0.2
3789 | 30/07/2025 11:32:43.298 | 99.72 | 84 | 100 | 70 | 52 | 31.176 | 9.438 | 7.291 | 134.427 | 30.884 | 28.679 | 29.157 | 601.955 | 26.57 | 27.527 | 1279.946 | 27.374 | 27.611 | 40.268 | 25.001 | 2.3 | 3.4 | 0.6 | 0.1 | 0.3
3790 | 30/07/2025 11:32:44.940 | 99.336 | 85 | 100 | 70 | 52 | 32.22 | 9.292 | 7.267 | 134.317 | 30.89 | 28.695 | 29.151 | 602.477 | 26.575 | 27.511 | 1284.984 | 27.345 | 27.592 | 40.193 | 25.001 | 2.3 | 3.4 | 0.6 | 0.1 | 0.3
3791 | 30/07/2025 11:32:46.575 | 99.048 | 84 | 100 | 71 | 52 | 32.128 | 9.161 | 7.203 | 134.763 | 30.877 | 28.703 | 29.136 | 603.264 | 26.582 | 27.538 | 1276.627 | 27.371 | 27.589 | 38.153 | 23.001 | 3 | 4.6 | 0.9 | 0.1 | 0.2
3792 | 30/07/2025 11:32:48.210 | 99.48 | 84 | 100 | 70 | 52 | 28.465 | 9.208 | 7.189 | 134.708 | 30.888 | 28.689 | 29.125 | 603.158 | 26.601 | 27.544 | 1280.077 | 27.316 | 27.61 | 38.361 | 25.001 | 2.9 | 2.7 | 1 | 0 | 0.3
3793 | 30/07/2025 11:32:49.846 | 99.888 | 86 | 100 | 69 | 52 | 30.502 | 9.179 | 7.185 | 134.75 | 30.875 | 28.676 | 29.147 | 603.158 | 26.591 | 27.519 | 1279.692 | 27.342 | 27.609 | 38.381 | 26.001 | 2.4 | 1.1 | 2.3 | 0 | 0.2
3794 | 30/07/2025 11:32:51.563 | 99.864 | 86 | 100 | 70 | 52 | 32.418 | 8.988 | 7.187 | 134.373 | 30.866 | 28.692 | 29.137 | 603.107 | 26.59 | 27.546 | 1287.211 | 27.345 | 27.591 | 38.502 | 29.001 | 3 | 2.4 | 1.7 | 0 | 0.2
3795 | 30/07/2025 11:32:53.198 | 99.336 | 85 | 100 | 70 | 52 | 30.462 | 9.13 | 7.187 | 134.871 | 30.877 | 28.694 | 29.146 | 603.354 | 26.611 | 27.537 | 1285.117 | 27.341 | 27.584 | 38.163 | 29.001 | 3 | 2.4 | 1.7 | 0 | 0.2
3796 | 30/07/2025 11:32:54.832 | 99.312 | 84 | 100 | 70 | 52 | 28.504 | 9.137 | 7.191 | 134.78 | 30.856 | 28.696 | 29.126 | 603.29 | 26.608 | 27.555 | 1282.794 | 27.345 | 27.616 | 38.384 | 27.001 | 2.6 | 3.8 | 0.7 | 0 | 0.2
3797 | 30/07/2025 11:32:56.467 | 99.264 | 86 | 100 | 70 | 52 | 31.581 | 9.158 | 7.213 | 134.744 | 30.864 | 28.686 | 29.119 | 603.294 | 26.593 | 27.549 | 1279.491 | 27.316 | 27.611 | 38.459 | 27.001 | 1.8 | 3.8 | 0.6 | 0.5 | 0.2
3798 | 30/07/2025 11:32:58.103 | 99.096 | 83 | 99 | 70 | 51 | 28.228 | 9.212 | 7.204 | 134.613 | 30.866 | 28.665 | 29.143 | 603.238 | 26.596 | 27.569 | 1287.242 | 27.371 | 27.597 | 38.265 | 26.001 | 3.6 | 2.4 | 0.7 | 0.5 | 0.2
3799 | 30/07/2025 11:32:59.739 | 99.888 | 86 | 100 | 71 | 52 | 31.037 | 9.136 | 7.204 | 134.417 | 30.864 | 28.696 | 29.143 | 603.184 | 26.596 | 27.57 | 1278.114 | 27.346 | 27.58 | 38.477 | 26.001 | 2.3 | 2.6 | 0.6 | 0.6 | 0.2
3800 | 30/07/2025 11:33:01.374 | 99.504 | 85 | 100 | 70 | 52 | 32.434 | 9.129 | 7.237 | 134.675 | 30.864 | 28.69 | 29.143 | 602.53 | 26.594 | 27.556 | 1274.05 | 27.341 | 27.598 | 38.025 | 23.001 | 3.1 | 3.2 | 0.1 | 0.6 | 0.3
3801 | 30/07/2025 11:33:03.011 | 99.504 | 86 | 100 | 70 | 52 | 29.934 | 9.133 | 7.227 | 134.684 | 30.879 | 28.695 | 29.116 | 601.948 | 26.606 | 27.576 | 1267.622 | 27.326 | 27.607 | 38.595 | 23.001 | 3.1 | 3.2 | 0.1 | 0.6 | 0.3
3802 | 30/07/2025 11:33:04.645 | 98.976 | 84 | 100 | 71 | 52 | 28.93 | 8.982 | 7.219 | 134.779 | 30.894 | 28.667 | 29.138 | 601.951 | 26.604 | 27.551 | 1279.176 | 27.342 | 27.593 | 38.5 | 21.001 | 4 | 2.3 | 1.9 | 0.5 | 0.3
3803 | 30/07/2025 11:33:06.280 | 98.928 | 85 | 100 | 70 | 53 | 31.203 | 9.119 | 7.222 | 134.641 | 30.882 | 28.663 | 29.146 | 601.968 | 26.591 | 27.553 | 1285.101 | 27.351 | 27.595 | 38.628 | 24.001 | 3.2 | 2.9 | 0.9 | 0.5 | 0.2
3804 | 30/07/2025 11:33:07.915 | 98.784 | 84 | 100 | 70 | 52 | 28.298 | 9.225 | 7.22 | 134.558 | 30.895 | 28.697 | 29.147 | 603.225 | 26.603 | 27.557 | 1281.353 | 27.355 | 27.598 | 38.205 | 25.001 | 4 | 3.4 | 0.6 | 1 | 0.2
3805 | 30/07/2025 11:33:09.550 | 99.336 | 85 | 100 | 71 | 52 | 31.661 | 9.133 | 7.186 | 134.677 | 30.885 | 28.695 | 29.144 | 603.209 | 26.602 | 27.552 | 1277.02 | 27.355 | 27.606 | 38.462 | 24.001 | 2.3 | 3.2 | 0.6 | 1 | 0.2
3806 | 30/07/2025 11:33:11.216 | 99 | 83 | 100 | 70 | 52 | 32.473 | 8.983 | 7.188 | 134.653 | 30.895 | 28.679 | 29.101 | 603.092 | 26.601 | 27.542 | 1285.126 | 27.31 | 27.6 | 38.54 | 24.001 | 2.3 | 3.2 | 0.6 | 1 | 0.2
3807 | 30/07/2025 11:33:12.852 | 99.216 | 84 | 100 | 70 | 52 | 29.25 | 9.222 | 7.185 | 134.701 | 30.89 | 28.674 | 29.156 | 603.282 | 26.582 | 27.535 | 1274.3 | 27.351 | 27.607 | 38.423 | 26.001 | 1.2 | 2.3 | 0 | 0.5 | 0.2
3808 | 30/07/2025 11:33:14.488 | 99.048 | 86 | 100 | 70 | 52 | 32.44 | 9.143 | 7.187 | 134.622 | 30.897 | 28.683 | 29.156 | 603.119 | 26.599 | 27.552 | 1265.37 | 27.352 | 27.597 | 38.53 | 26.001 | 1.4 | 2.8 | 0 | 0.5 | 0.2
3809 | 30/07/2025 11:33:16.151 | 99.456 | 87 | 100 | 71 | 52 | 30.651 | 8.989 | 7.185 | 134.52 | 30.884 | 28.698 | 29.144 | 602.115 | 26.579 | 27.535 | 1274.234 | 27.351 | 27.582 | 38.409 | 22.001 | 2.1 | 4.6 | 0.6 | 0.5 | 0.1
3810 | 30/07/2025 11:33:17.788 | 99.336 | 84 | 100 | 71 | 52 | 28.608 | 9.212 | 7.188 | 134.789 | 30.883 | 28.694 | 29.139 | 601.995 | 26.586 | 27.552 | 1271.511 | 27.334 | 27.606 | 40.353 | 23.001 | 2.6 | 3.7 | 1.2 | 0.5 | 0.2
3811 | 30/07/2025 11:33:19.422 | 99.192 | 85 | 100 | 70 | 52 | 32.065 | 9.324 | 7.185 | 134.582 | 30.891 | 28.678 | 29.135 | 602.05 | 26.588 | 27.527 | 1274.068 | 27.322 | 27.599 | 40.371 | 26.001 | 3.6 | 2.9 | 0.9 | 0.7 | 0.2
3812 | 30/07/2025 11:33:21.057 | 98.592 | 84 | 100 | 70 | 53 | 32.433 | 9.002 | 7.186 | 134.555 | 30.876 | 28.679 | 29.159 | 601.98 | 26.584 | 27.544 | 1269.692 | 27.371 | 27.614 | 40.38 | 26.001 | 3.6 | 2.9 | 0.9 | 0.7 | 0.2
3813 | 30/07/2025 11:33:22.692 | 98.016 | 85 | 100 | 71 | 52 | 28.83 | 9.151 | 7.188 | 134.538 | 30.872 | 28.692 | 29.132 | 601.78 | 26.601 | 27.54 | 1263.433 | 27.356 | 27.574 | 38.3 | 31.001 | 2.4 | 2.3 | 1.3 | 0.7 | 0.2
3814 | 30/07/2025 11:33:24.328 | 98.448 | 82 | 100 | 71 | 52 | 32.471 | 9.259 | 7.187 | 134.639 | 30.872 | 28.692 | 29.142 | 601.951 | 26.59 | 27.543 | 1260.179 | 27.346 | 27.598 | 38.168 | 30.001 | 4.4 | 3.4 | 0.9 | 0.7 | 0.1
3815 | 30/07/2025 11:33:25.964 | 98.592 | 82 | 100 | 70 | 52 | 29.933 | 9.287 | 7.202 | 134.777 | 30.886 | 28.686 | 29.117 | 601.989 | 26.607 | 27.542 | 1264.199 | 27.315 | 27.608 | 38.603 | 30.001 | 2.3 | 4.8 | 1.1 | 0.7 | 0.1
3816 | 30/07/2025 11:33:27.599 | 98.64 | 84 | 99 | 71 | 52 | 28.866 | 9.207 | 7.201 | 134.739 | 30.88 | 28.67 | 29.151 | 602.054 | 26.596 | 27.552 | 1267.461 | 27.333 | 27.619 | 38.492 | 27.001 | 2.7 | 4 | 0.8 | 0 | 0.2
3817 | 30/07/2025 11:33:29.257 | 98.208 | 83 | 100 | 70 | 52 | 32.119 | 9.23 | 7.204 | 134.458 | 30.859 | 28.686 | 29.146 | 600.757 | 26.583 | 27.56 | 1274.173 | 27.353 | 27.597 | 40.273 | 27.001 | 2.7 | 4 | 0.8 | 0 | 0.2
3818 | 30/07/2025 11:33:30.900 | 98.712 | 84 | 100 | 70 | 52 | 32.047 | 9.132 | 7.233 | 134.484 | 30.865 | 28.693 | 29.159 | 600.479 | 26.603 | 27.559 | 1277.159 | 27.348 | 27.591 | 40.048 | 24.001 | 2.8 | 2.5 | 0.6 | 0 | 0.2
3819 | 30/07/2025 11:33:32.570 | 98.64 | 83 | 100 | 71 | 52 | 31.519 | 9.131 | 7.241 | 134.528 | 30.861 | 28.689 | 29.131 | 600.357 | 26.605 | 27.566 | 1286.783 | 27.336 | 27.603 | 40.075 | 23.001 | 1.9 | 2.9 | 0.3 | 0.6 | 0.2
3820 | 30/07/2025 11:33:34.206 | 98.448 | 84 | 100 | 70 | 52 | 32.491 | 9.248 | 7.278 | 134.707 | 30.857 | 28.686 | 29.124 | 602.226 | 26.6 | 27.542 | 1293.048 | 27.301 | 27.603 | 40.553 | 27.001 | 2.8 | 4 | 0.6 | 0.6 | 0.2
3821 | 30/07/2025 11:33:35.842 | 98.352 | 83 | 100 | 70 | 52 | 29.375 | 9.286 | 7.288 | 134.46 | 30.864 | 28.671 | 29.136 | 602.094 | 26.593 | 27.56 | 1292.573 | 27.363 | 27.6 | 38.669 | 25.001 | 3.1 | 3.5 | 0.1 | 0 | 0.2
3822 | 30/07/2025 11:33:37.479 | 97.92 | 83 | 100 | 71 | 52 | 29.459 | 9.131 | 7.223 | 134.443 | 30.885 | 28.69 | 29.141 | 601.895 | 26.606 | 27.558 | 1288.96 | 27.342 | 27.599 | 38.462 | 26.001 | 2.1 | 2.1 | 0.6 | 0 | 0.2
3823 | 30/07/2025 11:33:39.113 | 98.28 | 84 | 100 | 72 | 52 | 32.274 | 9.291 | 7.202 | 134.795 | 30.87 | 28.698 | 29.146 | 602.008 | 26.585 | 27.548 | 1288.484 | 27.353 | 27.6 | 38.168 | 26.001 | 2.1 | 2.1 | 0.6 | 0 | 0.2
3824 | 30/07/2025 11:33:40.750 | 97.56 | 82 | 100 | 70 | 52 | 28.535 | 9.129 | 7.205 | 134.652 | 30.899 | 28.687 | 29.144 | 601.711 | 26.612 | 27.562 | 1294.968 | 27.33 | 27.607 | 38.282 | 29.001 | 2.7 | 2.7 | 1.3 | 0.6 | 0.2
3825 | 30/07/2025 11:33:42.387 | 97.056 | 82 | 100 | 71 | 52 | 31.923 | 9.13 | 7.202 | 134.693 | 30.891 | 28.684 | 29.12 | 602.074 | 26.598 | 27.542 | 1291.31 | 27.326 | 27.611 | 38.491 | 26.001 | 2.2 | 2.6 | 1.2 | 0.6 | 0.2
3826 | 30/07/2025 11:33:44.023 | 97.176 | 84 | 100 | 71 | 52 | 32.349 | 9.267 | 7.204 | 134.646 | 30.9 | 28.672 | 29.144 | 601.926 | 26.584 | 27.558 | 1289.789 | 27.358 | 27.605 | 38.443 | 30.001 | 2.3 | 2.9 | 0.9 | 0.6 | 0.2
3827 | 30/07/2025 11:33:45.657 | 97.512 | 83 | 100 | 71 | 52 | 28.692 | 9.272 | 7.239 | 134.393 | 30.902 | 28.698 | 29.153 | 602.088 | 26.6 | 27.54 | 1287.241 | 27.342 | 27.575 | 38.242 | 22.001 | 1.8 | 3.1 | 1.3 | 0.6 | 0.2
3828 | 30/07/2025 11:33:47.295 | 97.056 | 82 | 100 | 70 | 52 | 30.015 | 9.179 | 7.22 | 134.766 | 30.883 | 28.702 | 29.129 | 602.075 | 26.585 | 27.551 | 1299.334 | 27.358 | 27.597 | 38.378 | 28.001 | 2.8 | 1.5 | 0.3 | 0.1 | 0.2
3829 | 30/07/2025 11:33:48.943 | 96.96 | 82 | 100 | 70 | 51 | 32.333 | 9.136 | 7.221 | 134.869 | 30.889 | 28.685 | 29.116 | 601.837 | 26.589 | 27.544 | 1304.222 | 27.313 | 27.597 | 38.431 | 28.001 | 2.8 | 1.5 | 0.3 | 0.1 | 0.2
3830 | 30/07/2025 11:33:50.577 | 97.08 | 84 | 100 | 70 | 52 | 28.981 | 9.212 | 7.219 | 134.353 | 30.881 | 28.669 | 29.129 | 602.038 | 26.578 | 27.551 | 1299.317 | 27.327 | 27.602 | 38.565 | 22.001 | 3.1 | 1.7 | 1 | 0.1 | 0.2
3831 | 30/07/2025 11:33:52.213 | 97.728 | 82 | 100 | 70 | 51 | 32.224 | 8.987 | 7.22 | 134.641 | 30.871 | 28.682 | 29.146 | 602.017 | 26.579 | 27.536 | 1302.45 | 27.356 | 27.595 | 38.61 | 25.001 | 1.9 | 2.2 | 0.9 | 0.5 | 0.2
3832 | 30/07/2025 11:33:53.847 | 97.728 | 83 | 100 | 71 | 52 | 32.192 | 8.99 | 7.203 | 134.618 | 30.887 | 28.699 | 29.148 | 602.052 | 26.574 | 27.529 | 1294.297 | 27.356 | 27.602 | 38.351 | 28.001 | 3.3 | 3.2 | 0.7 | 0.5 | 0.2
3833 | 30/07/2025 11:33:55.483 | 97.824 | 84 | 100 | 70 | 52 | 28.509 | 8.993 | 7.204 | 134.749 | 30.883 | 28.687 | 29.137 | 601.887 | 26.58 | 27.543 | 1287.815 | 27.33 | 27.603 | 38.433 | 30.001 | 5.3 | 3.5 | 0.9 | 0.3 | 0.2
3834 | 30/07/2025 11:33:57.116 | 97.344 | 84 | 100 | 70 | 53 | 30.648 | 8.914 | 7.218 | 134.605 | 30.89 | 28.679 | 29.139 | 601.974 | 26.589 | 27.535 | 1289.915 | 27.32 | 27.6 | 38.477 | 30.001 | 5.3 | 3.5 | 0.9 | 0.3 | 0.2
3835 | 30/07/2025 11:33:58.750 | 96.936 | 83 | 100 | 71 | 52 | 32.451 | 9.431 | 7.202 | 134.542 | 30.861 | 28.676 | 29.14 | 602.199 | 26.604 | 27.552 | 1287.894 | 27.373 | 27.601 | 38.651 | 24.001 | 3.1 | 3.2 | 0.2 | 0.3 | 0.2
3836 | 30/07/2025 11:34:00.383 | 97.104 | 84 | 100 | 71 | 52 | 29.441 | 9.435 | 7.203 | 134.312 | 30.875 | 28.689 | 29.145 | 602.148 | 26.598 | 27.534 | 1287.694 | 27.346 | 27.603 | 38.533 | 27.001 | 2.2 | 3.5 | 0.6 | 0 | 0.2
3837 | 30/07/2025 11:34:02.017 | 97.608 | 83 | 100 | 71 | 52 | 32.342 | 9.004 | 7.221 | 134.504 | 30.868 | 28.698 | 29.131 | 602.028 | 26.592 | 27.565 | 1277.12 | 27.357 | 27.578 | 38.38 | 29.001 | 2.8 | 2.3 | 1.1 | 0 | 0.2
3838 | 30/07/2025 11:34:03.649 | 97.632 | 84 | 100 | 70 | 52 | 31.72 | 8.981 | 7.219 | 134.886 | 30.876 | 28.686 | 29.13 | 601.828 | 26.611 | 27.559 | 1281.836 | 27.322 | 27.611 | 38.386 | 21.001 | 3.6 | 4 | 1.1 | 0.2 | 0.2
3839 | 30/07/2025 11:34:05.283 | 97.272 | 84 | 100 | 70 | 53 | 28.289 | 9.132 | 7.217 | 133.109 | 30.85 | 28.676 | 29.124 | 601.955 | 26.596 | 27.551 | 1280.081 | 27.329 | 27.61 | 38.553 | 21.001 | 3.6 | 4 | 1.1 | 0.2 | 0.2
3840 | 30/07/2025 11:34:06.916 | 97.128 | 82 | 100 | 71 | 52 | 31.059 | 9.286 | 7.186 | 133.041 | 30.863 | 28.686 | 29.137 | 601.997 | 26.599 | 27.552 | 1277.586 | 27.345 | 27.595 | 38.528 | 25.001 | 3 | 1.7 | 0.6 | 0.2 | 0.3
3841 | 30/07/2025 11:34:08.552 | 97.296 | 83 | 100 | 70 | 52 | 28.931 | 9.287 | 7.187 | 132.929 | 30.858 | 28.697 | 29.141 | 601.998 | 26.589 | 27.565 | 1280.703 | 27.367 | 27.592 | 38.488 | 24.001 | 2.1 | 3.2 | 0.6 | 0.5 | 0.2
3842 | 30/07/2025 11:34:10.184 | 98.328 | 85 | 100 | 69 | 52 | 30.213 | 9.211 | 7.136 | 133.155 | 30.868 | 28.684 | 29.136 | 602.023 | 26.588 | 27.556 | 1294.679 | 27.337 | 27.585 | 38.254 | 23.001 | 3.6 | 3.3 | 0.7 | 0.5 | 0.3
3843 | 30/07/2025 11:34:11.816 | 98.76 | 86 | 100 | 70 | 52 | 32.355 | 9.213 | 7.134 | 133.269 | 30.882 | 28.685 | 29.127 | 602.05 | 26.581 | 27.551 | 1305.785 | 27.316 | 27.616 | 38.633 | 25.001 | 3.3 | 4.1 | 1.5 | 0.5 | 0.3
3844 | 30/07/2025 11:34:13.448 | 99.048 | 85 | 100 | 70 | 51 | 31.147 | 9.063 | 7.133 | 133.218 | 30.88 | 28.665 | 29.135 | 602.009 | 26.594 | 27.572 | 1306.489 | 27.352 | 27.601 | 40.476 | 30.001 | 1.9 | 3.1 | 0.6 | 0.5 | 0.2
3845 | 30/07/2025 11:34:15.081 | 99.312 | 84 | 100 | 71 | 52 | 28.306 | 9.128 | 7.135 | 133.053 | 30.9 | 28.692 | 29.153 | 601.92 | 26.619 | 27.557 | 1295.709 | 27.348 | 27.585 | 39.864 | 30.001 | 1.9 | 3.1 | 0.6 | 0.5 | 0.2
3846 | 30/07/2025 11:34:16.714 | 99.432 | 85 | 100 | 72 | 52 | 32.078 | 9.14 | 7.136 | 132.906 | 30.89 | 28.693 | 29.146 | 602 | 26.595 | 27.562 | 1291.309 | 27.352 | 27.591 | 38.327 | 24.001 | 1.3 | 3 | 1.5 | 0.8 | 0.2
3847 | 30/07/2025 11:34:18.347 | 99.096 | 85 | 100 | 71 | 51 | 28.39 | 9.204 | 7.15 | 133.201 | 30.903 | 28.69 | 29.141 | 602.015 | 26.604 | 27.555 | 1287.247 | 27.34 | 27.606 | 38.302 | 22.001 | 2.4 | 2.7 | 0.7 | 0.8 | 0.3
3848 | 30/07/2025 11:34:19.981 | 99.168 | 86 | 100 | 71 | 51 | 30.565 | 8.989 | 7.15 | 133.219 | 30.882 | 28.681 | 29.12 | 601.99 | 26.594 | 27.546 | 1286.296 | 27.342 | 27.59 | 38.63 | 29.001 | 3 | 2.6 | 0.1 | 0 | 0.3
3849 | 30/07/2025 11:34:21.616 | 99.624 | 84 | 100 | 70 | 51 | 32.459 | 8.984 | 7.152 | 133.171 | 30.881 | 28.673 | 29.148 | 601.977 | 26.588 | 27.556 | 1281.446 | 27.356 | 27.605 | 38.446 | 30.001 | 3 | 2 | 0.7 | 0 | 0.2
3850 | 30/07/2025 11:34:23.252 | 99.528 | 85 | 100 | 70 | 52 | 30.611 | 9.215 | 7.151 | 133.019 | 30.885 | 28.698 | 29.152 | 602.258 | 26.592 | 27.544 | 1269.985 | 27.344 | 27.589 | 38.305 | 30.001 | 3 | 2 | 0.7 | 0 | 0.2
3851 | 30/07/2025 11:34:24.888 | 99.36 | 84 | 100 | 71 | 52 | 28.603 | 9.135 | 7.151 | 133.14 | 30.877 | 28.701 | 29.13 | 602.011 | 26.575 | 27.559 | 1274.245 | 27.36 | 27.608 | 38.179 | 33.001 | 2.3 | 2 | 1 | 0.6 | 0.2
3852 | 30/07/2025 11:34:26.522 | 99.672 | 86 | 100 | 71 | 52 | 31.865 | 9.133 | 7.151 | 133.352 | 30.871 | 28.692 | 29.133 | 602.143 | 26.573 | 27.533 | 1269.796 | 27.326 | 27.622 | 38.429 | 28.001 | 2.1 | 2.7 | 0.5 | 0.6 | 0.2
3853 | 30/07/2025 11:34:28.157 | 99.6 | 86 | 100 | 70 | 52 | 28.298 | 9.288 | 7.151 | 133.12 | 30.875 | 28.679 | 29.117 | 601.716 | 26.584 | 27.554 | 1275.145 | 27.331 | 27.599 | 38.466 | 24.001 | 3.3 | 2.1 | 0.6 | 1.5 | 0.1
3854 | 30/07/2025 11:34:29.791 | 99.504 | 85 | 100 | 70 | 50 | 31.21 | 9.025 | 7.151 | 133.196 | 30.895 | 28.677 | 29.145 | 602.231 | 26.586 | 27.518 | 1280.845 | 27.35 | 27.593 | 38.713 | 26.001 | 1.7 | 4.3 | 0.9 | 1.5 | 0.2
3855 | 30/07/2025 11:34:31.426 | 99.144 | 86 | 100 | 71 | 52 | 32.55 | 9.151 | 7.152 | 132.971 | 30.889 | 28.702 | 29.146 | 602.104 | 26.597 | 27.532 | 1289.069 | 27.362 | 27.602 | 38.296 | 26.001 | 2.1 | 2.6 | 1 | 0.6 | 0.2
3856 | 30/07/2025 11:34:33.060 | 99.288 | 85 | 100 | 71 | 52 | 29.973 | 9.239 | 7.153 | 133.255 | 30.874 | 28.695 | 29.137 | 601.854 | 26.61 | 27.565 | 1297.311 | 27.33 | 27.605 | 38.315 | 26.001 | 2.1 | 2.6 | 1 | 0.6 | 0.2
3857 | 30/07/2025 11:34:34.695 | 98.232 | 84 | 100 | 70 | 52 | 32.348 | 9.418 | 7.151 | 133.238 | 30.867 | 28.697 | 29.13 | 601.806 | 26.608 | 27.562 | 1297.089 | 27.343 | 27.614 | 38.444 | 23.001 | 1.6 | 1.5 | 1 | 0.6 | 0.2
3858 | 30/07/2025 11:34:36.329 | 97.608 | 82 | 100 | 70 | 51 | 31.169 | 9.29 | 7.15 | 134.687 | 30.867 | 28.667 | 29.122 | 601.702 | 26.605 | 27.56 | 1290.587 | 27.333 | 27.599 | 38.567 | 24.001 | 1.1 | 2.7 | 1.7 | 0.3 | 0.2
3859 | 30/07/2025 11:34:37.963 | 97.008 | 84 | 100 | 70 | 50 | 28.316 | 9.287 | 7.186 | 134.448 | 30.861 | 28.685 | 29.161 | 602.041 | 26.586 | 27.56 | 1285.019 | 27.348 | 27.607 | 38.302 | 25.001 | 3 | 2.6 | 0.8 | 0.3 | 0.3
3860 | 30/07/2025 11:34:39.599 | 95.856 | 82 | 100 | 71 | 52 | 31.601 | 9.142 | 7.187 | 134.196 | 30.86 | 28.696 | 29.146 | 601.949 | 26.598 | 27.581 | 1285.532 | 27.345 | 27.588 | 38.298 | 26.001 | 2.1 | 2.3 | 0 | 0.8 | 0.3
3861 | 30/07/2025 11:34:41.234 | 96 | 83 | 100 | 70 | 52 | 32.565 | 9.283 | 7.185 | 134.924 | 30.873 | 28.69 | 29.134 | 601.95 | 26.612 | 27.552 | 1284.267 | 27.325 | 27.609 | 40.237 | 26.001 | 2.1 | 2.3 | 0 | 0.8 | 0.3
3862 | 30/07/2025 11:34:42.869 | 95.952 | 82 | 100 | 71 | 52 | 29.474 | 9.179 | 7.186 | 134.681 | 30.862 | 28.668 | 29.129 | 601.996 | 26.588 | 27.548 | 1284.819 | 27.346 | 27.604 | 40.542 | 26.001 | 3.7 | 2.8 | 0.6 | 0.8 | 0.3
3863 | 30/07/2025 11:34:44.505 | 96.624 | 82 | 100 | 71 | 52 | 32.412 | 9.134 | 7.185 | 134.638 | 30.869 | 28.671 | 29.16 | 602.009 | 26.587 | 27.538 | 1284.429 | 27.346 | 27.603 | 40.287 | 27.001 | 3.5 | 2.6 | 1.3 | 0.1 | 0.2
3864 | 30/07/2025 11:34:46.141 | 97.104 | 82 | 100 | 69 | 52 | 30.671 | 8.991 | 7.187 | 134.297 | 30.884 | 28.695 | 29.156 | 602.069 | 26.598 | 27.557 | 1287.541 | 27.373 | 27.591 | 38.585 | 30.001 | 3.1 | 3.1 | 0.6 | 0.1 | 0.2
3865 | 30/07/2025 11:34:47.776 | 97.152 | 84 | 100 | 70 | 52 | 28.479 | 9.128 | 7.152 | 133.312 | 30.882 | 28.686 | 29.147 | 601.985 | 26.599 | 27.56 | 1292.07 | 27.345 | 27.583 | 38.34 | 30.001 | 4.3 | 2.1 | 0.9 | 0.1 | 0.2
3866 | 30/07/2025 11:34:49.414 | 98.304 | 84 | 100 | 71 | 52 | 31.911 | 9.229 | 7.151 | 133.32 | 30.891 | 28.689 | 29.131 | 602.207 | 26.581 | 27.537 | 1283.3 | 27.317 | 27.615 | 38.713 | 24.001 | 2.7 | 4.2 | 0.6 | 0.1 | 0.2
3867 | 30/07/2025 11:34:51.049 | 97.944 | 83 | 100 | 69 | 52 | 32.364 | 9.431 | 7.187 | 133.231 | 30.896 | 28.668 | 29.131 | 601.86 | 26.585 | 27.564 | 1281.581 | 27.342 | 27.597 | 38.556 | 24.001 | 2.7 | 4.2 | 0.6 | 0.1 | 0.2
3868 | 30/07/2025 11:34:52.685 | 98.616 | 84 | 100 | 70 | 53 | 31.045 | 9.443 | 7.183 | 133.186 | 30.893 | 28.68 | 29.154 | 601.994 | 26.584 | 27.55 | 1287.162 | 27.354 | 27.614 | 38.37 | 26.001 | 1.2 | 2.4 | 0.6 | 1.2 | 0.2
3869 | 30/07/2025 11:34:54.319 | 98.736 | 86 | 100 | 70 | 52 | 32.473 | 9.292 | 7.189 | 132.769 | 30.892 | 28.69 | 29.146 | 602.032 | 26.587 | 27.561 | 1282.908 | 27.343 | 27.588 | 38.493 | 24.001 | 2.1 | 2.5 | 0.9 | 1.2 | 0.2
3870 | 30/07/2025 11:34:55.953 | 99.096 | 84 | 100 | 70 | 52 | 29.947 | 9.423 | 7.186 | 133.333 | 30.887 | 28.687 | 29.135 | 602.104 | 26.579 | 27.539 | 1279.459 | 27.333 | 27.586 | 38.425 | 28.001 | 3.2 | 3.2 | 0.3 | 0 | 0.1
3871 | 30/07/2025 11:34:57.589 | 99.168 | 85 | 100 | 70 | 52 | 28.925 | 9.288 | 7.186 | 133.14 | 30.881 | 28.687 | 29.129 | 600.409 | 26.591 | 27.551 | 1282.227 | 27.332 | 27.621 | 38.458 | 23.001 | 3.9 | 3.6 | 0 | 0 | 0.1
3872 | 30/07/2025 11:34:59.224 | 98.88 | 87 | 100 | 70 | 52 | 32.198 | 9.142 | 7.221 | 133.174 | 30.884 | 28.665 | 29.148 | 601.674 | 26.576 | 27.56 | 1267.837 | 27.353 | 27.601 | 38.491 | 23.001 | 3.9 | 3.6 | 0 | 0 | 0.1
3873 | 30/07/2025 11:35:00.859 | 99.408 | 84 | 100 | 70 | 52 | 32.149 | 8.986 | 7.268 | 132.969 | 30.891 | 28.695 | 29.145 | 602.029 | 26.577 | 27.506 | 1257.752 | 27.345 | 27.59 | 38.524 | 25.001 | 2.5 | 4.4 | 0.6 | 0 | 0.1
3874 | 30/07/2025 11:35:02.492 | 99.312 | 85 | 100 | 71 | 52 | 31.64 | 9.202 | 7.279 | 133.179 | 30.89 | 28.693 | 29.143 | 601.955 | 26.604 | 27.527 | 1259.888 | 27.347 | 27.579 | 38.303 | 29.001 | 4.3 | 2.6 | 0.7 | 0 | 0.1
3875 | 30/07/2025 11:35:04.124 | 99.024 | 84 | 100 | 71 | 52 | 32.539 | 9.139 | 7.275 | 133.193 | 30.866 | 28.692 | 29.132 | 602.038 | 26.586 | 27.524 | 1264.082 | 27.344 | 27.612 | 40.239 | 25.001 | 3.4 | 3.5 | 0.6 | 0 | 0.1
3876 | 30/07/2025 11:35:05.758 | 99.288 | 84 | 100 | 69 | 52 | 29.391 | 9.129 | 7.262 | 132.937 | 30.874 | 28.668 | 29.111 | 601.802 | 26.583 | 27.532 | 1266.709 | 27.32 | 27.602 | 38.336 | 30.001 | 1.5 | 4.3 | 0.3 | 0 | 0.1
3877 | 30/07/2025 11:35:07.394 | 99.168 | 85 | 100 | 71 | 52 | 29.486 | 9.213 | 7.218 | 133.17 | 30.884 | 28.68 | 29.164 | 601.876 | 26.602 | 27.542 | 1266.84 | 27.357 | 27.6 | 38.375 | 30.001 | 2.9 | 4.8 | 0.6 | 0.2 | 0.1
3878 | 30/07/2025 11:35:09.030 | 99.504 | 84 | 100 | 69 | 52 | 32.34 | 9.136 | 7.188 | 132.909 | 30.864 | 28.69 | 29.137 | 602.067 | 26.591 | 27.552 | 1277.16 | 27.362 | 27.582 | 38.478 | 30.001 | 2.9 | 4.8 | 0.6 | 0.2 | 0.1
3879 | 30/07/2025 11:35:10.666 | 99.288 | 85 | 100 | 71 | 52 | 28.565 | 9.131 | 7.187 | 133.16 | 30.879 | 28.693 | 29.154 | 602.022 | 26.597 | 27.545 | 1276.887 | 27.344 | 27.583 | 38.296 | 28.001 | 2.6 | 4.3 | 1.4 | 0.2 | 0.1
3880 | 30/07/2025 11:35:12.304 | 99.528 | 87 | 100 | 70 | 52 | 32.042 | 9.132 | 7.135 | 132.963 | 30.859 | 28.687 | 29.133 | 601.946 | 26.594 | 27.573 | 1277.138 | 27.338 | 27.607 | 38.563 | 31.001 | 3.2 | 2 | 1.5 | 0 | 0.1
3881 | 30/07/2025 11:35:13.940 | 99.336 | 85 | 100 | 70 | 52 | 32.489 | 9.276 | 7.132 | 133.444 | 30.865 | 28.666 | 29.138 | 601.963 | 26.621 | 27.569 | 1276.95 | 27.334 | 27.604 | 38.462 | 28.001 | 1.6 | 3.8 | 0.6 | 0 | 0
3882 | 30/07/2025 11:35:15.576 | 99.384 | 86 | 100 | 71 | 53 | 28.976 | 9.296 | 7.121 | 133.046 | 30.869 | 28.693 | 29.144 | 601.981 | 26.59 | 27.559 | 1272.241 | 27.352 | 27.611 | 38.429 | 25.001 | 3 | 2.5 | 1 | 0 | 0.1
3883 | 30/07/2025 11:35:17.212 | 99.048 | 85 | 100 | 69 | 53 | 30.077 | 9.44 | 7.13 | 133.004 | 30.854 | 28.689 | 29.135 | 601.78 | 26.592 | 27.573 | 1272.117 | 27.348 | 27.586 | 39.996 | 25.001 | 3 | 2.5 | 1 | 0 | 0.1
3884 | 30/07/2025 11:35:18.847 | 99.096 | 84 | 100 | 71 | 52 | 32.339 | 9.431 | 7.134 | 133.33 | 30.881 | 28.69 | 29.132 | 602.005 | 26.753 | 27.548 | 1269.537 | 27.321 | 27.601 | 38.38 | 24.001 | 2.1 | 3.4 | 0.8 | 0 | 0.1
3885 | 30/07/2025 11:35:20.484 | 99 | 85 | 100 | 71 | 52 | 28.899 | 9.288 | 7.168 | 132.989 | 30.883 | 28.687 | 29.112 | 602 | 26.735 | 27.564 | 1271.499 | 27.32 | 27.592 | 38.567 | 29.001 | 3.1 | 1.7 | 1.5 | 0.1 | 0.1
3886 | 30/07/2025 11:35:22.119 | 98.616 | 84 | 100 | 70 | 52 | 32.175 | 9.184 | 7.185 | 133.187 | 30.895 | 28.676 | 29.147 | 602.038 | 26.587 | 27.538 | 1258.481 | 27.34 | 27.592 | 39.924 | 25.001 | 3.2 | 4.3 | 1 | 0.1 | 0.2
3887 | 30/07/2025 11:35:23.754 | 98.328 | 84 | 100 | 71 | 52 | 32.155 | 9.162 | 7.222 | 132.86 | 30.874 | 28.702 | 29.147 | 601.849 | 26.588 | 27.567 | 1263.144 | 27.368 | 27.596 | 38.476 | 25.001 | 1.7 | 3.9 | 0.2 | 0.5 | 0.2
3888 | 30/07/2025 11:35:25.387 | 98.112 | 85 | 100 | 70 | 52 | 28.443 | 9.128 | 7.19 | 134.659 | 30.907 | 28.688 | 29.142 | 601.785 | 26.634 | 27.554 | 1262.186 | 27.338 | 27.587 | 38.19 | 27.001 | 2.8 | 4.5 | 0 | 0.5 | 0.2
3889 | 30/07/2025 11:35:27.021 | 98.208 | 84 | 100 | 71 | 52 | 30.477 | 9.266 | 7.187 | 134.681 | 30.893 | 28.688 | 29.132 | 602.065 | 26.581 | 27.543 | 1270.001 | 27.326 | 27.61 | 38.618 | 27.001 | 2.8 | 4.5 | 0 | 0.5 | 0.2
3890 | 30/07/2025 11:35:28.678 | 98.304 | 85 | 100 | 70 | 52 | 29.351 | 9.287 | 7.185 | 134.628 | 30.892 | 28.68 | 29.124 | 602.026 | 26.604 | 27.548 | 1272.432 | 27.304 | 27.598 | 38.56 | 30.001 | 3.2 | 4.1 | 1.1 | 0.6 | 0.2
3891 | 30/07/2025 11:35:30.312 | 98.088 | 84 | 100 | 70 | 52 | 29.391 | 9.176 | 7.181 | 134.78 | 30.881 | 28.684 | 29.147 | 602.01 | 26.733 | 27.542 | 1266.862 | 27.37 | 27.595 | 38.396 | 27.001 | 4 | 4.6 | 0.5 | 0.6 | 0.2
3892 | 30/07/2025 11:35:31.947 | 98.184 | 83 | 100 | 71 | 52 | 32.338 | 9.291 | 7.155 | 134.356 | 30.881 | 28.693 | 29.144 | 601.863 | 26.726 | 27.547 | 1258.485 | 27.351 | 27.586 | 38.291 | 23.001 | 3.5 | 3.2 | 1.6 | 0.5 | 0.2
3893 | 30/07/2025 11:35:33.582 | 97.872 | 83 | 100 | 70 | 54 | 31.746 | 9.233 | 7.152 | 134.778 | 30.885 | 28.693 | 29.147 | 601.986 | 26.726 | 27.538 | 1257.153 | 27.341 | 27.594 | 38.203 | 28.001 | 4.2 | 2.7 | 0.6 | 0.5 | 0.2
3894 | 30/07/2025 11:35:35.218 | 98.376 | 84 | 100 | 70 | 52 | 28.283 | 9.209 | 7.151 | 134.525 | 30.873 | 28.697 | 29.133 | 603.029 | 26.729 | 27.521 | 1263.771 | 27.335 | 27.606 | 38.57 | 28.001 | 4.2 | 2.7 | 0.6 | 0.5 | 0.2
3895 | 30/07/2025 11:35:36.858 | 98.376 | 83 | 100 | 72 | 52 | 31.104 | 9.128 | 7.151 | 134.684 | 30.893 | 28.665 | 29.133 | 602.134 | 26.745 | 27.535 | 1269.939 | 27.35 | 27.589 | 38.63 | 28.001 | 3.2 | 4.4 | 0.9 | 0.1 | 0.3
3896 | 30/07/2025 11:35:38.493 | 98.232 | 83 | 100 | 70 | 53 | 28.785 | 8.993 | 7.152 | 134.5 | 30.883 | 28.677 | 29.13 | 601.897 | 26.73 | 27.529 | 1269.827 | 27.356 | 27.591 | 38.634 | 30.001 | 2.8 | 1.9 | 0.6 | 0.1 | 0.2
3897 | 30/07/2025 11:35:40.129 | 98.208 | 83 | 100 | 70 | 52 | 29.971 | 8.979 | 7.152 | 134.561 | 30.886 | 28.687 | 29.142 | 602.008 | 26.759 | 27.534 | 1267.711 | 27.337 | 27.581 | 38.331 | 24.001 | 2.3 | 2.2 | 0.7 | 0.8 | 0.2
3898 | 30/07/2025 11:35:41.764 | 98.256 | 84 | 100 | 71 | 52 | 32.368 | 9.136 | 7.168 | 134.536 | 30.867 | 28.695 | 29.134 | 601.936 | 26.75 | 27.536 | 1267.394 | 27.344 | 27.61 | 38.457 | 28.001 | 2.3 | 2.6 | 1.2 | 0.8 | 0.2
3899 | 30/07/2025 11:35:43.398 | 98.184 | 84 | 100 | 71 | 52 | 31.206 | 9.131 | 7.188 | 134.602 | 30.866 | 28.677 | 29.114 | 601.877 | 26.741 | 27.568 | 1260.681 | 27.318 | 27.602 | 38.352 | 27.001 | 1.9 | 2.4 | 0.9 | 0.6 | 0.2
3900 | 30/07/2025 11:35:45.033 | 97.992 | 84 | 100 | 70 | 52 | 28.284 | 9.208 | 7.185 | 134.655 | 30.878 | 28.671 | 29.165 | 602.047 | 26.751 | 27.555 | 1257.345 | 27.353 | 27.597 | 38.475 | 27.001 | 1.9 | 2.4 | 0.9 | 0.6 | 0.2
3901 | 30/07/2025 11:35:46.669 | 97.992 | 84 | 100 | 70 | 52 | 32.245 | 9.289 | 7.187 | 134.503 | 30.864 | 28.686 | 29.144 | 601.836 | 26.747 | 27.573 | 1256.49 | 27.351 | 27.589 | 38.402 | 29.001 | 3.2 | 3.3 | 0.9 | 0.6 | 0.1
3902 | 30/07/2025 11:35:48.304 | 97.992 | 83 | 100 | 69 | 52 | 28.523 | 9.228 | 7.188 | 134.658 | 30.848 | 28.688 | 29.142 | 602.069 | 26.739 | 27.699 | 1258.385 | 27.342 | 27.573 | 38.187 | 25.001 | 2.7 | 2.3 | 0.8 | 0.4 | 0.2
3903 | 30/07/2025 11:35:49.941 | 97.896 | 84 | 100 | 70 | 53 | 30.687 | 9.213 | 7.203 | 134.525 | 30.848 | 28.681 | 29.12 | 601.876 | 26.741 | 27.595 | 1266.141 | 27.343 | 27.604 | 38.773 | 27.001 | 1.4 | 2.5 | 2.6 | 0.4 | 0.2
3904 | 30/07/2025 11:35:51.580 | 97.92 | 84 | 100 | 71 | 51 | 32.387 | 9.154 | 7.203 | 134.676 | 30.883 | 28.67 | 29.138 | 601.805 | 26.756 | 27.562 | 1259.746 | 27.315 | 27.611 | 39.135 | 26.001 | 2 | 2.4 | 1.2 | 1 | 0.2
3905 | 30/07/2025 11:35:53.217 | 97.536 | 83 | 100 | 71 | 51 | 30.701 | 9.22 | 7.22 | 134.526 | 30.87 | 28.685 | 29.142 | 601.958 | 26.743 | 27.553 | 1261.459 | 27.358 | 27.597 | 38.471 | 26.001 | 2 | 2.4 | 1.2 | 1 | 0.2
3906 | 30/07/2025 11:35:54.852 | 97.632 | 84 | 100 | 70 | 52 | 28.561 | 9.25 | 7.223 | 134.356 | 30.88 | 28.696 | 29.137 | 600.351 | 26.751 | 27.714 | 1269.55 | 27.347 | 27.573 | 38.22 | 29.001 | 1.4 | 3.7 | 0 | 1 | 0.2
3907 | 30/07/2025 11:35:56.486 | 98.136 | 84 | 100 | 70 | 51 | 31.802 | 9.45 | 7.239 | 133.348 | 30.878 | 28.692 | 29.143 | 600.579 | 26.74 | 27.701 | 1276.828 | 27.353 | 27.59 | 38.18 | 31.001 | 3.5 | 2.4 | 0.7 | 1.3 | 0.3
3908 | 30/07/2025 11:35:58.123 | 98.592 | 82 | 100 | 70 | 51 | 28.261 | 8.994 | 7.241 | 133.005 | 30.895 | 28.693 | 29.135 | 600.37 | 26.752 | 27.707 | 1277.176 | 27.313 | 27.606 | 38.624 | 26.001 | 2.9 | 3.8 | 0.6 | 1.3 | 0.2
3909 | 30/07/2025 11:35:59.757 | 98.736 | 84 | 100 | 71 | 52 | 31.096 | 8.92 | 7.238 | 133.223 | 30.892 | 28.676 | 29.152 | 601.875 | 26.737 | 27.562 | 1279.807 | 27.335 | 27.608 | 38.465 | 24.001 | 2.2 | 3.1 | 0.7 | 0 | 0.2
3910 | 30/07/2025 11:36:01.393 | 98.496 | 85 | 100 | 70 | 52 | 32.518 | 8.988 | 7.135 | 132.823 | 30.886 | 28.693 | 29.147 | 602.037 | 26.623 | 27.71 | 1294.441 | 27.359 | 27.595 | 38.486 | 27.001 | 2.4 | 1.8 | 0.6 | 0 | 0.2
3911 | 30/07/2025 11:36:03.028 | 98.16 | 83 | 100 | 70 | 52 | 30.031 | 9.133 | 7.1 | 133.19 | 30.895 | 28.688 | 29.149 | 601.984 | 26.749 | 27.707 | 1296.971 | 27.34 | 27.591 | 38.273 | 27.001 | 2.4 | 1.8 | 0.6 | 0 | 0.2
3912 | 30/07/2025 11:36:04.663 | 97.896 | 84 | 100 | 71 | 52 | 32.383 | 9.18 | 7.088 | 133.052 | 30.875 | 28.691 | 29.135 | 600.584 | 26.725 | 27.711 | 1296.635 | 27.34 | 27.612 | 38.38 | 26.001 | 2.1 | 3.1 | 1.5 | 0 | 0.3
3913 | 30/07/2025 11:36:06.297 | 98.328 | 83 | 100 | 70 | 52 | 31.33 | 9.13 | 7.094 | 132.952 | 30.894 | 28.686 | 29.12 | 600.548 | 26.721 | 27.535 | 1297.406 | 27.309 | 27.61 | 38.507 | 27.001 | 4 | 2.2 | 0.6 | 0 | 0.3
3914 | 30/07/2025 11:36:07.932 | 98.352 | 83 | 100 | 70 | 53 | 28.328 | 9.149 | 7.12 | 133.06 | 30.87 | 28.672 | 29.138 | 600.326 | 26.721 | 27.682 | 1302.23 | 27.366 | 27.612 | 38.327 | 25.001 | 3.8 | 2.4 | 0.7 | 0.7 | 0.3
3915 | 30/07/2025 11:36:09.567 | 98.112 | 85 | 100 | 69 | 51 | 31.574 | 9.136 | 7.137 | 132.912 | 30.884 | 28.695 | 29.13 | 601.426 | 26.729 | 27.678 | 1296.841 | 27.343 | 27.585 | 38.458 | 28.001 | 1.3 | 4.2 | 0.6 | 0.7 | 0.3
3916 | 30/07/2025 11:36:11.203 | 97.68 | 84 | 100 | 70 | 52 | 32.545 | 9.13 | 7.134 | 133.223 | 30.882 | 28.688 | 29.163 | 600.653 | 26.731 | 27.671 | 1286.657 | 27.341 | 27.603 | 38.047 | 28.001 | 1.3 | 4.2 | 0.6 | 0.7 | 0.3
3917 | 30/07/2025 11:36:12.838 | 97.8 | 84 | 100 | 71 | 52 | 30.494 | 9.128 | 7.154 | 133.3 | 30.882 | 28.688 | 29.133 | 600.425 | 26.744 | 27.68 | 1278.407 | 27.328 | 27.61 | 38.548 | 21.001 | 2.9 | 3.9 | 0.6 | 0 | 0.2
3918 | 30/07/2025 11:36:14.473 | 98.568 | 85 | 100 | 70 | 52 | 32.443 | 9.216 | 7.153 | 133.235 | 30.883 | 28.681 | 29.12 | 600.326 | 26.744 | 27.676 | 1282.745 | 27.328 | 27.61 | 38.444 | 25.001 | 2.2 | 1.9 | 1 | 0 | 0.3
3919 | 30/07/2025 11:36:16.108 | 98.304 | 84 | 100 | 70 | 52 | 30.568 | 9.131 | 7.188 | 134.442 | 30.88 | 28.668 | 29.146 | 600.346 | 26.75 | 27.703 | 1277.214 | 27.35 | 27.588 | 38.577 | 26.001 | 1.8 | 3.9 | 1.8 | 0.6 | 0.3
3920 | 30/07/2025 11:36:17.743 | 97.92 | 85 | 100 | 70 | 52 | 28.463 | 9.285 | 7.135 | 134.588 | 30.876 | 28.698 | 29.149 | 600.628 | 26.75 | 27.696 | 1287.123 | 27.34 | 27.594 | 38.204 | 26.001 | 2.9 | 3.5 | 1.5 | 0.6 | 0.3
3921 | 30/07/2025 11:36:19.377 | 97.848 | 84 | 100 | 69 | 52 | 31.95 | 9.208 | 7.135 | 134.503 | 30.857 | 28.693 | 29.139 | 600.54 | 26.755 | 27.708 | 1281.974 | 27.349 | 27.601 | 38.333 | 28.001 | 4.6 | 2.9 | 0 | 0 | 0.2
3922 | 30/07/2025 11:36:21.021 | 97.824 | 83 | 100 | 71 | 53 | 32.473 | 9.122 | 7.136 | 134.57 | 30.862 | 28.681 | 29.115 | 600.39 | 26.75 | 27.564 | 1277.042 | 27.309 | 27.602 | 38.548 | 28.001 | 4.6 | 2.9 | 0 | 0 | 0.2
3923 | 30/07/2025 11:36:22.659 | 97.704 | 83 | 100 | 70 | 54 | 31.092 | 8.992 | 7.134 | 134.706 | 30.849 | 28.665 | 29.12 | 600.456 | 26.736 | 27.704 | 1277.158 | 27.347 | 27.598 | 38.467 | 28.001 | 2.2 | 3.2 | 0.6 | 0 | 0.2
3924 | 30/07/2025 11:36:24.293 | 98.208 | 83 | 100 | 70 | 52 | 32.475 | 9.134 | 7.152 | 133.34 | 30.865 | 28.684 | 29.154 | 600.547 | 26.753 | 27.69 | 1272.987 | 27.353 | 27.581 | 38.549 | 21.001 | 2.1 | 2.7 | 0 | 0.5 | 0.2
3925 | 30/07/2025 11:36:25.927 | 98.064 | 84 | 99 | 70 | 52 | 30.138 | 9.133 | 7.152 | 134.551 | 30.873 | 28.701 | 29.15 | 600.511 | 26.735 | 27.696 | 1269.787 | 27.347 | 27.593 | 38.186 | 29.001 | 3.6 | 4.5 | 0.6 | 0.5 | 0.2
3926 | 30/07/2025 11:36:27.561 | 97.728 | 85 | 100 | 71 | 52 | 28.977 | 9.293 | 7.152 | 134.542 | 30.882 | 28.689 | 29.125 | 600.472 | 26.741 | 27.708 | 1276.945 | 27.343 | 27.613 | 38.488 | 28.001 | 3.9 | 4.2 | 0 | 1.1 | 0.2
3927 | 30/07/2025 11:36:29.198 | 98.088 | 83 | 100 | 71 | 52 | 32.255 | 9.136 | 7.151 | 133.196 | 30.891 | 28.671 | 29.121 | 599.484 | 26.749 | 27.689 | 1285.077 | 27.321 | 27.608 | 38.554 | 28.001 | 3.9 | 4.2 | 0 | 1.1 | 0.2
3928 | 30/07/2025 11:36:30.834 | 98.592 | 84 | 100 | 70 | 51 | 32.183 | 9.289 | 7.184 | 133.043 | 30.895 | 28.682 | 29.151 | 599.251 | 26.742 | 27.594 | 1267.664 | 27.366 | 27.592 | 40.528 | 26.001 | 3 | 4.9 | 1.2 | 1.1 | 0.2
3929 | 30/07/2025 11:36:32.471 | 98.664 | 84 | 100 | 70 | 52 | 31.639 | 9.289 | 7.186 | 133.054 | 30.898 | 28.693 | 29.149 | 599.49 | 26.629 | 27.686 | 1271.587 | 27.344 | 27.581 | 40.365 | 27.001 | 3.1 | 5.6 | 0.6 | 0.5 | 0.2
3930 | 30/07/2025 11:36:34.105 | 99.264 | 86 | 100 | 70 | 52 | 32.509 | 9.266 | 7.187 | 133.216 | 30.887 | 28.703 | 29.135 | 600.386 | 26.737 | 27.696 | 1267.083 | 27.352 | 27.599 | 38.684 | 30.001 | 2.4 | 5.5 | 0.6 | 0.5 | 0.2
3931 | 30/07/2025 11:36:35.740 | 98.76 | 84 | 100 | 71 | 52 | 29.485 | 9.129 | 7.188 | 133.33 | 30.886 | 28.688 | 29.116 | 600.517 | 26.593 | 27.545 | 1267.388 | 27.321 | 27.598 | 38.611 | 24.001 | 3.8 | 2.6 | 0.6 | 0.7 | 0.1
3932 | 30/07/2025 11:36:37.374 | 98.952 | 87 | 100 | 69 | 52 | 29.432 | 9.118 | 7.201 | 133.266 | 30.889 | 28.668 | 29.127 | 600.409 | 26.723 | 27.536 | 1277.207 | 27.342 | 27.599 | 38.612 | 31.001 | 3 | 2 | 0.7 | 0.7 | 0.1
3933 | 30/07/2025 11:36:39.009 | 99.264 | 85 | 100 | 71 | 52 | 32.333 | 8.99 | 7.239 | 132.774 | 30.877 | 28.692 | 29.141 | 600.521 | 26.72 | 27.549 | 1276.741 | 27.353 | 27.592 | 38.685 | 31.001 | 3 | 2 | 0.7 | 0.7 | 0.1
3934 | 30/07/2025 11:36:40.642 | 99.216 | 86 | 100 | 70 | 51 | 28.569 | 8.917 | 7.239 | 133.192 | 30.875 | 28.702 | 29.139 | 600.56 | 26.721 | 27.525 | 1276.977 | 27.364 | 27.585 | 40.007 | 30.001 | 2.9 | 3.2 | 0 | 0.5 | 0.1
3935 | 30/07/2025 11:36:42.276 | 99.024 | 86 | 100 | 71 | 51 | 31.985 | 9.129 | 7.221 | 133.294 | 30.883 | 28.688 | 29.132 | 600.352 | 26.726 | 27.616 | 1279.285 | 27.341 | 27.595 | 38.33 | 26.001 | 3.5 | 2.7 | 2.1 | 0.5 | 0.1
3936 | 30/07/2025 11:36:43.912 | 99.168 | 86 | 100 | 70 | 51 | 32.444 | 9.136 | 7.219 | 133.327 | 30.885 | 28.684 | 29.127 | 600.55 | 26.731 | 27.581 | 1296.479 | 27.315 | 27.613 | 38.336 | 27.001 | 3.6 | 1.7 | 1 | 0.7 | 0.1
3937 | 30/07/2025 11:36:45.547 | 99.048 | 84 | 100 | 70 | 52 | 28.87 | 9.131 | 7.218 | 133.022 | 30.867 | 28.663 | 29.15 | 600.325 | 26.739 | 27.532 | 1296.724 | 27.374 | 27.61 | 38.485 | 24.001 | 2.4 | 3.2 | 0.7 | 0.7 | 0.2
3938 | 30/07/2025 11:36:47.182 | 98.976 | 85 | 100 | 70 | 52 | 29.9 | 9.135 | 7.241 | 132.89 | 30.876 | 28.698 | 29.138 | 600.628 | 26.594 | 27.667 | 1288.226 | 27.353 | 27.592 | 38.331 | 24.001 | 2.4 | 3.2 | 0.7 | 0.7 | 0.2
3939 | 30/07/2025 11:36:48.814 | 99.216 | 85 | 100 | 70 | 52 | 29.885 | 9.135 | 7.239 | 132.823 | 30.87 | 28.706 | 29.123 | 600.4 | 26.729 | 27.55 | 1284.74 | 27.353 | 27.584 | 38.376 | 25.001 | 1.3 | 3.8 | 0.6 | 0 | 0.2
3940 | 30/07/2025 11:36:50.449 | 99.504 | 84 | 100 | 70 | 52 | 28.847 | 9.129 | 7.204 | 133.372 | 30.873 | 28.684 | 29.141 | 600.59 | 26.733 | 27.564 | 1296.58 | 27.326 | 27.608 | 38.348 | 24.001 | 3.7 | 1.9 | 0.7 | 0 | 0.2
3941 | 30/07/2025 11:36:52.084 | 99.648 | 86 | 100 | 70 | 52 | 32.18 | 9.134 | 7.202 | 133.358 | 30.87 | 28.682 | 29.117 | 600.505 | 26.749 | 27.702 | 1297.102 | 27.314 | 27.61 | 38.558 | 24.001 | 2.6 | 3.6 | 0.6 | 0 | 0.2
3942 | 30/07/2025 11:36:53.718 | 99.768 | 87 | 100 | 70 | 53 | 32.165 | 8.932 | 7.186 | 133.087 | 30.847 | 28.667 | 29.147 | 600.293 | 26.74 | 27.567 | 1280.548 | 27.349 | 27.594 | 38.558 | 26.001 | 2.9 | 2.7 | 0.7 | 0 | 0.2
3943 | 30/07/2025 11:36:55.353 | 99.144 | 85 | 100 | 70 | 52 | 28.488 | 9.15 | 7.186 | 133.035 | 30.869 | 28.692 | 29.152 | 600.748 | 26.746 | 27.627 | 1274.431 | 27.347 | 27.586 | 38.363 | 28.001 | 3.7 | 4.1 | 0.6 | 0 | 0.2
3944 | 30/07/2025 11:36:56.988 | 99.672 | 88 | 100 | 70 | 52 | 30.548 | 8.982 | 7.188 | 133.21 | 30.846 | 28.694 | 29.144 | 600.663 | 26.74 | 27.702 | 1267.697 | 27.365 | 27.603 | 38.482 | 28.001 | 3.7 | 4.1 | 0.6 | 0 | 0.2
3945 | 30/07/2025 11:36:58.626 | 99.384 | 86 | 100 | 70 | 52 | 29.385 | 8.991 | 7.184 | 133.421 | 30.866 | 28.689 | 29.136 | 600.636 | 26.744 | 27.693 | 1265.855 | 27.328 | 27.6 | 38.639 | 29.001 | 2.3 | 3.9 | 0.1 | 0 | 0.1
3946 | 30/07/2025 11:37:00.261 | 100.032 | 85 | 100 | 70 | 52 | 29.433 | 9.042 | 7.184 | 133.008 | 30.863 | 28.679 | 29.136 | 600.37 | 26.739 | 27.715 | 1257.647 | 27.348 | 27.614 | 38.469 | 27.001 | 1.9 | 4.2 | 0.9 | 0 | 0.1
3947 | 30/07/2025 11:37:01.897 | 100.224 | 85 | 100 | 70 | 52 | 32.274 | 8.996 | 7.186 | 133.124 | 30.888 | 28.681 | 29.143 | 600.439 | 26.604 | 27.699 | 1265.458 | 27.353 | 27.583 | 38.457 | 27.001 | 1.6 | 3.4 | 0.7 | 0 | 0.1
3948 | 30/07/2025 11:37:03.532 | 99.768 | 85 | 100 | 72 | 52 | 31.751 | 9.134 | 7.203 | 133.083 | 30.886 | 28.694 | 29.14 | 600.584 | 26.59 | 27.692 | 1265.501 | 27.354 | 27.589 | 38.197 | 23.001 | 2.2 | 3 | 0.9 | 0.5 | 0.2
3949 | 30/07/2025 11:37:05.170 | 100.272 | 85 | 100 | 71 | 52 | 28.288 | 9.134 | 7.205 | 133.02 | 30.931 | 28.685 | 29.125 | 600.552 | 26.742 | 27.701 | 1257.912 | 27.331 | 27.614 | 38.604 | 23.001 | 2.2 | 3 | 0.9 | 0.5 | 0.2
3950 | 30/07/2025 11:37:06.806 | 99.888 | 88 | 100 | 70 | 53 | 31.096 | 9.136 | 7.238 | 134.746 | 30.994 | 28.682 | 29.115 | 600.483 | 26.748 | 27.695 | 1265.018 | 27.322 | 27.603 | 38.555 | 23.001 | 3.2 | 1.2 | 1.8 | 0.5 | 0.2
3951 | 30/07/2025 11:37:08.441 | 99.648 | 87 | 100 | 70 | 52 | 28.917 | 8.995 | 7.239 | 134.5 | 31.025 | 28.672 | 29.133 | 600.306 | 26.734 | 27.549 | 1264.547 | 27.34 | 27.593 | 38.574 | 25.001 | 2.2 | 2.2 | 0.6 | 0.5 | 0.2
3952 | 30/07/2025 11:37:10.079 | 100.032 | 86 | 100 | 71 | 52 | 30.041 | 8.984 | 7.239 | 134.59 | 31.04 | 28.696 | 29.156 | 600.594 | 26.74 | 27.572 | 1259.886 | 27.348 | 27.597 | 38.281 | 29.001 | 3.4 | 4.6 | 1.6 | 0.5 | 0.2
3953 | 30/07/2025 11:37:11.714 | 99.456 | 87 | 100 | 69 | 52 | 32.391 | 9.2 | 7.239 | 134.634 | 31.038 | 28.701 | 29.151 | 602.009 | 26.73 | 27.696 | 1249.414 | 27.363 | 27.599 | 38.291 | 34.001 | 3.6 | 4.2 | 1.9 | 0 | 0.2
3954 | 30/07/2025 11:37:13.349 | 99.696 | 85 | 100 | 71 | 51 | 31.362 | 9.13 | 7.24 | 134.777 | 30.934 | 28.684 | 29.114 | 601.901 | 26.696 | 27.542 | 1246.968 | 27.323 | 27.6 | 38.556 | 24.001 | 3 | 4 | 0.6 | 0 | 0.2
3955 | 30/07/2025 11:37:14.990 | 99.336 | 84 | 100 | 71 | 52 | 28.365 | 8.875 | 7.274 | 134.662 | 30.88 | 28.673 | 29.12 | 601.877 | 26.58 | 27.676 | 1241.021 | 27.344 | 27.614 | 38.471 | 24.001 | 3 | 4 | 0.6 | 0 | 0.2
3956 | 30/07/2025 11:37:16.625 | 99.528 | 89 | 100 | 70 | 53 | 32.191 | 8.975 | 7.266 | 134.754 | 30.963 | 28.671 | 29.154 | 601.708 | 26.739 | 27.685 | 1237.397 | 27.356 | 27.594 | 38.514 | 26.001 | 2.1 | 3 | 0.9 | 1 | 0.2
3957 | 30/07/2025 11:37:18.262 | 99.336 | 84 | 100 | 70 | 52 | 28.551 | 8.952 | 7.222 | 134.486 | 31.027 | 28.705 | 29.146 | 602.008 | 26.72 | 27.671 | 1246.626 | 27.359 | 27.585 | 38.287 | 30.001 | 2 | 3.5 | 1.6 | 1 | 0.2
3958 | 30/07/2025 11:37:19.898 | 98.976 | 85 | 100 | 72 | 52 | 30.537 | 9.211 | 7.227 | 134.713 | 30.938 | 28.687 | 29.143 | 601.766 | 26.732 | 27.68 | 1239.441 | 27.337 | 27.594 | 38.274 | 22.001 | 2.8 | 3.9 | 0.8 | 0.6 | 0.1
3959 | 30/07/2025 11:37:21.535 | 99.336 | 87 | 100 | 70 | 52 | 32.467 | 9.212 | 7.238 | 134.603 | 31.015 | 28.681 | 29.122 | 600.69 | 26.591 | 27.623 | 1234.138 | 27.321 | 27.613 | 38.503 | 24.001 | 2.8 | 3.6 | 0.7 | 0.6 | 0.1
3960 | 30/07/2025 11:37:23.173 | 99 | 85 | 100 | 69 | 51 | 30.613 | 9.134 | 7.236 | 134.576 | 30.863 | 28.666 | 29.149 | 600.476 | 26.599 | 27.547 | 1234.83 | 27.362 | 27.609 | 38.532 | 24.001 | 2.8 | 3.6 | 0.7 | 0.6 | 0.1
3961 | 30/07/2025 11:37:24.809 | 99.648 | 84 | 100 | 71 | 52 | 28.459 | 9.285 | 7.222 | 134.358 | 31.009 | 28.684 | 29.134 | 600.539 | 26.602 | 27.698 | 1238.544 | 27.343 | 27.584 | 38.657 | 28.001 | 0.9 | 2.5 | 0.9 | 0 | 0.2
3962 | 30/07/2025 11:37:26.445 | 99.144 | 84 | 100 | 70 | 52 | 31.793 | 9.22 | 7.221 | 134.265 | 31.021 | 28.696 | 29.137 | 602.012 | 26.601 | 27.717 | 1246.818 | 27.357 | 27.577 | 38.611 | 24.001 | 2.2 | 3.3 | 1.3 | 0 | 0.2
3963 | 30/07/2025 11:37:28.081 | 99.264 | 84 | 100 | 70 | 52 | 28.309 | 9.13 | 7.22 | 134.89 | 31.006 | 28.687 | 29.147 | 602.029 | 26.601 | 27.567 | 1247.045 | 27.335 | 27.615 | 38.426 | 28.001 | 2.4 | 3.4 | 0.1 | 0.6 | 0.2
3964 | 30/07/2025 11:37:29.718 | 99.408 | 84 | 100 | 71 | 52 | 31.065 | 9.384 | 7.219 | 134.586 | 31.012 | 28.69 | 29.127 | 602.044 | 26.593 | 27.59 | 1237.891 | 27.321 | 27.628 | 38.72 | 27.001 | 3.6 | 4.2 | 0.9 | 0.6 | 0.2
3965 | 30/07/2025 11:37:31.358 | 99.024 | 86 | 100 | 70 | 52 | 32.469 | 9.136 | 7.239 | 134.65 | 31.004 | 28.674 | 29.148 | 601.782 | 26.597 | 27.669 | 1235.238 | 27.347 | 27.596 | 38.534 | 30.001 | 2.5 | 3.3 | 1.7 | 0.4 | 0.3
3966 | 30/07/2025 11:37:32.992 | 98.832 | 84 | 100 | 69 | 52 | 30.001 | 9.159 | 7.2 | 134.582 | 31.013 | 28.696 | 29.152 | 601.981 | 26.595 | 27.556 | 1242.861 | 27.349 | 27.582 | 38.295 | 30.001 | 2.5 | 3.3 | 1.7 | 0.4 | 0.3
3967 | 30/07/2025 11:37:34.624 | 98.592 | 84 | 100 | 70 | 52 | 32.328 | 9.287 | 7.187 | 134.414 | 31.021 | 28.688 | 29.139 | 601.938 | 26.6 | 27.571 | 1246.801 | 27.337 | 27.579 | 39.827 | 28.001 | 3.8 | 1.7 | 0.8 | 0.4 | 0.2
3968 | 30/07/2025 11:37:36.259 | 97.704 | 83 | 100 | 71 | 52 | 31.21 | 9.127 | 7.186 | 134.68 | 31.033 | 28.689 | 29.139 | 602.088 | 26.591 | 27.685 | 1246.77 | 27.33 | 27.602 | 38.4 | 24.001 | 3.7 | 2.4 | 1.5 | 0 | 0.2
3969 | 30/07/2025 11:37:37.897 | 97.32 | 83 | 100 | 71 | 53 | 28.259 | 9.011 | 7.186 | 134.52 | 31.027 | 28.664 | 29.119 | 602.007 | 26.585 | 27.566 | 1266.644 | 27.334 | 27.599 | 38.695 | 27.001 | 2.4 | 3.7 | 0.3 | 0 | 0.3
3970 | 30/07/2025 11:37:39.534 | 97.44 | 82 | 100 | 70 | 52 | 31.536 | 9.27 | 7.204 | 134.749 | 31.045 | 28.685 | 29.153 | 601.62 | 26.599 | 27.545 | 1263.29 | 27.349 | 27.599 | 38.345 | 24.001 | 2.2 | 3.6 | 0.6 | 0.7 | 0.3
3971 | 30/07/2025 11:37:41.168 | 97.368 | 83 | 100 | 70 | 52 | 32.591 | 9.167 | 7.219 | 134.419 | 31.034 | 28.701 | 29.138 | 602.028 | 26.579 | 27.54 | 1263.957 | 27.36 | 27.581 | 40.21 | 24.001 | 2.2 | 3.6 | 0.6 | 0.7 | 0.3
3972 | 30/07/2025 11:37:42.804 | 97.152 | 83 | 100 | 70 | 53 | 29.549 | 8.983 | 7.24 | 134.511 | 31.025 | 28.683 | 29.139 | 603.066 | 26.589 | 27.584 | 1258.047 | 27.331 | 27.606 | 38.413 | 28.001 | 2.5 | 3 | 0.7 | 0.7 | 0.3
3973 | 30/07/2025 11:37:44.439 | 97.2 | 83 | 100 | 70 | 53 | 32.43 | 9.204 | 7.221 | 134.821 | 31.036 | 28.702 | 29.128 | 603.196 | 26.592 | 27.699 | 1246.105 | 27.331 | 27.617 | 38.616 | 26.001 | 1.8 | 3 | 0.3 | 0.6 | 0.2
3974 | 30/07/2025 11:37:46.074 | 97.032 | 84 | 100 | 70 | 51 | 30.797 | 9.134 | 7.221 | 134.649 | 31.032 | 28.674 | 29.131 | 603.028 | 26.59 | 27.558 | 1247.018 | 27.346 | 27.602 | 38.509 | 29.001 | 2.1 | 2.7 | 1.2 | 0.6 | 0.2
3975 | 30/07/2025 11:37:47.711 | 97.176 | 84 | 100 | 70 | 52 | 28.611 | 8.903 | 7.22 | 134.621 | 31.02 | 28.687 | 29.141 | 602.03 | 26.576 | 27.537 | 1252.802 | 27.346 | 27.597 | 39.408 | 28.001 | 2.5 | 1.9 | 0.6 | 0.5 | 0.2
3976 | 30/07/2025 11:37:49.347 | 97.128 | 83 | 100 | 70 | 52 | 32.064 | 9.009 | 7.199 | 134.366 | 31.033 | 28.696 | 29.132 | 601.93 | 26.588 | 27.545 | 1256.866 | 27.355 | 27.572 | 40.011 | 26.001 | 2 | 3.4 | 0.9 | 0.5 | 0.3
3977 | 30/07/2025 11:37:50.982 | 97.128 | 82 | 100 | 71 | 52 | 32.51 | 8.994 | 7.188 | 134.736 | 31.042 | 28.685 | 29.122 | 601.917 | 26.612 | 27.544 | 1249.429 | 27.325 | 27.61 | 40.208 | 26.001 | 2 | 3.4 | 0.9 | 0.5 | 0.3
3978 | 30/07/2025 11:37:52.616 | 97.008 | 84 | 100 | 71 | 52 | 31.209 | 8.988 | 7.187 | 134.481 | 31.03 | 28.679 | 29.111 | 601.944 | 26.589 | 27.643 | 1245.246 | 27.32 | 27.594 | 40.527 | 22.001 | 3.5 | 1.6 | 0.6 | 0.5 | 0.2
3979 | 30/07/2025 11:37:54.252 | 97.008 | 83 | 100 | 71 | 52 | 32.565 | 9.204 | 7.185 | 134.66 | 31.044 | 28.676 | 29.152 | 601.842 | 26.61 | 27.532 | 1239.311 | 27.348 | 27.61 | 40.319 | 24.001 | 3.8 | 2.6 | 0.6 | 0.5 | 0.2
3980 | 30/07/2025 11:37:55.887 | 96.408 | 83 | 100 | 70 | 52 | 30.106 | 9.137 | 7.187 | 134.419 | 31.016 | 28.703 | 29.136 | 601.973 | 26.601 | 27.546 | 1245.909 | 27.369 | 27.59 | 40.25 | 24.001 | 1.9 | 4.2 | 0.1 | 0.5 | 0.2
3981 | 30/07/2025 11:37:57.522 | 96.12 | 82 | 100 | 71 | 52 | 28.846 | 9.281 | 7.188 | 134.704 | 31.021 | 28.693 | 29.127 | 601.865 | 26.609 | 27.562 | 1246.997 | 27.34 | 27.586 | 40.101 | 25.001 | 1.7 | 4.1 | 1.2 | 0.5 | 0.1
3982 | 30/07/2025 11:37:59.155 | 96.696 | 83 | 100 | 70 | 52 | 32.188 | 8.998 | 7.186 | 134.613 | 31.014 | 28.689 | 29.121 | 602.082 | 26.594 | 27.56 | 1252.56 | 27.32 | 27.624 | 40.234 | 25.001 | 1.7 | 4.1 | 1.2 | 0.5 | 0.1
3983 | 30/07/2025 11:38:00.792 | 96.576 | 82 | 100 | 70 | 52 | 28.317 | 9.128 | 7.187 | 134.776 | 31.008 | 28.675 | 29.13 | 601.896 | 26.612 | 27.564 | 1258.65 | 27.317 | 27.597 | 40.385 | 23.001 | 1.9 | 3.9 | 0.6 | 0.1 | 0.1
3984 | 30/07/2025 11:38:02.428 | 97.008 | 82 | 100 | 71 | 52 | 31.549 | 8.924 | 7.184 | 134.542 | 31.004 | 28.678 | 29.142 | 601.973 | 26.604 | 27.56 | 1260.137 | 27.358 | 27.608 | 40.384 | 23.001 | 2.1 | 4.4 | 0.9 | 0.1 | 0.1
3985 | 30/07/2025 11:38:04.063 | 96.624 | 83 | 100 | 71 | 52 | 32.583 | 9.218 | 7.187 | 134.312 | 31.016 | 28.7 | 29.142 | 600.983 | 26.606 | 27.567 | 1238.887 | 27.348 | 27.584 | 40.325 | 26.001 | 2.9 | 2.2 | 0.6 | 0.6 | 0.1
3986 | 30/07/2025 11:38:05.697 | 96.816 | 83 | 100 | 70 | 51 | 29.49 | 9.124 | 7.186 | 134.618 | 31.015 | 28.699 | 29.151 | 600.587 | 26.597 | 27.565 | 1235.139 | 27.337 | 27.604 | 38.439 | 26.001 | 2.6 | 3.5 | 0.6 | 0.6 | 0.1
3987 | 30/07/2025 11:38:07.333 | 96.864 | 82 | 100 | 70 | 51 | 29.377 | 8.983 | 7.186 | 134.673 | 31.012 | 28.692 | 29.12 | 602.013 | 26.585 | 27.557 | 1240.405 | 27.329 | 27.613 | 38.766 | 28.001 | 1.7 | 1.6 | 0.3 | 0.5 | 0.2
3988 | 30/07/2025 11:38:08.969 | 96.624 | 83 | 100 | 70 | 52 | 32.276 | 9.131 | 7.184 | 134.555 | 31.027 | 28.674 | 29.12 | 601.858 | 26.597 | 27.553 | 1244.691 | 27.354 | 27.591 | 38.601 | 28.001 | 1.7 | 1.6 | 0.3 | 0.5 | 0.2
3989 | 30/07/2025 11:38:10.606 | 97.152 | 84 | 100 | 71 | 52 | 28.488 | 9.136 | 7.186 | 134.33 | 31.028 | 28.697 | 29.148 | 601.985 | 26.589 | 27.551 | 1247.155 | 27.362 | 27.598 | 38.454 | 30.001 | 2.4 | 2.9 | 0 | 0.5 | 0.2
3990 | 30/07/2025 11:38:12.242 | 97.104 | 84 | 99 | 70 | 52 | 31.874 | 9.057 | 7.188 | 134.585 | 31.03 | 28.691 | 29.142 | 601.944 | 26.608 | 27.56 | 1247.015 | 27.341 | 27.575 | 38.189 | 26.001 | 3 | 3.8 | 0.6 | 0.9 | 0.2
3991 | 30/07/2025 11:38:13.878 | 97.128 | 85 | 100 | 67 | 52 | 32.428 | 9.132 | 7.197 | 134.679 | 31.043 | 28.693 | 29.139 | 602.016 | 26.591 | 27.538 | 1252.364 | 27.332 | 27.608 | 38.361 | 32.001 | 2.2 | 3.1 | 0.3 | 0.9 | 0.2
3992 | 30/07/2025 11:38:15.514 | 97.248 | 83 | 100 | 70 | 52 | 28.92 | 9.134 | 7.22 | 134.632 | 31.039 | 28.674 | 29.124 | 601.919 | 26.589 | 27.562 | 1247.568 | 27.316 | 27.599 | 38.699 | 28.001 | 2.6 | 3.1 | 0.9 | 0.6 | 0.2
3993 | 30/07/2025 11:38:17.150 | 97.704 | 85 | 100 | 70 | 52 | 29.983 | 9.283 | 7.203 | 134.549 | 31.043 | 28.681 | 29.153 | 601.928 | 26.595 | 27.545 | 1253.69 | 27.351 | 27.603 | 38.69 | 28.001 | 2.6 | 3.1 | 0.9 | 0.6 | 0.2
3994 | 30/07/2025 11:38:18.785 | 97.368 | 86 | 100 | 70 | 52 | 30.159 | 9.14 | 7.205 | 132.892 | 31.034 | 28.69 | 29.137 | 601.882 | 26.593 | 27.554 | 1264.614 | 27.346 | 27.59 | 38.657 | 26.001 | 2.2 | 2.2 | 1.9 | 0.6 | 0.2
3995 | 30/07/2025 11:38:20.421 | 97.104 | 83 | 100 | 71 | 52 | 29.019 | 8.911 | 7.187 | 133.257 | 31.024 | 28.689 | 29.138 | 601.959 | 26.576 | 27.53 | 1271.545 | 27.346 | 27.584 | 38.237 | 26.001 | 2.8 | 3.4 | 0.2 | 1 | 0.2
3996 | 30/07/2025 11:38:22.055 | 97.824 | 84 | 100 | 71 | 53 | 32.249 | 9.203 | 7.187 | 133.394 | 31.025 | 28.695 | 29.129 | 601.889 | 26.584 | 27.55 | 1280.846 | 27.336 | 27.608 | 38.586 | 25.001 | 3.8 | 2.9 | 0.7 | 1 | 0.2
3997 | 30/07/2025 11:38:23.689 | 98.16 | 84 | 100 | 70 | 52 | 32.323 | 8.881 | 7.185 | 133.248 | 31.03 | 28.67 | 29.12 | 601.933 | 26.59 | 27.533 | 1281.818 | 27.332 | 27.593 | 38.559 | 26.001 | 2.5 | 2.9 | 0.7 | 0.9 | 0.2
3998 | 30/07/2025 11:38:25.323 | 98.568 | 84 | 100 | 71 | 52 | 28.541 | 9.132 | 7.186 | 133.201 | 31.029 | 28.689 | 29.152 | 601.843 | 26.583 | 27.515 | 1282.253 | 27.344 | 27.599 | 38.618 | 23.001 | 2 | 3.6 | 0.9 | 0.9 | 0.2
3999 | 30/07/2025 11:38:26.958 | 98.784 | 84 | 100 | 71 | 52 | 30.677 | 9.226 | 7.187 | 132.977 | 31.025 | 28.693 | 29.12 | 601.678 | 26.58 | 27.534 | 1283.709 | 27.357 | 27.568 | 38.378 | 23.001 | 2 | 3.6 | 0.9 | 0.9 | 0.2
4000 | 30/07/2025 11:38:28.596 | 98.376 | 84 | 100 | 70 | 51 | 29.567 | 9.283 | 7.186 | 133.285 | 31.014 | 28.689 | 29.137 | 601.832 | 26.601 | 27.526 | 1285.88 | 27.345 | 27.602 | 38.242 | 27.001 | 1.9 | 2.3 | 1.1 | 0.5 | 0.2
4001 | 30/07/2025 11:38:30.231 | 99.12 | 84 | 100 | 70 | 52 | 29.435 | 9.132 | 7.187 | 133.122 | 31.012 | 28.682 | 29.113 | 601.779 | 26.599 | 27.539 | 1294.213 | 27.311 | 27.595 | 38.742 | 29.001 | 1.3 | 2.8 | 0.8 | 0.5 | 0.2
4002 | 30/07/2025 11:38:31.866 | 98.496 | 84 | 100 | 70 | 53 | 32.327 | 9.218 | 7.184 | 133.013 | 31.03 | 28.668 | 29.157 | 601.945 | 26.605 | 27.549 | 1294.629 | 27.344 | 27.599 | 40.174 | 28.001 | 2.8 | 2.8 | 0.6 | 0.1 | 0.2
4003 | 30/07/2025 11:38:33.501 | 98.616 | 84 | 100 | 71 | 52 | 31.927 | 9.135 | 7.187 | 132.802 | 31.012 | 28.703 | 29.147 | 601.967 | 26.608 | 27.558 | 1295.249 | 27.368 | 27.587 | 40.514 | 23.001 | 3.9 | 2.6 | 1.3 | 0.1 | 0.2
4004 | 30/07/2025 11:38:35.135 | 98.952 | 84 | 100 | 70 | 52 | 28.435 | 8.838 | 7.189 | 133.39 | 31.015 | 28.689 | 29.13 | 601.793 | 26.61 | 27.557 | 1288.864 | 27.342 | 27.567 | 38.362 | 23.001 | 3.9 | 2.6 | 1.3 | 0.1 | 0.2
4005 | 30/07/2025 11:38:36.770 | 98.808 | 86 | 100 | 69 | 52 | 31.149 | 9.198 | 7.186 | 133.205 | 31.023 | 28.691 | 29.133 | 602.15 | 26.594 | 27.56 | 1281.594 | 27.33 | 27.616 | 38.424 | 28.001 | 3.2 | 4.7 | 0.9 | 0.4 | 0.2
4006 | 30/07/2025 11:38:38.411 | 99.504 | 86 | 100 | 70 | 52 | 29.037 | 9.286 | 7.186 | 133.203 | 31.005 | 28.68 | 29.115 | 601.758 | 26.613 | 27.571 | 1277.162 | 27.314 | 27.595 | 38.452 | 28.001 | 2.1 | 3.5 | 1 | 0.4 | 0.2
4007 | 30/07/2025 11:38:40.050 | 99.216 | 85 | 100 | 70 | 53 | 30.025 | 9.131 | 7.185 | 133.236 | 31.005 | 28.681 | 29.141 | 603.14 | 26.59 | 27.558 | 1274.447 | 27.359 | 27.609 | 38.335 | 27.001 | 2.4 | 4 | 0.6 | 0 | 0.2
4008 | 30/07/2025 11:38:41.687 | 99.288 | 86 | 100 | 70 | 52 | 32.417 | 8.993 | 7.187 | 132.931 | 31.019 | 28.689 | 29.14 | 601.786 | 26.6 | 27.568 | 1276.917 | 27.348 | 27.582 | 38.441 | 30.001 | 2.1 | 3.2 | 0.3 | 0 | 0.2
4009 | 30/07/2025 11:38:43.322 | 99.072 | 85 | 100 | 71 | 52 | 31.208 | 9.182 | 7.172 | 133.283 | 31.037 | 28.687 | 29.146 | 601.918 | 26.598 | 27.542 | 1274.424 | 27.34 | 27.594 | 38.307 | 30.001 | 4.1 | 3 | 0 | 0.5 | 0.2
4010 | 30/07/2025 11:38:44.956 | 98.664 | 84 | 100 | 69 | 52 | 28.273 | 9.125 | 7.15 | 133.055 | 31.054 | 28.697 | 29.124 | 603.185 | 26.592 | 27.57 | 1272.135 | 27.323 | 27.616 | 38.554 | 30.001 | 4.1 | 3 | 0 | 0.5 | 0.2
4011 | 30/07/2025 11:38:46.591 | 98.64 | 86 | 100 | 71 | 52 | 32.227 | 8.986 | 7.14 | 133.16 | 31.032 | 28.675 | 29.129 | 603.213 | 26.594 | 27.551 | 1265.282 | 27.334 | 27.61 | 38.497 | 24.001 | 2.4 | 6.1 | 0.6 | 0.5 | 0.2
4012 | 30/07/2025 11:38:48.225 | 98.424 | 84 | 100 | 70 | 51 | 28.58 | 8.986 | 7.135 | 134.4 | 31.02 | 28.694 | 29.136 | 602.756 | 26.589 | 27.563 | 1257.276 | 27.369 | 27.599 | 38.437 | 31.001 | 2.1 | 4.3 | 0.6 | 0 | 0.1
4013 | 30/07/2025 11:38:49.858 | 98.376 | 85 | 100 | 69 | 52 | 30.503 | 9.133 | 7.136 | 134.478 | 31.045 | 28.693 | 29.145 | 603.038 | 26.608 | 27.56 | 1257.106 | 27.34 | 27.577 | 38.289 | 25.001 | 2.1 | 3.6 | 0.7 | 0 | 0.1
4014 | 30/07/2025 11:38:51.491 | 98.04 | 84 | 100 | 70 | 52 | 32.48 | 8.856 | 7.135 | 134.905 | 31.03 | 28.682 | 29.143 | 603.154 | 26.586 | 27.549 | 1250.02 | 27.329 | 27.62 | 38.409 | 26.001 | 3 | 2.6 | 0.6 | 1.1 | 0.3
4015 | 30/07/2025 11:38:53.124 | 97.992 | 84 | 100 | 70 | 51 | 30.729 | 8.985 | 7.134 | 134.616 | 31.025 | 28.679 | 29.112 | 603.133 | 26.577 | 27.557 | 1254.753 | 27.31 | 27.595 | 38.796 | 26.001 | 3 | 2.6 | 0.6 | 1.1 | 0.3
4016 | 30/07/2025 11:38:54.757 | 98.04 | 84 | 100 | 70 | 51 | 28.562 | 9.13 | 7.142 | 134.604 | 31.043 | 28.68 | 29.158 | 603.189 | 26.581 | 27.542 | 1257.63 | 27.347 | 27.603 | 38.578 | 21.001 | 2.9 | 1.1 | 0.6 | 1.1 | 0.3
4017 | 30/07/2025 11:38:56.388 | 97.896 | 84 | 100 | 70 | 52 | 31.895 | 8.985 | 7.154 | 134.21 | 31.022 | 28.694 | 29.14 | 602.965 | 26.587 | 27.543 | 1257.425 | 27.355 | 27.59 | 38.538 | 22.001 | 2.1 | 3.2 | 0.6 | 1.2 | 0.2
4018 | 30/07/2025 11:38:58.022 | 97.896 | 84 | 100 | 71 | 52 | 28.304 | 9.035 | 7.171 | 134.587 | 31.035 | 28.69 | 29.162 | 605.518 | 26.581 | 27.52 | 1266.616 | 27.35 | 27.582 | 38.21 | 29.001 | 2.7 | 1.1 | 0.1 | 1.2 | 0.3
4019 | 30/07/2025 11:38:59.660 | 97.92 | 82 | 100 | 69 | 52 | 31.167 | 9.213 | 7.186 | 134.499 | 31.023 | 28.703 | 29.118 | 606.788 | 26.563 | 27.529 | 1264.714 | 27.332 | 27.595 | 38.398 | 23.001 | 2.4 | 2.2 | 0 | 0.8 | 0.3
4020 | 30/07/2025 11:39:01.294 | 97.896 | 84 | 100 | 71 | 52 | 32.527 | 9.268 | 7.186 | 134.771 | 31.026 | 28.671 | 29.144 | 606.839 | 26.599 | 27.54 | 1257.536 | 27.33 | 27.611 | 38.379 | 23.001 | 2.4 | 2.2 | 0 | 0.8 | 0.3
4021 | 30/07/2025 11:39:02.931 | 97.248 | 83 | 100 | 71 | 52 | 30.062 | 9.135 | 7.203 | 134.629 | 31.015 | 28.688 | 29.14 | 608.004 | 26.596 | 27.522 | 1267.388 | 27.363 | 27.606 | 38.446 | 28.001 | 2.1 | 4.3 | 0.6 | 0.8 | 0.2
4022 | 30/07/2025 11:39:04.563 | 97.392 | 84 | 100 | 70 | 52 | 32.355 | 9.132 | 7.221 | 134.541 | 31.033 | 28.688 | 29.151 | 607.902 | 26.612 | 27.55 | 1267.337 | 27.338 | 27.595 | 38.322 | 24.001 | 1.1 | 3.1 | 0 | 0 | 0.3
4023 | 30/07/2025 11:39:06.207 | 96.936 | 83 | 100 | 70 | 52 | 31.376 | 9.212 | 7.204 | 134.668 | 31.022 | 28.69 | 29.14 | 607.903 | 26.594 | 27.541 | 1267.49 | 27.354 | 27.598 | 38.319 | 24.001 | 1.4 | 3.4 | 0 | 0 | 0.3
4024 | 30/07/2025 11:39:07.842 | 96.96 | 83 | 100 | 71 | 51 | 28.364 | 9.193 | 7.205 | 134.725 | 31.014 | 28.687 | 29.12 | 608.072 | 26.612 | 27.558 | 1270.032 | 27.315 | 27.601 | 38.622 | 25.001 | 2.7 | 2.9 | 0 | 0.8 | 0.2
4025 | 30/07/2025 11:39:09.475 | 97.2 | 83 | 100 | 70 | 53 | 31.681 | 9.131 | 7.2 | 134.762 | 31.015 | 28.662 | 29.143 | 608.126 | 26.594 | 27.55 | 1274.535 | 27.348 | 27.609 | 38.444 | 28.001 | 1.9 | 1.9 | 0.6 | 0.8 | 0.2
4026 | 30/07/2025 11:39:11.109 | 96.888 | 84 | 100 | 70 | 52 | 32.604 | 8.919 | 7.204 | 134.491 | 30.998 | 28.705 | 29.143 | 607.939 | 26.597 | 27.585 | 1275.896 | 27.364 | 27.597 | 40.17 | 28.001 | 1.9 | 1.9 | 0.6 | 0.8 | 0.2
4027 | 30/07/2025 11:39:12.744 | 96.216 | 82 | 99 | 70 | 52 | 30.599 | 8.988 | 7.204 | 134.648 | 31.011 | 28.695 | 29.162 | 608.085 | 26.59 | 27.565 | 1276.738 | 27.353 | 27.599 | 40.121 | 28.001 | 2 | 3.2 | 0.9 | 0.9 | 0.2
4028 | 30/07/2025 11:39:14.380 | 96.36 | 82 | 100 | 70 | 51 | 32.511 | 9.165 | 7.204 | 134.554 | 31.009 | 28.694 | 29.116 | 608.009 | 26.593 | 27.574 | 1276.971 | 27.335 | 27.606 | 40.293 | 29.001 | 2 | 4.1 | 0.9 | 0.9 | 0.2
4029 | 30/07/2025 11:39:16.014 | 96.168 | 82 | 100 | 70 | 51 | 30.725 | 9.311 | 7.203 | 134.551 | 31.02 | 28.677 | 29.116 | 608.18 | 26.601 | 27.545 | 1273.05 | 27.307 | 27.594 | 40.583 | 25.001 | 3.7 | 4.1 | 0.4 | 0 | 0.2
4030 | 30/07/2025 11:39:17.650 | 96.408 | 82 | 100 | 70 | 51 | 28.553 | 9.199 | 7.202 | 134.611 | 31.024 | 28.676 | 29.139 | 608.066 | 26.597 | 27.553 | 1275.436 | 27.367 | 27.603 | 40.309 | 26.001 | 2.7 | 2.8 | 0.9 | 0 | 0.2
4031 | 30/07/2025 11:39:19.285 | 96.912 | 83 | 100 | 70 | 51 | 31.951 | 9.073 | 7.206 | 134.304 | 31.037 | 28.693 | 29.135 | 609.168 | 26.587 | 27.559 | 1274.317 | 27.349 | 27.578 | 40.352 | 26.001 | 2.7 | 2.8 | 0.9 | 0 | 0.2
4032 | 30/07/2025 11:39:20.919 | 97.248 | 84 | 100 | 70 | 52 | 32.511 | 8.985 | 7.203 | 134.95 | 31.048 | 28.69 | 29.154 | 609.211 | 26.58 | 27.542 | 1266.968 | 27.34 | 27.589 | 40.073 | 28.001 | 1.7 | 4 | 0.2 | 0.6 | 0.2
4033 | 30/07/2025 11:39:22.553 | 97.2 | 84 | 100 | 70 | 52 | 31.017 | 8.912 | 7.16 | 134.658 | 31.039 | 28.689 | 29.136 | 608.046 | 26.608 | 27.561 | 1266.111 | 27.333 | 27.619 | 40.331 | 29.001 | 2.2 | 3.3 | 0 | 0.6 | 0.3
4034 | 30/07/2025 11:39:24.420 | 97.104 | 82 | 100 | 70 | 52 | 32.601 | 9.132 | 7.15 | 134.588 | 31.038 | 28.669 | 29.136 | 608.114 | 26.583 | 27.551 | 1283.337 | 27.323 | 27.612 | 40.389 | 26.001 | 3.2 | 3.9 | 0.6 | 0.5 | 0.3
4035 | 30/07/2025 11:39:26.054 | 97.248 | 83 | 100 | 70 | 52 | 30.215 | 8.987 | 7.186 | 134.417 | 31.029 | 28.683 | 29.166 | 608.004 | 26.582 | 27.564 | 1285.014 | 27.354 | 27.604 | 40.356 | 29.001 | 2.9 | 1.7 | 0 | 0.5 | 0.3
4036 | 30/07/2025 11:39:27.688 | 97.632 | 83 | 100 | 70 | 52 | 28.903 | 9.249 | 7.186 | 132.99 | 31.051 | 28.692 | 29.145 | 608.038 | 26.605 | 27.556 | 1287.089 | 27.337 | 27.581 | 40.076 | 26.001 | 2.8 | 2.9 | 0.7 | 0 | 0.3
4037 | 30/07/2025 11:39:29.323 | 97.68 | 84 | 100 | 70 | 52 | 32.206 | 9.133 | 7.186 | 133.265 | 31.021 | 28.694 | 29.141 | 607.977 | 26.582 | 27.536 | 1290.758 | 27.347 | 27.616 | 40.106 | 21.001 | 3.1 | 3.2 | 0.9 | 0 | 0.2
4038 | 30/07/2025 11:39:30.957 | 98.088 | 84 | 100 | 70 | 51 | 32.293 | 9.204 | 7.187 | 133.16 | 31.031 | 28.678 | 29.113 | 609.261 | 26.578 | 27.547 | 1287.087 | 27.308 | 27.594 | 40.398 | 21.001 | 3.1 | 3.2 | 0.9 | 0 | 0.2
4039 | 30/07/2025 11:39:32.591 | 98.232 | 84 | 100 | 70 | 52 | 31.609 | 9.13 | 7.185 | 133.081 | 31.027 | 28.683 | 29.131 | 609.214 | 26.578 | 27.545 | 1289.562 | 27.352 | 27.601 | 40.137 | 26.001 | 3.4 | 3.6 | 0.7 | 1.1 | 0.2
4040 | 30/07/2025 11:39:34.225 | 98.856 | 83 | 100 | 70 | 52 | 32.569 | 9.284 | 7.189 | 132.92 | 31.023 | 28.689 | 29.144 | 609.123 | 26.583 | 27.525 | 1302.978 | 27.346 | 27.592 | 40.446 | 30.001 | 2.3 | 2.8 | 0.6 | 1.1 | 0.2
4041 | 30/07/2025 11:39:35.859 | 98.352 | 86 | 100 | 70 | 54 | 29.458 | 9.137 | 7.186 | 133.126 | 31.024 | 28.695 | 29.147 | 609.183 | 26.579 | 27.516 | 1298.477 | 27.351 | 27.591 | 40.109 | 26.001 | 2.8 | 3.1 | 0.9 | 0.5 | 0.2
4042 | 30/07/2025 11:39:37.493 | 97.92 | 84 | 100 | 70 | 52 | 29.406 | 9.211 | 7.187 | 133.11 | 31.027 | 28.683 | 29.137 | 609.277 | 26.6 | 27.562 | 1296.87 | 27.334 | 27.617 | 40.278 | 25.001 | 1.9 | 1.9 | 0 | 0.5 | 0.2
4043 | 30/07/2025 11:39:39.128 | 98.616 | 84 | 100 | 70 | 53 | 32.318 | 8.974 | 7.185 | 133.422 | 31.033 | 28.675 | 29.128 | 609.321 | 26.614 | 27.553 | 1293.14 | 27.329 | 27.599 | 40.244 | 25.001 | 1.9 | 1.9 | 0 | 0.5 | 0.2
4044 | 30/07/2025 11:39:40.763 | 98.376 | 83 | 100 | 70 | 52 | 31.924 | 9.134 | 7.201 | 133.071 | 31.004 | 28.678 | 29.131 | 610.577 | 26.59 | 27.555 | 1297.103 | 27.363 | 27.606 | 40.287 | 25.001 | 4 | 2.8 | 0.6 | 0 | 0.2
4045 | 30/07/2025 11:39:42.397 | 98.688 | 84 | 100 | 70 | 52 | 31.989 | 9.133 | 7.221 | 133.054 | 31.03 | 28.696 | 29.164 | 610.425 | 26.593 | 27.558 | 1294.83 | 27.353 | 27.59 | 40.203 | 22.001 | 2.7 | 3.2 | 0.6 | 0 | 0.2
4046 | 30/07/2025 11:39:44.030 | 97.848 | 83 | 100 | 71 | 52 | 32.572 | 8.903 | 7.221 | 133.174 | 31.011 | 28.695 | 29.135 | 610.435 | 26.591 | 27.555 | 1294.844 | 27.361 | 27.596 | 40.107 | 29.001 | 2.6 | 2.6 | 0.9 | 0 | 0.3
4047 | 30/07/2025 11:39:45.665 | 97.992 | 84 | 99 | 71 | 52 | 29.062 | 8.911 | 7.222 | 133.192 | 31.004 | 28.689 | 29.131 | 610.538 | 26.596 | 27.576 | 1296.884 | 27.316 | 27.607 | 40.385 | 26.001 | 3 | 2.3 | 0.1 | 0 | 0.3
4048 | 30/07/2025 11:39:47.300 | 97.824 | 83 | 100 | 70 | 52 | 30.025 | 8.984 | 7.185 | 133.232 | 31.012 | 28.663 | 29.146 | 611.833 | 26.594 | 27.556 | 1297.299 | 27.334 | 27.603 | 38.42 | 26.001 | 3 | 2.3 | 0.1 | 0 | 0.3
4049 | 30/07/2025 11:39:48.935 | 98.088 | 84 | 100 | 71 | 52 | 32.39 | 9.136 | 7.164 | 134.16 | 31.011 | 28.69 | 29.142 | 612.965 | 26.595 | 27.579 | 1293.015 | 27.362 | 27.602 | 38.376 | 26.001 | 2.7 | 3.4 | 0.6 | 0 | 0.3
4050 | 30/07/2025 11:39:50.571 | 97.944 | 83 | 100 | 70 | 52 | 28.906 | 8.989 | 7.151 | 134.461 | 31.023 | 28.696 | 29.147 | 612.949 | 26.588 | 27.554 | 1293.34 | 27.356 | 27.59 | 38.283 | 22.001 | 2.9 | 2.5 | 0.6 | 0 | 0.2
4051 | 30/07/2025 11:39:52.207 | 97.512 | 84 | 100 | 70 | 52 | 32.188 | 8.986 | 7.152 | 134.469 | 31.032 | 28.681 | 29.117 | 612.836 | 26.585 | 27.574 | 1295.281 | 27.355 | 27.597 | 38.237 | 29.001 | 2.3 | 2.3 | 1 | 0.1 | 0.2
4052 | 30/07/2025 11:39:53.844 | 97.608 | 83 | 100 | 71 | 53 | 32.275 | 8.976 | 7.152 | 134.705 | 31.038 | 28.685 | 29.115 | 613.096 | 26.594 | 27.549 | 1287.199 | 27.314 | 27.611 | 38.392 | 27.001 | 3 | 4 | 1.1 | 0.1 | 0.2
4053 | 30/07/2025 11:39:55.479 | 98.064 | 83 | 100 | 70 | 52 | 28.681 | 8.951 | 7.133 | 133.224 | 31.043 | 28.663 | 29.147 | 612.862 | 26.589 | 27.546 | 1272.094 | 27.35 | 27.6 | 39.091 | 24.001 | 2.6 | 3.6 | 0.7 | 0.6 | 0.2
4054 | 30/07/2025 11:39:57.113 | 97.632 | 83 | 100 | 70 | 52 | 30.463 | 9.133 | 7.137 | 132.829 | 31.037 | 28.7 | 29.135 | 612.797 | 26.593 | 27.552 | 1272.001 | 27.35 | 27.578 | 40.146 | 24.001 | 2.6 | 3.6 | 0.7 | 0.6 | 0.2
4055 | 30/07/2025 11:39:58.748 | 97.608 | 84 | 99 | 71 | 52 | 32.516 | 9.133 | 7.133 | 133.35 | 31.043 | 28.688 | 29.15 | 612.974 | 26.585 | 27.531 | 1281.176 | 27.35 | 27.592 | 40.011 | 19 | 2.4 | 2.5 | 0.6 | 0.6 | 0.2
4056 | 30/07/2025 11:40:00.379 | 97.008 | 84 | 100 | 70 | 52 | 29.447 | 9.335 | 7.137 | 133.349 | 31.031 | 28.687 | 29.122 | 612.719 | 26.584 | 27.551 | 1281.964 | 27.33 | 27.601 | 40.261 | 24.001 | 2.4 | 1.8 | 0.3 | 0.5 | 0.2
4057 | 30/07/2025 11:40:02.013 | 97.824 | 84 | 100 | 69 | 52 | 32.333 | 9.156 | 7.133 | 133.131 | 31.033 | 28.68 | 29.117 | 613.135 | 26.582 | 27.534 | 1277.913 | 27.328 | 27.612 | 40.209 | 23.001 | 1.8 | 2.3 | 0.9 | 0.5 | 0.3
4058 | 30/07/2025 11:40:03.650 | 97.944 | 84 | 100 | 70 | 53 | 31.867 | 9.213 | 7.151 | 133.084 | 31.033 | 28.678 | 29.137 | 612.82 | 26.584 | 27.551 | 1279.112 | 27.348 | 27.601 | 40.44 | 25.001 | 1.8 | 4 | 0.4 | 0.5 | 0.2
4059 | 30/07/2025 11:40:05.291 | 98.664 | 85 | 100 | 70 | 51 | 28.339 | 9.282 | 7.151 | 132.942 | 31.029 | 28.691 | 29.142 | 613.057 | 26.592 | 27.533 | 1285.088 | 27.345 | 27.581 | 40.279 | 25.001 | 1.8 | 4 | 0.4 | 0.5 | 0.2
4060 | 30/07/2025 11:40:06.934 | 98.496 | 87 | 100 | 70 | 53 | 31.087 | 9.134 | 7.152 | 133.283 | 31.022 | 28.692 | 29.137 | 612.918 | 26.573 | 27.531 | 1274.938 | 27.359 | 27.613 | 40.233 | 24.001 | 2.2 | 3.2 | 0.7 | 0.5 | 0.3
4061 | 30/07/2025 11:40:08.570 | 98.352 | 86 | 100 | 70 | 52 | 28.92 | 9.126 | 7.152 | 133.183 | 31.025 | 28.688 | 29.136 | 612.965 | 26.588 | 27.534 | 1271.892 | 27.324 | 27.619 | 40.293 | 24.001 | 1.4 | 2.3 | 1.5 | 0.5 | 0.3
4062 | 30/07/2025 11:40:10.204 | 98.352 | 84 | 100 | 70 | 52 | 29.918 | 9.284 | 7.184 | 133.207 | 31.008 | 28.669 | 29.127 | 613.028 | 26.597 | 27.535 | 1269.507 | 27.349 | 27.606 | 40.274 | 27.001 | 4.1 | 2.8 | 1.5 | 0.5 | 0.3
4063 | 30/07/2025 11:40:11.837 | 98.376 | 84 | 99 | 70 | 52 | 32.366 | 9.152 | 7.188 | 133.149 | 31.03 | 28.686 | 29.146 | 612.946 | 26.601 | 27.539 | 1279.311 | 27.358 | 27.585 | 40.191 | 24.001 | 1.3 | 3 | 0.9 | 0.5 | 0.3
4064 | 30/07/2025 11:40:13.472 | 98.664 | 84 | 100 | 70 | 52 | 31.331 | 9.289 | 7.186 | 133.117 | 31.022 | 28.693 | 29.145 | 613.081 | 26.598 | 27.544 | 1287.087 | 27.349 | 27.582 | 39.896 | 21.001 | 2.3 | 4.2 | 1.2 | 0.5 | 0.3
4065 | 30/07/2025 11:40:15.106 | 98.832 | 84 | 100 | 70 | 52 | 28.339 | 9.13 | 7.186 | 133.264 | 31.019 | 28.686 | 29.13 | 612.782 | 26.601 | 27.565 | 1287.102 | 27.336 | 27.595 | 40.302 | 21.001 | 2.3 | 4.2 | 1.2 | 0.5 | 0.3
4066 | 30/07/2025 11:40:16.741 | 99 | 85 | 100 | 70 | 52 | 31.586 | 9.263 | 7.185 | 133.266 | 31.01 | 28.679 | 29.135 | 613.007 | 26.6 | 27.559 | 1288.855 | 27.317 | 27.609 | 40.224 | 23.001 | 1.5 | 2.5 | 0.6 | 1.1 | 0.2
4067 | 30/07/2025 11:40:18.375 | 99.072 | 85 | 100 | 70 | 52 | 28.592 | 9.178 | 7.185 | 132.961 | 31.011 | 28.669 | 29.136 | 612.855 | 26.601 | 27.568 | 1287.109 | 27.342 | 27.594 | 40.344 | 25.001 | 1.5 | 4.2 | 0.7 | 1.1 | 0.2
4068 | 30/07/2025 11:40:20.008 | 98.832 | 84 | 100 | 71 | 52 | 30.56 | 9.133 | 7.187 | 133.058 | 31.014 | 28.691 | 29.151 | 614.292 | 26.596 | 27.552 | 1287.233 | 27.35 | 27.594 | 40.2 | 28.001 | 2.2 | 2.4 | 2.2 | 0.8 | 0.3
4069 | 30/07/2025 11:40:21.642 | 98.88 | 84 | 100 | 71 | 52 | 32.518 | 9.139 | 7.186 | 133.046 | 31.001 | 28.698 | 29.137 | 614.175 | 26.59 | 27.569 | 1285.022 | 27.363 | 27.598 | 40.108 | 28.001 | 2.8 | 3.6 | 0.8 | 0.8 | 0.3
4070 | 30/07/2025 11:40:23.277 | 98.088 | 83 | 100 | 70 | 52 | 30.738 | 9.134 | 7.188 | 133.163 | 31.022 | 28.69 | 29.13 | 614.069 | 26.597 | 27.562 | 1287.251 | 27.321 | 27.608 | 40.325 | 28.001 | 2.8 | 3.6 | 0.8 | 0.8 | 0.3
4071 | 30/07/2025 11:40:24.912 | 98.064 | 86 | 100 | 70 | 52 | 28.508 | 9.132 | 7.211 | 133.241 | 31.037 | 28.677 | 29.132 | 614.199 | 26.579 | 27.542 | 1278.28 | 27.338 | 27.596 | 40.241 | 24.001 | 2.3 | 2.8 | 0.9 | 0.6 | 0.2
4072 | 30/07/2025 11:40:26.545 | 97.584 | 82 | 100 | 71 | 52 | 31.913 | 9.133 | 7.219 | 133.212 | 31.039 | 28.665 | 29.139 | 614.27 | 26.61 | 27.561 | 1276.164 | 27.34 | 27.604 | 40.14 | 23.001 | 2.5 | 4.5 | 0.7 | 0.6 | 0.3
4073 | 30/07/2025 11:40:28.184 | 97.08 | 84 | 100 | 70 | 52 | 28.413 | 8.866 | 7.237 | 132.976 | 31.038 | 28.697 | 29.143 | 614.164 | 26.594 | 27.549 | 1268.488 | 27.357 | 27.602 | 40.28 | 25.001 | 1.5 | 1.9 | 0.6 | 0.5 | 0.3
4074 | 30/07/2025 11:40:29.819 | 97.128 | 84 | 100 | 70 | 52 | 31.181 | 9.133 | 7.224 | 133.196 | 31.035 | 28.685 | 29.12 | 614.05 | 26.588 | 27.549 | 1269.485 | 27.336 | 27.584 | 40.169 | 25.001 | 2.7 | 2.2 | 1 | 0.5 | 0.3
4075 | 30/07/2025 11:40:31.453 | 97.56 | 84 | 100 | 70 | 53 | 32.584 | 9.149 | 7.186 | 133.213 | 31.045 | 28.68 | 29.127 | 614.045 | 26.587 | 27.554 | 1266.903 | 27.313 | 27.611 | 40.244 | 28.001 | 3.5 | 1.7 | 2.1 | 1.2 | 0.3
4076 | 30/07/2025 11:40:33.087 | 96.888 | 83 | 100 | 70 | 52 | 30.328 | 9.29 | 7.185 | 133.159 | 31.023 | 28.665 | 29.148 | 614.216 | 26.582 | 27.553 | 1273.661 | 27.369 | 27.604 | 40.205 | 28.001 | 3.5 | 1.7 | 2.1 | 1.2 | 0.3
4077 | 30/07/2025 11:40:34.721 | 97.248 | 84 | 100 | 70 | 52 | 32.406 | 9.216 | 7.185 | 133.134 | 31.023 | 28.683 | 29.158 | 614.241 | 26.583 | 27.543 | 1274.728 | 27.355 | 27.596 | 40.171 | 28.001 | 1.7 | 3.7 | 1.1 | 1.2 | 0.3
4078 | 30/07/2025 11:40:36.355 | 98.088 | 84 | 100 | 70 | 52 | 31.458 | 9.137 | 7.152 | 132.99 | 31.036 | 28.699 | 29.141 | 614.119 | 26.576 | 27.54 | 1266.766 | 27.364 | 27.59 | 38.308 | 23.001 | 2 | 2.4 | 0.6 | 0.5 | 0.3
4079 | 30/07/2025 11:40:37.988 | 98.4 | 84 | 100 | 72 | 52 | 28.357 | 9.233 | 7.153 | 133.175 | 31.02 | 28.683 | 29.135 | 614.03 | 26.59 | 27.553 | 1267.042 | 27.332 | 27.608 | 38.356 | 27.001 | 2.7 | 2.6 | 0.9 | 0.5 | 0.3
4080 | 30/07/2025 11:40:39.622 | 98.592 | 85 | 100 | 70 | 52 | 31.646 | 8.986 | 7.15 | 133.06 | 31.035 | 28.684 | 29.121 | 614.134 | 26.578 | 27.53 | 1265.221 | 27.327 | 27.61 | 38.551 | 30.001 | 1.8 | 2.8 | 0 | 1.1 | 0.2
4081 | 30/07/2025 11:40:41.257 | 97.824 | 84 | 100 | 70 | 52 | 32.628 | 9.29 | 7.172 | 133.054 | 31.016 | 28.673 | 29.141 | 614.249 | 26.584 | 27.547 | 1269.523 | 27.359 | 27.601 | 40.245 | 30.001 | 1.8 | 2.8 | 0 | 1.1 | 0.2
4082 | 30/07/2025 11:40:42.891 | 98.688 | 85 | 100 | 71 | 53 | 29.466 | 9.215 | 7.177 | 133.04 | 31.024 | 28.687 | 29.149 | 614.249 | 26.593 | 27.537 | 1272.078 | 27.343 | 27.589 | 40.123 | 26.001 | 3.2 | 3.2 | 0 | 1.1 | 0.3
4083 | 30/07/2025 11:40:44.525 | 98.688 | 84 | 100 | 70 | 52 | 32.461 | 9.214 | 7.154 | 133.124 | 31.022 | 28.686 | 29.135 | 614.091 | 26.601 | 27.545 | 1269.001 | 27.344 | 27.58 | 38.243 | 25.001 | 3.7 | 2.9 | 0 | 0.5 | 0.2
4084 | 30/07/2025 11:40:46.159 | 97.896 | 84 | 99 | 70 | 52 | 30.787 | 8.987 | 7.151 | 133.229 | 31.032 | 28.687 | 29.131 | 613.06 | 26.592 | 27.531 | 1274.103 | 27.327 | 27.618 | 40.099 | 28.001 | 2.3 | 5.7 | 0.6 | 0.5 | 0.2
4085 | 30/07/2025 11:40:47.795 | 98.376 | 84 | 100 | 70 | 52 | 28.517 | 9.081 | 7.15 | 133.019 | 31.014 | 28.668 | 29.131 | 612.953 | 26.588 | 27.558 | 1286.231 | 27.334 | 27.609 | 40.345 | 27.001 | 1.7 | 4.7 | 0.9 | 1.3 | 0.2
4086 | 30/07/2025 11:40:49.431 | 98.688 | 86 | 100 | 71 | 52 | 31.95 | 9.209 | 7.152 | 133.073 | 31.015 | 28.677 | 29.141 | 612.963 | 26.629 | 27.568 | 1287.295 | 27.347 | 27.59 | 40.276 | 26.001 | 4.6 | 3.3 | 0.6 | 1.3 | 0.2
4087 | 30/07/2025 11:40:51.065 | 98.976 | 84 | 100 | 70 | 51 | 32.526 | 8.988 | 7.151 | 132.838 | 30.989 | 28.693 | 29.137 | 612.887 | 26.601 | 27.553 | 1282.589 | 27.348 | 27.589 | 38.314 | 26.001 | 4.6 | 3.3 | 0.6 | 1.3 | 0.2
4088 | 30/07/2025 11:40:52.698 | 99.12 | 85 | 100 | 70 | 52 | 28.905 | 9.136 | 7.152 | 133.293 | 30.999 | 28.694 | 29.13 | 612.798 | 26.587 | 27.556 | 1272.008 | 27.33 | 27.599 | 38.458 | 25.001 | 2.3 | 3.1 | 1 | 0.7 | 0.2
4089 | 30/07/2025 11:40:54.333 | 99.48 | 86 | 100 | 70 | 52 | 32.583 | 9.131 | 7.151 | 133.165 | 31.007 | 28.689 | 29.105 | 612.792 | 26.596 | 27.568 | 1279.98 | 27.339 | 27.609 | 38.616 | 30.001 | 2.4 | 4 | 0.6 | 0.7 | 0.2
4090 | 30/07/2025 11:40:55.967 | 99.888 | 85 | 100 | 70 | 52 | 30.034 | 9.135 | 7.15 | 133.09 | 31.018 | 28.662 | 29.136 | 612.875 | 26.589 | 27.573 | 1276.886 | 27.348 | 27.594 | 40.234 | 29.001 | 2.2 | 1.9 | 0.7 | 0.9 | 0.2
4091 | 30/07/2025 11:40:57.601 | 100.008 | 85 | 100 | 70 | 52 | 28.899 | 9.173 | 7.152 | 132.983 | 31.036 | 28.692 | 29.165 | 612.163 | 26.585 | 27.556 | 1276.787 | 27.353 | 27.602 | 40.201 | 33.001 | 2.3 | 3.4 | 0.6 | 0.9 | 0.1
4092 | 30/07/2025 11:40:59.238 | 100.368 | 84 | 100 | 71 | 52 | 32.19 | 9.291 | 7.152 | 133.083 | 31.02 | 28.702 | 29.127 | 611.81 | 26.592 | 27.567 | 1276.983 | 27.362 | 27.584 | 40.072 | 33.001 | 2.3 | 3.4 | 0.6 | 0.9 | 0.1
4093 | 30/07/2025 11:41:00.874 | 100.44 | 87 | 100 | 70 | 52 | 32.298 | 9.242 | 7.153 | 133.194 | 31.043 | 28.685 | 29.116 | 610.336 | 26.609 | 27.543 | 1282.32 | 27.317 | 27.58 | 40.31 | 29.001 | 3 | 4 | 0 | 0.6 | 0.1
4094 | 30/07/2025 11:41:02.509 | 100.296 | 88 | 100 | 71 | 52 | 31.604 | 9.213 | 7.151 | 133.174 | 31.038 | 28.681 | 29.105 | 610.422 | 26.585 | 27.57 | 1277.048 | 27.311 | 27.612 | 38.893 | 32.001 | 2.3 | 4.3 | 1.5 | 0.6 | 0.2
4095 | 30/07/2025 11:41:04.145 | 100.56 | 88 | 100 | 69 | 52 | 32.605 | 9.288 | 7.15 | 133.289 | 31.051 | 28.669 | 29.143 | 610.637 | 26.607 | 27.556 | 1255.34 | 27.344 | 27.6 | 38.342 | 29.001 | 4.8 | 3.6 | 0.6 | 0.6 | 0.2
4096 | 30/07/2025 11:41:05.780 | 100.248 | 86 | 100 | 70 | 52 | 29.729 | 9.179 | 7.152 | 133.1 | 31.024 | 28.713 | 29.144 | 610.665 | 26.582 | 27.553 | 1247.071 | 27.356 | 27.594 | 40.152 | 27.001 | 2.2 | 2.6 | 0.6 | 0.6 | 0.2
4097 | 30/07/2025 11:41:07.415 | 100.176 | 88 | 100 | 71 | 52 | 29.466 | 9.161 | 7.152 | 133.305 | 31.03 | 28.693 | 29.125 | 610.381 | 26.581 | 27.555 | 1259.412 | 27.344 | 27.593 | 40.224 | 23.001 | 3.7 | 4.4 | 0.9 | 0 | 0.2
4098 | 30/07/2025 11:41:09.050 | 100.776 | 87 | 100 | 71 | 52 | 32.339 | 9.239 | 7.186 | 133.154 | 31.037 | 28.693 | 29.138 | 610.536 | 26.576 | 27.54 | 1257.706 | 27.317 | 27.606 | 40.473 | 23.001 | 3.7 | 4.4 | 0.9 | 0 | 0.2
4099 | 30/07/2025 11:41:10.684 | 100.536 | 88 | 100 | 70 | 52 | 31.955 | 8.992 | 7.151 | 132.986 | 31.04 | 28.677 | 29.142 | 610.495 | 26.569 | 27.545 | 1247.078 | 27.36 | 27.596 | 40.271 | 27.001 | 3.6 | 4.9 | 0.8 | 0 | 0.3
4100 | 30/07/2025 11:41:12.321 | 100.056 | 89 | 100 | 70 | 51 | 32.03 | 9.02 | 7.151 | 133.217 | 31.032 | 28.679 | 29.146 | 610.304 | 26.578 | 27.519 | 1253.804 | 27.361 | 27.599 | 40.394 | 30.001 | 2.7 | 2.9 | 0.6 | 0.6 | 0.3
4101 | 30/07/2025 11:41:13.956 | 99.408 | 88 | 100 | 71 | 51 | 32.557 | 8.991 | 7.152 | 132.909 | 31.017 | 28.7 | 29.14 | 610.481 | 26.583 | 27.552 | 1250.936 | 27.354 | 27.59 | 40.109 | 34.001 | 2.3 | 2.8 | 0.7 | 0.6 | 0.2
4102 | 30/07/2025 11:41:15.591 | 99.552 | 86 | 100 | 70 | 52 | 29.048 | 9.127 | 7.153 | 133.346 | 31.031 | 28.686 | 29.134 | 609.19 | 26.602 | 27.541 | 1262.329 | 27.34 | 27.609 | 40.033 | 26.001 | 2.3 | 2 | 1.3 | 0.8 | 0.2
4103 | 30/07/2025 11:41:17.226 | 99.096 | 84 | 100 | 70 | 52 | 29.902 | 9.114 | 7.185 | 133.208 | 31.019 | 28.679 | 29.12 | 608.069 | 26.577 | 27.524 | 1267.588 | 27.328 | 27.607 | 40.372 | 26.001 | 2.3 | 2 | 1.3 | 0.8 | 0.2
4104 | 30/07/2025 11:41:18.861 | 99.288 | 85 | 99 | 70 | 52 | 32.374 | 8.99 | 7.155 | 134.472 | 31.021 | 28.677 | 29.146 | 608.046 | 26.594 | 27.557 | 1266.975 | 27.348 | 27.597 | 38.453 | 28.001 | 2.7 | 2.9 | 0.1 | 0.8 | 0.2
4105 | 30/07/2025 11:41:20.504 | 99.336 | 86 | 100 | 70 | 52 | 28.868 | 8.988 | 7.152 | 134.659 | 31.027 | 28.693 | 29.153 | 608.076 | 26.596 | 27.549 | 1267.207 | 27.372 | 27.593 | 38.439 | 26.001 | 1.7 | 2 | 0.7 | 0 | 0.1
4106 | 30/07/2025 11:41:22.140 | 98.64 | 86 | 100 | 71 | 52 | 32.193 | 9.168 | 7.168 | 134.56 | 31.021 | 28.691 | 29.142 | 607.97 | 26.601 | 27.55 | 1274.732 | 27.346 | 27.585 | 38.433 | 27.001 | 2.6 | 3.6 | 0.6 | 0 | 0.1
4107 | 30/07/2025 11:41:23.777 | 98.832 | 83 | 100 | 70 | 52 | 32.358 | 9.13 | 7.186 | 134.616 | 31.013 | 28.693 | 29.134 | 607.964 | 26.598 | 27.546 | 1267.28 | 27.332 | 27.61 | 38.472 | 30.001 | 2.5 | 2.3 | 0.9 | 0.2 | 0.1
4108 | 30/07/2025 11:41:25.413 | 98.712 | 85 | 99 | 70 | 52 | 28.545 | 9.02 | 7.151 | 134.682 | 31.017 | 28.675 | 29.115 | 608.071 | 26.598 | 27.573 | 1267.41 | 27.338 | 27.602 | 38.519 | 30.001 | 2.3 | 3.7 | 0.7 | 0.2 | 0.1
4109 | 30/07/2025 11:41:27.048 | 98.664 | 85 | 100 | 69 | 52 | 30.473 | 9.127 | 7.135 | 134.745 | 31.011 | 28.684 | 29.152 | 608.062 | 26.607 | 27.572 | 1262.185 | 27.349 | 27.61 | 38.294 | 30.001 | 2.3 | 3.7 | 0.7 | 0.2 | 0.1
4110 | 30/07/2025 11:41:28.683 | 98.832 | 85 | 100 | 70 | 51 | 29.428 | 9.136 | 7.135 | 134.257 | 31 | 28.694 | 29.148 | 608.038 | 26.6 | 27.569 | 1262.242 | 27.349 | 27.595 | 38.38 | 27.001 | 3.2 | 5.1 | 0.7 | 0.8 | 0.2
4111 | 30/07/2025 11:41:30.320 | 98.376 | 83 | 100 | 70 | 52 | 29.374 | 9.208 | 7.133 | 134.72 | 31.031 | 28.695 | 29.158 | 608.014 | 26.596 | 27.547 | 1269.546 | 27.342 | 27.589 | 38.221 | 23.001 | 4.1 | 2.8 | 0.6 | 0.8 | 0.2
4112 | 30/07/2025 11:41:31.954 | 98.328 | 84 | 100 | 70 | 52 | 32.347 | 9.133 | 7.133 | 134.692 | 31.018 | 28.682 | 29.12 | 608.04 | 26.593 | 27.547 | 1268.129 | 27.347 | 27.605 | 38.507 | 23.001 | 5.9 | 5.9 | 0.3 | 0.6 | 0.3
4113 | 30/07/2025 11:41:33.588 | 97.944 | 83 | 100 | 70 | 52 | 31.912 | 9.134 | 7.151 | 134.502 | 31.031 | 28.668 | 29.152 | 608.021 | 26.601 | 27.561 | 1259.742 | 27.335 | 27.611 | 38.401 | 26.001 | 3.1 | 5 | 1 | 0.6 | 0.2
4114 | 30/07/2025 11:41:35.226 | 97.92 | 83 | 100 | 70 | 52 | 28.317 | 8.985 | 7.152 | 134.477 | 31.04 | 28.686 | 29.161 | 608.089 | 26.602 | 27.54 | 1269.553 | 27.349 | 27.597 | 38.358 | 26.001 | 3.1 | 5 | 1 | 0.6 | 0.2
4115 | 30/07/2025 11:41:36.862 | 98.208 | 83 | 100 | 71 | 52 | 31.057 | 9.22 | 7.151 | 134.558 | 31.042 | 28.698 | 29.145 | 608.065 | 26.583 | 27.552 | 1277.2 | 27.359 | 27.586 | 38.364 | 23.001 | 3.4 | 2 | 0.2 | 0.2 | 0.2
4116 | 30/07/2025 11:41:38.497 | 97.92 | 84 | 100 | 70 | 52 | 29.143 | 9.207 | 7.152 | 134.833 | 31.032 | 28.695 | 29.132 | 608.091 | 26.58 | 27.544 | 1276.927 | 27.345 | 27.603 | 38.333 | 24.001 | 2.2 | 3.3 | 0.6 | 0.2 | 0.2
4117 | 30/07/2025 11:41:40.132 | 97.656 | 83 | 100 | 70 | 52 | 30.061 | 9.262 | 7.152 | 134.589 | 31.034 | 28.679 | 29.101 | 607.958 | 26.59 | 27.575 | 1287.458 | 27.326 | 27.629 | 38.334 | 31.001 | 1.1 | 2.5 | 1.5 | 0 | 0.2
4118 | 30/07/2025 11:41:41.768 | 98.256 | 84 | 100 | 70 | 52 | 32.399 | 9.128 | 7.15 | 134.685 | 31.034 | 28.675 | 29.145 | 608.116 | 26.579 | 27.537 | 1285.685 | 27.349 | 27.594 | 38.356 | 30.001 | 1.7 | 3.4 | 0.3 | 0 | 0.2
4119 | 30/07/2025 11:41:43.633 | 98.376 | 83 | 100 | 70 | 52 | 31.516 | 9.292 | 7.151 | 134.351 | 31.025 | 28.704 | 29.149 | 608.049 | 26.588 | 27.55 | 1279.608 | 27.37 | 27.598 | 38.517 | 22.001 | 3.5 | 3.3 | 0.6 | 0.5 | 0.2
4120 | 30/07/2025 11:41:45.270 | 98.616 | 84 | 100 | 70 | 53 | 28.388 | 9.132 | 7.153 | 134.7 | 31.035 | 28.689 | 29.139 | 608.016 | 26.601 | 27.559 | 1286.246 | 27.348 | 27.59 | 38.342 | 22.001 | 3.5 | 3.3 | 0.6 | 0.5 | 0.2
4121 | 30/07/2025 11:41:46.907 | 98.328 | 86 | 100 | 70 | 52 | 31.697 | 9.132 | 7.151 | 134.545 | 31.028 | 28.688 | 29.13 | 606.98 | 26.576 | 27.529 | 1291.994 | 27.319 | 27.616 | 38.51 | 25.001 | 4.1 | 2.1 | 0.7 | 0.5 | 0.2
4122 | 30/07/2025 11:41:48.544 | 98.232 | 84 | 100 | 70 | 52 | 32.658 | 9.129 | 7.154 | 134.48 | 31.028 | 28.666 | 29.133 | 606.937 | 26.573 | 27.537 | 1301.26 | 27.344 | 27.618 | 38.655 | 31.001 | 4.4 | 1.1 | 0 | 0.3 | 0.2
4123 | 30/07/2025 11:41:50.178 | 98.496 | 84 | 100 | 70 | 52 | 30.593 | 9.285 | 7.185 | 134.595 | 31.037 | 28.688 | 29.165 | 605.777 | 26.575 | 27.533 | 1297.72 | 27.36 | 27.617 | 38.561 | 29.001 | 2.8 | 3.1 | 0 | 0.3 | 0.2
4124 | 30/07/2025 11:41:51.813 | 98.232 | 85 | 100 | 70 | 52 | 32.57 | 9.217 | 7.187 | 134.474 | 31.016 | 28.69 | 29.127 | 604.403 | 26.589 | 27.53 | 1290.884 | 27.354 | 27.571 | 38.481 | 25.001 | 2.5 | 2.8 | 0 | 0.8 | 0.2
4125 | 30/07/2025 11:41:53.449 | 97.56 | 83 | 100 | 71 | 52 | 30.951 | 9.21 | 7.186 | 134.682 | 31.03 | 28.694 | 29.133 | 604.29 | 26.592 | 27.536 | 1273.909 | 27.331 | 27.604 | 38.351 | 27.001 | 2.4 | 3.4 | 0.6 | 0.8 | 0.2
4126 | 30/07/2025 11:41:55.087 | 97.608 | 84 | 100 | 71 | 53 | 28.555 | 9.268 | 7.186 | 134.574 | 31.02 | 28.687 | 29.114 | 604.268 | 26.603 | 27.558 | 1274.474 | 27.33 | 27.618 | 38.48 | 27.001 | 2.4 | 3.4 | 0.6 | 0.8 | 0.2
4127 | 30/07/2025 11:41:56.734 | 97.632 | 84 | 100 | 70 | 52 | 31.923 | 9.326 | 7.186 | 134.522 | 31.01 | 28.667 | 29.146 | 604.231 | 26.594 | 27.566 | 1278.551 | 27.349 | 27.603 | 38.519 | 22.001 | 2.2 | 4.9 | 0.3 | 0.5 | 0.2
4128 | 30/07/2025 11:41:58.368 | 97.704 | 84 | 100 | 70 | 51 | 28.41 | 9.143 | 7.186 | 134.358 | 31.011 | 28.688 | 29.142 | 604.357 | 26.604 | 27.563 | 1280.723 | 27.363 | 27.591 | 38.647 | 23.001 | 1.3 | 4.5 | 0 | 0.5 | 0.3
4129 | 30/07/2025 11:42:00.002 | 97.536 | 82 | 100 | 71 | 52 | 31.016 | 9.268 | 7.188 | 134.605 | 31.014 | 28.682 | 29.145 | 604.321 | 26.617 | 27.57 | 1267.209 | 27.341 | 27.58 | 38.296 | 25.001 | 4.3 | 5 | 0 | 0.6 | 0.2
4130 | 30/07/2025 11:42:01.634 | 97.032 | 83 | 100 | 70 | 52 | 32.585 | 9.231 | 7.186 | 134.625 | 31.013 | 28.692 | 29.141 | 604.385 | 26.594 | 27.559 | 1267.347 | 27.327 | 27.62 | 38.405 | 26.001 | 1.6 | 3.3 | 0.6 | 0.6 | 0.2
4131 | 30/07/2025 11:42:03.269 | 97.128 | 83 | 100 | 70 | 52 | 30.123 | 9.023 | 7.133 | 134.427 | 31.01 | 28.679 | 29.122 | 604.319 | 26.593 | 27.566 | 1264.695 | 27.319 | 27.607 | 40.327 | 26.001 | 1.6 | 3.3 | 0.6 | 0.6 | 0.2
4132 | 30/07/2025 11:42:04.906 | 97.08 | 84 | 100 | 70 | 52 | 28.846 | 9.126 | 7.133 | 134.644 | 31.039 | 28.685 | 29.167 | 604.385 | 26.617 | 27.558 | 1263.122 | 27.35 | 27.605 | 39.847 | 26.001 | 3.1 | 3.4 | 0.7 | 1.1 | 0.2
4133 | 30/07/2025 11:42:06.541 | 97.2 | 84 | 100 | 70 | 52 | 32.162 | 9.137 | 7.134 | 134.371 | 31.02 | 28.697 | 29.141 | 604.512 | 26.585 | 27.558 | 1276.94 | 27.369 | 27.587 | 38.352 | 25.001 | 2.3 | 4.2 | 0.7 | 1.1 | 0.2
4134 | 30/07/2025 11:42:08.189 | 97.296 | 84 | 100 | 70 | 52 | 28.263 | 8.987 | 7.135 | 134.776 | 31.043 | 28.694 | 29.159 | 604.379 | 26.6 | 27.552 | 1279.122 | 27.34 | 27.583 | 38.116 | 26.001 | 1.9 | 2.3 | 0.6 | 0.5 | 0.2
4135 | 30/07/2025 11:42:09.825 | 97.632 | 85 | 100 | 70 | 52 | 31.512 | 9.199 | 7.152 | 134.715 | 31.034 | 28.699 | 29.13 | 603.097 | 26.596 | 27.563 | 1287.194 | 27.342 | 27.612 | 38.561 | 24.001 | 2 | 3.4 | 1.2 | 0.5 | 0.2
4136 | 30/07/2025 11:42:11.462 | 97.728 | 83 | 100 | 70 | 51 | 32.616 | 9.138 | 7.185 | 134.609 | 31.052 | 28.661 | 29.13 | 603.108 | 26.592 | 27.565 | 1278.793 | 27.332 | 27.599 | 40.297 | 26.001 | 2.8 | 3.6 | 0.6 | 0.5 | 0.1
4137 | 30/07/2025 11:42:13.102 | 98.04 | 86 | 100 | 70 | 52 | 29.581 | 9.133 | 7.187 | 134.464 | 31.034 | 28.694 | 29.147 | 603.269 | 26.586 | 27.543 | 1270.082 | 27.353 | 27.6 | 40.197 | 26.001 | 2.8 | 3.6 | 0.6 | 0.5 | 0.1
4138 | 30/07/2025 11:42:14.749 | 98.16 | 82 | 100 | 70 | 52 | 29.491 | 8.992 | 7.187 | 134.449 | 31.037 | 28.702 | 29.149 | 602.967 | 26.593 | 27.568 | 1264.463 | 27.348 | 27.6 | 40.061 | 30.001 | 3.4 | 3.6 | 1.5 | 0.5 | 0.1
4139 | 30/07/2025 11:42:16.383 | 97.896 | 83 | 100 | 71 | 52 | 32.364 | 8.837 | 7.187 | 134.688 | 31.043 | 28.694 | 29.133 | 603.117 | 26.586 | 27.531 | 1257.738 | 27.33 | 27.595 | 38.663 | 24.001 | 1.3 | 3 | 0.6 | 0 | 0.1
4140 | 30/07/2025 11:42:18.017 | 97.632 | 84 | 100 | 71 | 52 | 28.62 | 8.983 | 7.187 | 134.593 | 31.034 | 28.683 | 29.117 | 604.359 | 26.576 | 27.556 | 1262.419 | 27.323 | 27.597 | 38.719 | 25.001 | 4.6 | 4 | 0.9 | 0 | 0.1
4141 | 30/07/2025 11:42:19.654 | 97.512 | 84 | 100 | 71 | 52 | 32.04 | 8.983 | 7.184 | 134.685 | 31.021 | 28.667 | 29.152 | 603.265 | 26.577 | 27.532 | 1262.96 | 27.342 | 27.599 | 38.333 | 25.001 | 5.9 | 3.5 | 1 | 1.3 | 0.1
4142 | 30/07/2025 11:42:21.288 | 97.92 | 84 | 100 | 71 | 52 | 32.58 | 8.91 | 7.188 | 134.461 | 31.028 | 28.693 | 29.153 | 603.173 | 26.576 | 27.533 | 1269.699 | 27.371 | 27.594 | 38.37 | 25.001 | 5.9 | 3.5 | 1 | 1.3 | 0.1
4143 | 30/07/2025 11:42:22.923 | 97.944 | 83 | 100 | 70 | 52 | 29.155 | 9.13 | 7.205 | 134.841 | 31.034 | 28.685 | 29.14 | 603.175 | 26.59 | 27.507 | 1287.132 | 27.339 | 27.573 | 38.357 | 29.001 | 4.8 | 3.6 | 0.3 | 1.3 | 0.1
4144 | 30/07/2025 11:42:24.559 | 97.512 | 84 | 100 | 69 | 52 | 30.023 | 9.131 | 7.203 | 134.597 | 31.028 | 28.701 | 29.128 | 603.061 | 26.583 | 27.527 | 1287.064 | 27.328 | 27.619 | 38.459 | 28.001 | 2.7 | 2.3 | 0 | 0.6 | 0.1
4145 | 30/07/2025 11:42:26.194 | 97.68 | 83 | 100 | 71 | 53 | 30.399 | 9.132 | 7.202 | 134.732 | 31.034 | 28.679 | 29.124 | 602.99 | 26.608 | 27.546 | 1287.202 | 27.307 | 27.587 | 40.294 | 29.001 | 4 | 2.4 | 1.2 | 0.6 | 0.1
4146 | 30/07/2025 11:42:27.829 | 97.272 | 83 | 100 | 70 | 52 | 28.94 | 9.134 | 7.185 | 134.587 | 31.007 | 28.671 | 29.152 | 603.268 | 26.6 | 27.539 | 1280.612 | 27.364 | 27.615 | 40.314 | 24.001 | 1.8 | 2.8 | 1.1 | 0 | 0.1
4147 | 30/07/2025 11:42:29.475 | 97.704 | 83 | 100 | 71 | 52 | 32.251 | 9.133 | 7.188 | 134.484 | 31.013 | 28.688 | 29.135 | 603.137 | 26.597 | 27.562 | 1267.387 | 27.341 | 27.574 | 40.174 | 22.001 | 2.3 | 2 | 0.6 | 0 | 0.2
4148 | 30/07/2025 11:42:31.112 | 97.656 | 84 | 100 | 71 | 53 | 32.408 | 9.286 | 7.186 | 134.728 | 31.014 | 28.693 | 29.148 | 603.19 | 26.59 | 27.554 | 1264.866 | 27.338 | 27.6 | 40.094 | 22.001 | 2.3 | 2 | 0.6 | 0 | 0.2
4149 | 30/07/2025 11:42:32.747 | 97.56 | 84 | 100 | 70 | 53 | 28.645 | 9.132 | 7.21 | 134.519 | 31.015 | 28.684 | 29.121 | 603.163 | 26.596 | 27.565 | 1274.965 | 27.327 | 27.604 | 38.568 | 24.001 | 3.5 | 2.7 | 0.3 | 0.6 | 0.2
4150 | 30/07/2025 11:42:34.383 | 97.776 | 83 | 100 | 72 | 52 | 32.661 | 8.991 | 7.218 | 134.51 | 31.004 | 28.671 | 29.127 | 603.255 | 26.594 | 27.551 | 1269.884 | 27.321 | 27.6 | 40.193 | 24.001 | 2 | 3.8 | 1 | 0.6 | 0.1
4151 | 30/07/2025 11:42:36.018 | 97.656 | 82 | 100 | 70 | 51 | 29.568 | 8.986 | 7.22 | 133.015 | 31.003 | 28.685 | 29.134 | 603.361 | 26.592 | 27.57 | 1272.208 | 27.37 | 27.608 | 38.788 | 24.001 | 4.1 | 4.7 | 0.2 | 0.1 | 0.2
4152 | 30/07/2025 11:42:37.652 | 97.776 | 85 | 100 | 70 | 52 | 29.277 | 9.24 | 7.222 | 133.104 | 31.015 | 28.686 | 29.129 | 603.244 | 26.609 | 27.567 | 1267.472 | 27.343 | 27.569 | 40.146 | 23.001 | 3.7 | 2.5 | 0.6 | 0.1 | 0.2
4153 | 30/07/2025 11:42:39.288 | 97.992 | 83 | 100 | 70 | 52 | 32.318 | 9.148 | 7.219 | 133.342 | 31.021 | 28.689 | 29.126 | 603.221 | 26.59 | 27.541 | 1271.48 | 27.343 | 27.611 | 40.351 | 23.001 | 3.7 | 2.5 | 0.6 | 0.1 | 0.2
4154 | 30/07/2025 11:42:40.921 | 98.736 | 84 | 100 | 71 | 52 | 31.86 | 9.132 | 7.203 | 133.233 | 31.026 | 28.68 | 29.111 | 603 | 26.593 | 27.554 | 1272.197 | 27.313 | 27.599 | 40.28 | 28.001 | 2.7 | 2 | 1.9 | 0.2 | 0.2
4155 | 30/07/2025 11:42:42.557 | 98.784 | 85 | 100 | 70 | 53 | 28.396 | 8.984 | 7.203 | 133.248 | 31.048 | 28.684 | 29.165 | 603.367 | 26.593 | 27.537 | 1257.926 | 27.347 | 27.585 | 40.326 | 28.001 | 2.8 | 3 | 0.7 | 0.2 | 0.2
4156 | 30/07/2025 11:42:44.192 | 98.688 | 85 | 100 | 70 | 52 | 32.579 | 9.098 | 7.217 | 132.899 | 31.049 | 28.688 | 29.137 | 603.197 | 26.595 | 27.553 | 1255.271 | 27.349 | 27.589 | 40.305 | 28.001 | 2.7 | 2.8 | 0.2 | 0.3 | 0.2
4157 | 30/07/2025 11:42:45.828 | 98.136 | 84 | 100 | 70 | 52 | 29.074 | 9.156 | 7.214 | 133.145 | 31.032 | 28.689 | 29.143 | 603.266 | 26.588 | 27.528 | 1247.046 | 27.344 | 27.573 | 40.162 | 27.001 | 3.2 | 2.6 | 0.9 | 0.3 | 0.3
4158 | 30/07/2025 11:42:47.463 | 98.376 | 85 | 100 | 70 | 53 | 29.985 | 9.216 | 7.204 | 132.978 | 31.041 | 28.691 | 29.121 | 602.966 | 26.592 | 27.554 | 1238.191 | 27.331 | 27.609 | 40.347 | 24.001 | 3.2 | 4.7 | 0.7 | 0.5 | 0.3
4159 | 30/07/2025 11:42:49.100 | 98.424 | 84 | 100 | 70 | 52 | 32.38 | 9.041 | 7.187 | 133.326 | 31.03 | 28.667 | 29.124 | 603.063 | 26.597 | 27.559 | 1239.125 | 27.328 | 27.601 | 40.32 | 24.001 | 3.2 | 4.7 | 0.7 | 0.5 | 0.3
4160 | 30/07/2025 11:42:50.734 | 98.184 | 84 | 100 | 70 | 52 | 31.438 | 9.144 | 7.186 | 132.989 | 31.024 | 28.69 | 29.151 | 603.236 | 26.59 | 27.528 | 1252.799 | 27.355 | 27.614 | 40.265 | 26.001 | 3 | 2 | 0.1 | 0.5 | 0.2
4161 | 30/07/2025 11:42:52.370 | 98.304 | 84 | 100 | 70 | 51 | 32.226 | 9.206 | 7.186 | 133.035 | 31.044 | 28.692 | 29.156 | 603.174 | 26.583 | 27.536 | 1249.304 | 27.34 | 27.584 | 40.298 | 26.001 | 3.2 | 4.9 | 0.6 | 0.8 | 0.2
4162 | 30/07/2025 11:42:54.089 | 98.472 | 84 | 100 | 70 | 52 | 32.377 | 9.257 | 7.185 | 133.266 | 31.021 | 28.7 | 29.15 | 603.254 | 26.567 | 27.537 | 1258.318 | 27.359 | 27.609 | 40.09 | 25.001 | 2.7 | 4.7 | 1.2 | 0.8 | 0.2
4163 | 30/07/2025 11:42:55.727 | 98.328 | 84 | 100 | 70 | 52 | 28.603 | 8.989 | 7.187 | 133.208 | 31.03 | 28.685 | 29.127 | 602.975 | 26.582 | 27.539 | 1267.172 | 27.327 | 27.601 | 40.446 | 22.001 | 3 | 3.7 | 0.1 | 0.1 | 0.2
4164 | 30/07/2025 11:42:57.363 | 97.968 | 84 | 100 | 71 | 52 | 30.56 | 9.129 | 7.185 | 133.191 | 31.033 | 28.673 | 29.14 | 603.338 | 26.581 | 27.524 | 1275.122 | 27.347 | 27.604 | 40.344 | 24.001 | 3.8 | 3.3 | 0.6 | 0.1 | 0.2
4165 | 30/07/2025 11:42:58.999 | 97.752 | 84 | 100 | 71 | 52 | 32.525 | 9.289 | 7.187 | 132.982 | 31.012 | 28.715 | 29.142 | 603.1 | 26.579 | 27.549 | 1274.538 | 27.362 | 27.6 | 40.128 | 24.001 | 3.8 | 3.3 | 0.6 | 0.1 | 0.2
4166 | 30/07/2025 11:43:00.636 | 98.064 | 84 | 100 | 71 | 52 | 30.994 | 8.985 | 7.188 | 133.321 | 31.026 | 28.69 | 29.129 | 603.064 | 26.614 | 27.552 | 1256.932 | 27.334 | 27.572 | 40.08 | 23.001 | 3.1 | 2.1 | 0.9 | 0 | 0.2
4167 | 30/07/2025 11:43:02.270 | 98.088 | 84 | 100 | 71 | 53 | 32.362 | 8.985 | 7.187 | 133.2 | 31.026 | 28.703 | 29.133 | 603.145 | 26.606 | 27.559 | 1256.95 | 27.339 | 27.604 | 40.15 | 24.001 | 2.4 | 1.7 | 1.3 | 0 | 0.2
4168 | 30/07/2025 11:43:03.904 | 98.328 | 84 | 100 | 70 | 52 | 32.083 | 8.984 | 7.152 | 133.464 | 31.018 | 28.682 | 29.125 | 602.967 | 26.594 | 27.541 | 1247.321 | 27.309 | 27.595 | 40.312 | 21.001 | 1.8 | 3.6 | 0.7 | 0.5 | 0.2
4169 | 30/07/2025 11:43:05.540 | 98.4 | 84 | 100 | 71 | 52 | 28.449 | 9.134 | 7.133 | 133.025 | 31.014 | 28.669 | 29.147 | 603.187 | 26.583 | 27.568 | 1247.33 | 27.374 | 27.61 | 40.472 | 30.001 | 2.6 | 1.8 | 0 | 0.5 | 0.2
4170 | 30/07/2025 11:43:07.176 | 98.664 | 83 | 100 | 70 | 52 | 31.072 | 9.198 | 7.137 | 132.876 | 30.999 | 28.693 | 29.149 | 603.094 | 26.603 | 27.568 | 1250.539 | 27.344 | 27.587 | 40.177 | 30.001 | 2.6 | 1.8 | 0 | 0.5 | 0.2
4171 | 30/07/2025 11:43:08.812 | 98.808 | 87 | 100 | 71 | 52 | 32.587 | 9.133 | 7.133 | 133.131 | 31.006 | 28.69 | 29.138 | 603.288 | 26.587 | 27.542 | 1259.106 | 27.342 | 27.591 | 39.904 | 31.001 | 2.6 | 3.6 | 1.2 | 0.9 | 0.2
4172 | 30/07/2025 11:43:10.449 | 98.856 | 84 | 100 | 70 | 52 | 30.262 | 8.993 | 7.122 | 133.021 | 31.003 | 28.695 | 29.113 | 603.095 | 26.591 | 27.564 | 1252.77 | 27.326 | 27.608 | 40.296 | 25.001 | 3.6 | 4.3 | 0.6 | 0.9 | 0.2
4173 | 30/07/2025 11:43:12.086 | 98.568 | 84 | 100 | 70 | 53 | 32.417 | 9.09 | 7.119 | 133.243 | 31.019 | 28.678 | 29.124 | 603.19 | 26.598 | 27.551 | 1249.697 | 27.32 | 27.612 | 40.304 | 25.001 | 3.9 | 1.7 | 0.9 | 0.5 | 0.3
4174 | 30/07/2025 11:43:13.721 | 98.736 | 85 | 100 | 71 | 52 | 31.43 | 9.283 | 7.09 | 132.88 | 31.031 | 28.677 | 29.134 | 603.139 | 26.596 | 27.567 | 1257.247 | 27.348 | 27.597 | 40.233 | 29.001 | 2.2 | 2.7 | 0.2 | 0.5 | 0.3
4175 | 30/07/2025 11:43:15.359 | 98.112 | 84 | 100 | 70 | 52 | 28.295 | 9.19 | 7.088 | 133.099 | 31.039 | 28.691 | 29.138 | 603.156 | 26.61 | 27.544 | 1258.838 | 27.34 | 27.585 | 40.095 | 28.001 | 2.7 | 2.1 | 0 | 0.3 | 0.3
4176 | 30/07/2025 11:43:16.994 | 98.64 | 84 | 100 | 71 | 52 | 31.496 | 9.288 | 7.059 | 133.315 | 31.029 | 28.695 | 29.139 | 603.113 | 26.594 | 27.552 | 1257.258 | 27.345 | 27.622 | 40.11 | 28.001 | 2.7 | 2.1 | 0 | 0.3 | 0.3
4177 | 30/07/2025 11:43:18.634 | 98.616 | 84 | 100 | 71 | 52 | 32.648 | 8.985 | 7.059 | 133.021 | 31.035 | 28.68 | 29.119 | 603.035 | 26.586 | 27.554 | 1255.031 | 27.31 | 27.603 | 40.335 | 28.001 | 3.7 | 2.3 | 0 | 0.3 | 0.2
4178 | 30/07/2025 11:43:20.271 | 98.736 | 85 | 100 | 70 | 52 | 30.448 | 9.129 | 7.057 | 133.205 | 31.026 | 28.665 | 29.137 | 603.246 | 26.59 | 27.545 | 1255.268 | 27.354 | 27.602 | 40.352 | 29.001 | 2.3 | 4.3 | 1.2 | 0 | 0.2
4179 | 30/07/2025 11:43:21.906 | 98.688 | 86 | 100 | 70 | 52 | 32.49 | 9.257 | 7.089 | 132.99 | 31.04 | 28.687 | 29.132 | 603.209 | 26.597 | 27.553 | 1264.978 | 27.34 | 27.581 | 40.44 | 20.001 | 3.5 | 2.4 | 0.6 | 0 | 0.2
4180 | 30/07/2025 11:43:23.540 | 99.024 | 85 | 100 | 70 | 52 | 30.775 | 8.996 | 7.135 | 133.244 | 31.041 | 28.692 | 29.142 | 603.226 | 26.582 | 27.536 | 1266.622 | 27.344 | 27.574 | 39.875 | 26.001 | 3.9 | 2.2 | 0.6 | 0 | 0.2
4181 | 30/07/2025 11:43:25.183 | 98.928 | 84 | 100 | 70 | 52 | 28.534 | 8.992 | 7.186 | 133.037 | 31.039 | 28.683 | 29.111 | 603.142 | 26.583 | 27.555 | 1257.426 | 27.343 | 27.614 | 40.349 | 26.001 | 3.9 | 2.2 | 0.6 | 0 | 0.2
4182 | 30/07/2025 11:43:26.819 | 99.12 | 85 | 99 | 70 | 52 | 31.944 | 9.129 | 7.216 | 133.189 | 31.047 | 28.67 | 29.105 | 603.113 | 26.587 | 27.539 | 1261.412 | 27.331 | 27.601 | 40.195 | 25.001 | 2.4 | 2.4 | 0.6 | 0 | 0.2
4183 | 30/07/2025 11:43:28.454 | 98.928 | 84 | 100 | 71 | 52 | 32.551 | 8.987 | 7.275 | 133.046 | 31.018 | 28.692 | 29.152 | 602.107 | 26.585 | 27.518 | 1268.238 | 27.367 | 27.62 | 40.355 | 26.001 | 2.4 | 1.8 | 0.9 | 0 | 0.2
4184 | 30/07/2025 11:43:30.090 | 98.952 | 86 | 100 | 69 | 52 | 31.001 | 9.251 | 7.277 | 132.987 | 31.045 | 28.698 | 29.162 | 601.999 | 26.594 | 27.535 | 1271.758 | 27.343 | 27.586 | 40.25 | 26.001 | 3.4 | 2.8 | 0.7 | 0 | 0.3
4185 | 30/07/2025 11:43:31.725 | 98.832 | 84 | 100 | 70 | 53 | 32.567 | 8.886 | 7.274 | 133.203 | 31.025 | 28.691 | 29.134 | 601.972 | 26.598 | 27.541 | 1266.777 | 27.368 | 27.602 | 39.861 | 20.001 | 3 | 2.8 | 0 | 0.2 | 0.4
4186 | 30/07/2025 11:43:33.360 | 99.288 | 85 | 100 | 70 | 52 | 30.361 | 9.053 | 7.24 | 133.216 | 31.018 | 28.678 | 29.125 | 601.833 | 26.593 | 27.54 | 1269.201 | 27.322 | 27.599 | 40.527 | 22.001 | 2.1 | 3 | 0.7 | 0.2 | 0.3
4187 | 30/07/2025 11:43:35.018 | 99.408 | 84 | 100 | 70 | 51 | 28.949 | 9.175 | 7.216 | 133.277 | 31.027 | 28.676 | 29.153 | 602.06 | 26.605 | 27.536 | 1273.633 | 27.342 | 27.594 | 38.648 | 22.001 | 2.1 | 3 | 0.7 | 0.2 | 0.3
4188 | 30/07/2025 11:43:36.652 | 99.264 | 85 | 100 | 71 | 51 | 32.24 | 9.135 | 7.203 | 132.99 | 31.02 | 28.697 | 29.148 | 601.928 | 26.6 | 27.581 | 1264.457 | 27.363 | 27.609 | 38.36 | 28.001 | 2 | 2.9 | 1 | 0.2 | 0.3
4189 | 30/07/2025 11:43:38.284 | 99.24 | 85 | 100 | 70 | 52 | 32.393 | 9.214 | 7.239 | 134.807 | 31.017 | 28.687 | 29.139 | 601.957 | 26.614 | 27.557 | 1270.074 | 27.346 | 27.575 | 38.256 | 27.001 | 2.8 | 1.9 | 1.1 | 0.2 | 0.3
4190 | 30/07/2025 11:43:39.920 | 98.976 | 85 | 100 | 72 | 52 | 31.614 | 8.987 | 7.24 | 134.592 | 31 | 28.694 | 29.135 | 601.846 | 26.597 | 27.578 | 1263.581 | 27.341 | 27.595 | 38.252 | 28.001 | 2.6 | 4.4 | 0.6 | 0.6 | 0.3
4191 | 30/07/2025 11:43:41.554 | 99.408 | 87 | 100 | 70 | 51 | 32.605 | 9.388 | 7.186 | 134.805 | 31.026 | 28.683 | 29.12 | 601.989 | 26.598 | 27.564 | 1257.669 | 27.312 | 27.613 | 38.593 | 26.001 | 2 | 3.7 | 0.3 | 0.6 | 0.3
4192 | 30/07/2025 11:43:43.203 | 99.024 | 85 | 100 | 70 | 52 | 29.693 | 9.134 | 7.164 | 134.635 | 31.016 | 28.659 | 29.138 | 601.93 | 26.588 | 27.558 | 1255.144 | 27.373 | 27.605 | 40.318 | 26.001 | 2 | 3.7 | 0.3 | 0.6 | 0.3
4193 | 30/07/2025 11:43:44.837 | 98.976 | 86 | 100 | 70 | 52 | 29.371 | 9.12 | 7.154 | 134.482 | 30.999 | 28.698 | 29.131 | 602.08 | 26.602 | 27.557 | 1266.638 | 27.352 | 27.579 | 40.448 | 27.001 | 1.1 | 4.1 | 0.6 | 0.5 | 0.3
4194 | 30/07/2025 11:43:46.469 | 98.736 | 86 | 100 | 70 | 51 | 32.323 | 9.257 | 7.184 | 134.748 | 31.036 | 28.698 | 29.156 | 601.898 | 26.596 | 27.55 | 1263.138 | 27.347 | 27.598 | 39.907 | 26.001 | 3.5 | 7 | 0.1 | 0.5 | 0.2
4195 | 30/07/2025 11:43:48.102 | 98.376 | 84 | 100 | 70 | 51 | 28.45 | 9.282 | 7.187 | 134.654 | 31.031 | 28.688 | 29.127 | 601.766 | 26.61 | 27.584 | 1252.577 | 27.339 | 27.603 | 40.109 | 24.001 | 2.2 | 3.4 | 1.8 | 0 | 0.2
4196 | 30/07/2025 11:43:49.737 | 97.728 | 84 | 100 | 70 | 52 | 31.986 | 8.993 | 7.186 | 134.646 | 31.039 | 28.678 | 29.14 | 602.002 | 26.584 | 27.545 | 1255.085 | 27.322 | 27.606 | 40.244 | 27.001 | 3.9 | 2.9 | 1.4 | 0 | 0.2
4197 | 30/07/2025 11:43:51.371 | 97.344 | 83 | 100 | 71 | 52 | 32.592 | 8.987 | 7.187 | 134.449 | 31.033 | 28.675 | 29.144 | 601.655 | 26.594 | 27.572 | 1266.202 | 27.357 | 27.603 | 40.405 | 22.001 | 1.9 | 4.5 | 1 | 0.5 | 0.2
4198 | 30/07/2025 11:43:53.004 | 97.512 | 84 | 100 | 71 | 52 | 29.149 | 9.127 | 7.187 | 134.515 | 31.054 | 28.691 | 29.138 | 601.935 | 26.589 | 27.547 | 1275.858 | 27.34 | 27.562 | 40.137 | 22.001 | 1.9 | 4.5 | 1 | 0.5 | 0.2
4199 | 30/07/2025 11:43:54.638 | 97.632 | 83 | 100 | 70 | 50 | 30 | 9.284 | 7.186 | 134.572 | 31.033 | 28.696 | 29.141 | 602.096 | 26.587 | 27.551 | 1288.219 | 27.362 | 27.601 | 40.203 | 21.001 | 3.1 | 2.5 | 0.6 | 0.5 | 0.2
4200 | 30/07/2025 11:43:56.273 | 97.656 | 84 | 100 | 70 | 52 | 32.423 | 9.133 | 7.186 | 134.426 | 31.035 | 28.676 | 29.106 | 603.133 | 26.592 | 27.553 | 1292.428 | 27.316 | 27.604 | 40.443 | 26.001 | 3.1 | 5.1 | 0.3 | 0.5 | 0.2
4201 | 30/07/2025 11:43:57.907 | 97.68 | 84 | 100 | 71 | 52 | 28.929 | 9.135 | 7.184 | 134.469 | 31.035 | 28.687 | 29.141 | 601.979 | 26.591 | 27.555 | 1292.294 | 27.347 | 27.614 | 40.288 | 26.001 | 2.7 | 3.1 | 0 | 0.5 | 0.2
4202 | 30/07/2025 11:43:59.600 | 97.872 | 85 | 100 | 71 | 52 | 32.205 | 9.147 | 7.171 | 134.536 | 31.026 | 28.688 | 29.142 | 602.129 | 26.591 | 27.538 | 1286.907 | 27.361 | 27.594 | 40.425 | 26.001 | 3.1 | 2.8 | 0.7 | 1 | 0.2
4203 | 30/07/2025 11:44:01.236 | 98.616 | 83 | 100 | 70 | 51 | 32.334 | 9.152 | 7.152 | 134.58 | 31.017 | 28.692 | 29.14 | 602.57 | 26.578 | 27.533 | 1286.939 | 27.347 | 27.582 | 40.069 | 26.001 | 3.1 | 2.8 | 0.7 | 1 | 0.2
4204 | 30/07/2025 11:44:02.870 | 98.832 | 84 | 100 | 71 | 52 | 28.618 | 8.989 | 7.153 | 134.695 | 31.037 | 28.686 | 29.121 | 601.887 | 26.578 | 27.534 | 1294.208 | 27.329 | 27.613 | 40.382 | 26.001 | 1.8 | 3.4 | 0.7 | 1 | 0.2
4205 | 30/07/2025 11:44:04.504 | 98.784 | 84 | 100 | 70 | 52 | 30.409 | 9.123 | 7.15 | 134.558 | 31.033 | 28.676 | 29.121 | 601.903 | 26.577 | 27.518 | 1287.275 | 27.315 | 27.595 | 40.237 | 29.001 | 2.9 | 3 | 1.2 | 1.2 | 0.2
4206 | 30/07/2025 11:44:06.140 | 98.976 | 86 | 100 | 69 | 53 | 29.641 | 9.133 | 7.185 | 134.437 | 31.019 | 28.659 | 29.146 | 601.846 | 26.592 | 27.531 | 1287.255 | 27.338 | 27.592 | 40.205 | 27.001 | 2.1 | 3 | 0.7 | 1.2 | 0.3
4207 | 30/07/2025 11:44:07.782 | 98.952 | 86 | 100 | 70 | 52 | 29.351 | 9.138 | 7.186 | 134.47 | 31.036 | 28.69 | 29.164 | 601.742 | 26.6 | 27.536 | 1278.633 | 27.347 | 27.592 | 40.198 | 31.001 | 1.6 | 6 | 2.1 | 0.2 | 0.2
4208 | 30/07/2025 11:44:09.417 | 98.88 | 84 | 100 | 71 | 54 | 32.363 | 8.985 | 7.186 | 134.626 | 31.023 | 28.698 | 29.148 | 602.038 | 26.599 | 27.544 | 1277.027 | 27.366 | 27.586 | 40.038 | 25.001 | 1 | 2.4 | 1.8 | 0.2 | 0.4
4209 | 30/07/2025 11:44:11.052 | 99.24 | 84 | 100 | 71 | 53 | 32.021 | 9.127 | 7.137 | 134.856 | 31.016 | 28.684 | 29.12 | 600.572 | 26.6 | 27.557 | 1274.179 | 27.322 | 27.604 | 40.533 | 25.001 | 1 | 2.4 | 1.8 | 0.2 | 0.4
4210 | 30/07/2025 11:44:12.687 | 98.688 | 85 | 100 | 70 | 52 | 28.342 | 9.249 | 7.133 | 134.676 | 31.005 | 28.675 | 29.14 | 600.527 | 26.593 | 27.556 | 1275.877 | 27.333 | 27.603 | 38.608 | 23.001 | 2.3 | 5 | 0.8 | 0.6 | 0.4
4211 | 30/07/2025 11:44:14.324 | 98.304 | 84 | 100 | 70 | 52 | 31.096 | 9.137 | 7.187 | 134.316 | 31.01 | 28.689 | 29.15 | 600.351 | 26.597 | 27.564 | 1276.971 | 27.353 | 27.598 | 38.494 | 25.001 | 1.5 | 4.7 | 0.6 | 0.6 | 0.3
4212 | 30/07/2025 11:44:15.959 | 97.992 | 84 | 100 | 70 | 52 | 29.033 | 9.281 | 7.171 | 134.522 | 31.001 | 28.696 | 29.137 | 600.433 | 26.597 | 27.551 | 1288.581 | 27.349 | 27.593 | 39.806 | 25.001 | 1.9 | 2.5 | 0.1 | 0.8 | 0.3
4213 | 30/07/2025 11:44:17.593 | 97.416 | 82 | 100 | 71 | 52 | 29.904 | 9.154 | 7.153 | 134.585 | 31.004 | 28.687 | 29.135 | 600.511 | 26.598 | 27.562 | 1277.346 | 27.335 | 27.581 | 39.978 | 21.001 | 1.4 | 3.7 | 0.6 | 0.8 | 0.3
4214 | 30/07/2025 11:44:19.232 | 97.824 | 85 | 100 | 70 | 53 | 32.391 | 9.126 | 7.15 | 134.762 | 31.009 | 28.685 | 29.119 | 601.949 | 26.601 | 27.55 | 1271.685 | 27.303 | 27.61 | 40.283 | 21.001 | 1.4 | 3.7 | 0.6 | 0.8 | 0.3
4215 | 30/07/2025 11:44:20.867 | 97.848 | 84 | 100 | 70 | 52 | 31.534 | 9.288 | 7.142 | 134.631 | 31.022 | 28.659 | 29.132 | 601.993 | 26.589 | 27.546 | 1257.927 | 27.36 | 27.593 | 40.576 | 26.001 | 4 | 2.9 | 0.6 | 0.9 | 0.3
4216 | 30/07/2025 11:44:22.503 | 98.16 | 83 | 100 | 71 | 52 | 28.342 | 9.212 | 7.135 | 134.331 | 31.029 | 28.689 | 29.142 | 601.737 | 26.598 | 27.56 | 1267.09 | 27.348 | 27.59 | 40.12 | 26.001 | 2 | 3.9 | 0.6 | 0.8 | 0.2
4217 | 30/07/2025 11:44:24.137 | 97.92 | 83 | 100 | 70 | 50 | 32.444 | 9.138 | 7.135 | 134.254 | 31.028 | 28.707 | 29.144 | 601.783 | 26.594 | 27.565 | 1266.598 | 27.348 | 27.594 | 39.969 | 26.001 | 2 | 4.1 | 0.6 | 0 | 0.2
4218 | 30/07/2025 11:44:25.770 | 97.872 | 84 | 100 | 70 | 52 | 28.719 | 9.201 | 7.136 | 134.715 | 31.045 | 28.691 | 29.129 | 601.955 | 26.605 | 27.546 | 1259.865 | 27.336 | 27.599 | 40.099 | 25.001 | 2 | 3.4 | 0.6 | 0 | 0.2
4219 | 30/07/2025 11:44:27.407 | 97.776 | 83 | 100 | 70 | 52 | 30.54 | 9.129 | 7.148 | 134.636 | 31.025 | 28.684 | 29.117 | 603.319 | 26.591 | 27.549 | 1266.872 | 27.326 | 27.606 | 40.549 | 28.001 | 5 | 4 | 0.6 | 0 | 0.2
4220 | 30/07/2025 11:44:29.047 | 98.112 | 84 | 100 | 70 | 52 | 32.538 | 8.986 | 7.146 | 134.648 | 31.036 | 28.672 | 29.145 | 601.882 | 26.584 | 27.554 | 1264.384 | 27.349 | 27.592 | 40.233 | 28.001 | 5 | 4 | 0.6 | 0 | 0.2
4221 | 30/07/2025 11:44:30.683 | 97.776 | 84 | 100 | 70 | 52 | 30.879 | 8.989 | 7.135 | 134.41 | 31.038 | 28.699 | 29.153 | 601.89 | 26.586 | 27.549 | 1264.821 | 27.352 | 27.575 | 40.184 | 27.001 | 1.8 | 4.5 | 0.1 | 0 | 0.2
4222 | 30/07/2025 11:44:32.319 | 97.656 | 84 | 100 | 71 | 52 | 28.548 | 9.007 | 7.135 | 134.681 | 31.018 | 28.701 | 29.132 | 601.92 | 26.587 | 27.547 | 1263.168 | 27.362 | 27.597 | 40.284 | 25.001 | 2.3 | 2.8 | 0.6 | 0.5 | 0.3
4223 | 30/07/2025 11:44:33.954 | 98.232 | 84 | 100 | 70 | 53 | 32.012 | 8.988 | 7.133 | 134.661 | 31.037 | 28.69 | 29.148 | 602.093 | 26.577 | 27.528 | 1269.13 | 27.333 | 27.608 | 40.335 | 27.001 | 2.4 | 3.1 | 1.3 | 0.5 | 0.3
4224 | 30/07/2025 11:44:35.588 | 98.4 | 86 | 100 | 70 | 52 | 28.424 | 9.288 | 7.088 | 134.634 | 31.024 | 28.683 | 29.144 | 601.949 | 26.583 | 27.552 | 1267.345 | 27.335 | 27.605 | 40.245 | 27.001 | 3 | 3.2 | 1.2 | 0.6 | 0.3
4225 | 30/07/2025 11:44:37.225 | 98.16 | 84 | 100 | 71 | 52 | 32.644 | 9.211 | 7.088 | 134.599 | 31.044 | 28.686 | 29.15 | 602.01 | 26.593 | 27.548 | 1273.056 | 27.357 | 27.589 | 40.174 | 27.001 | 3 | 3.2 | 1.2 | 0.6 | 0.3
4226 | 30/07/2025 11:44:38.894 | 98.832 | 84 | 100 | 70 | 52 | 32.653 | 8.991 | 7.121 | 134.48 | 31.021 | 28.698 | 29.15 | 601.76 | 26.584 | 27.529 | 1267.329 | 27.345 | 27.584 | 40.268 | 26.001 | 1.9 | 2.4 | 1.1 | 0.6 | 0.2
4227 | 30/07/2025 11:44:40.532 | 98.928 | 86 | 100 | 71 | 51 | 30.392 | 8.971 | 7.121 | 134.679 | 31.028 | 28.688 | 29.122 | 601.969 | 26.597 | 27.542 | 1269.667 | 27.331 | 27.597 | 40.363 | 24.001 | 2.4 | 3.2 | 0 | 0.1 | 0.2
4228 | 30/07/2025 11:44:42.167 | 99.072 | 87 | 100 | 70 | 52 | 32.449 | 9.209 | 7.121 | 134.746 | 31.017 | 28.684 | 29.122 | 602.057 | 26.591 | 27.534 | 1270.035 | 27.34 | 27.606 | 40.528 | 23.001 | 2.8 | 4.8 | 0.6 | 0.1 | 0.2
4229 | 30/07/2025 11:44:43.803 | 98.784 | 85 | 100 | 70 | 51 | 31.559 | 9.134 | 7.128 | 134.588 | 31.019 | 28.672 | 29.141 | 600.449 | 26.603 | 27.56 | 1276.994 | 27.33 | 27.61 | 40.395 | 30.001 | 1.8 | 4.1 | 0.7 | 0.8 | 0.3
4230 | 30/07/2025 11:44:45.456 | 98.304 | 85 | 100 | 71 | 52 | 28.379 | 9.132 | 7.135 | 134.425 | 31.016 | 28.693 | 29.164 | 600.671 | 26.593 | 27.529 | 1270.139 | 27.35 | 27.594 | 40.389 | 24.001 | 1.6 | 3.5 | 0.6 | 0.1 | 0.3
4231 | 30/07/2025 11:44:47.092 | 97.968 | 84 | 100 | 71 | 52 | 31.483 | 9.212 | 7.152 | 134.593 | 31.011 | 28.703 | 29.134 | 601.776 | 26.591 | 27.568 | 1264.525 | 27.349 | 27.587 | 40.065 | 24.001 | 1.6 | 3.5 | 0.6 | 0.1 | 0.3
4232 | 30/07/2025 11:44:48.725 | 98.352 | 84 | 100 | 71 | 51 | 32.585 | 9.13 | 7.153 | 134.783 | 31.021 | 28.691 | 29.115 | 601.807 | 26.612 | 27.559 | 1264.594 | 27.326 | 27.596 | 40.284 | 24.001 | 1.6 | 3.4 | 0.6 | 1 | 0.3
4233 | 30/07/2025 11:44:50.360 | 98.472 | 84 | 100 | 69 | 52 | 30.434 | 8.936 | 7.152 | 134.53 | 30.991 | 28.677 | 29.121 | 601.924 | 26.582 | 27.57 | 1263.124 | 27.326 | 27.595 | 40.485 | 27.001 | 1 | 2.4 | 0.3 | 1 | 0.3
4234 | 30/07/2025 11:44:51.997 | 98.544 | 84 | 100 | 70 | 52 | 32.513 | 9.204 | 7.134 | 134.761 | 31.022 | 28.677 | 29.156 | 601.941 | 26.606 | 27.554 | 1276.955 | 27.346 | 27.596 | 40.209 | 28.001 | 2.5 | 3.3 | 0 | 0.5 | 0.3
4235 | 30/07/2025 11:44:53.633 | 98.4 | 84 | 100 | 70 | 52 | 30.972 | 9.135 | 7.134 | 134.558 | 31.017 | 28.695 | 29.146 | 602.013 | 26.595 | 27.555 | 1282.81 | 27.359 | 27.599 | 40.151 | 24.001 | 2.7 | 4.3 | 0.9 | 0.5 | 0.4
4236 | 30/07/2025 11:44:55.269 | 98.856 | 88 | 100 | 71 | 52 | 28.481 | 8.935 | 7.152 | 134.713 | 31.032 | 28.69 | 29.133 | 601.874 | 26.591 | 27.563 | 1280.754 | 27.343 | 27.593 | 40.231 | 24.001 | 2.7 | 4.3 | 0.9 | 0.5 | 0.4
4237 | 30/07/2025 11:44:56.904 | 98.616 | 84 | 100 | 70 | 52 | 31.955 | 9.128 | 7.15 | 134.574 | 31.041 | 28.688 | 29.119 | 601.942 | 26.597 | 27.542 | 1274.154 | 27.324 | 27.603 | 38.687 | 26.001 | 1.9 | 3.6 | 0.8 | 0.6 | 0.3
4238 | 30/07/2025 11:44:58.578 | 98.592 | 84 | 100 | 71 | 52 | 32.673 | 9.287 | 7.151 | 134.476 | 31.04 | 28.673 | 29.142 | 602.095 | 26.586 | 27.568 | 1287.58 | 27.348 | 27.599 | 38.634 | 28.001 | 2 | 3.1 | 0.7 | 0.6 | 0.3
4239 | 30/07/2025 11:45:00.213 | 98.76 | 86 | 100 | 70 | 51 | 29.177 | 9.156 | 7.153 | 134.377 | 31.043 | 28.695 | 29.136 | 601.901 | 26.612 | 27.55 | 1287.953 | 27.349 | 27.584 | 38.59 | 31.001 | 2.2 | 4 | 0.6 | 0.8 | 0.3
4240 | 30/07/2025 11:45:01.851 | 98.928 | 84 | 100 | 70 | 52 | 32.623 | 9.136 | 7.151 | 134.375 | 31.03 | 28.691 | 29.144 | 601.871 | 26.593 | 27.556 | 1286.25 | 27.355 | 27.583 | 38.487 | 23.001 | 3.1 | 3 | 0.6 | 0.8 | 0.3
4241 | 30/07/2025 11:45:03.529 | 98.568 | 84 | 100 | 71 | 53 | 30.302 | 9.134 | 7.135 | 134.718 | 31.037 | 28.691 | 29.149 | 602.88 | 26.595 | 27.561 | 1286.775 | 27.344 | 27.615 | 38.353 | 27.001 | 2.1 | 3.2 | 0.1 | 0.5 | 0.3
4242 | 30/07/2025 11:45:05.163 | 98.328 | 83 | 100 | 70 | 52 | 28.971 | 9.135 | 7.132 | 134.6 | 31.023 | 28.681 | 29.123 | 602.246 | 26.578 | 27.542 | 1289.77 | 27.333 | 27.613 | 38.37 | 27.001 | 2.1 | 3.2 | 0.1 | 0.5 | 0.3
4243 | 30/07/2025 11:45:06.799 | 98.568 | 84 | 100 | 71 | 52 | 32.269 | 9.202 | 7.136 | 134.53 | 31.03 | 28.672 | 29.148 | 601.828 | 26.579 | 27.552 | 1294.448 | 27.353 | 27.59 | 39.961 | 28.001 | 3.4 | 3 | 0.3 | 0.5 | 0.2
4244 | 30/07/2025 11:45:08.435 | 98.28 | 86 | 100 | 71 | 51 | 32.41 | 9.165 | 7.135 | 134.397 | 31.04 | 28.7 | 29.153 | 601.944 | 26.586 | 27.526 | 1287.37 | 27.342 | 27.585 | 40.304 | 28.001 | 3.4 | 3.3 | 0.3 | 0.8 | 0.2
4245 | 30/07/2025 11:45:10.069 | 97.992 | 83 | 100 | 70 | 53 | 28.811 | 8.991 | 7.134 | 134.504 | 31.021 | 28.693 | 29.137 | 602.029 | 26.564 | 27.528 | 1297.143 | 27.354 | 27.59 | 40.382 | 30.001 | 2.1 | 4.8 | 0 | 0.8 | 0.2
4246 | 30/07/2025 11:45:11.704 | 97.992 | 84 | 100 | 71 | 52 | 32.656 | 9.135 | 7.134 | 134.643 | 31.03 | 28.698 | 29.137 | 601.933 | 26.58 | 27.515 | 1297.02 | 27.328 | 27.611 | 40.379 | 28.001 | 3.9 | 4.3 | 0.9 | 1.1 | 0.2
4247 | 30/07/2025 11:45:13.340 | 97.8 | 84 | 100 | 71 | 52 | 29.806 | 8.944 | 7.133 | 134.609 | 31.02 | 28.678 | 29.126 | 601.831 | 26.588 | 27.548 | 1287.503 | 27.331 | 27.6 | 40.493 | 29.001 | 2.9 | 2.7 | 1.2 | 1.1 | 0.2
4248 | 30/07/2025 11:45:14.980 | 97.92 | 83 | 100 | 70 | 52 | 29.292 | 9.13 | 7.136 | 134.661 | 31.04 | 28.687 | 29.163 | 601.969 | 26.61 | 27.554 | 1294.281 | 27.346 | 27.608 | 40.2 | 29.001 | 2.9 | 2.7 | 1.2 | 1.1 | 0.2
4249 | 30/07/2025 11:45:16.618 | 97.992 | 84 | 100 | 70 | 52 | 32.358 | 9.229 | 7.152 | 134.512 | 31.02 | 28.701 | 29.152 | 602.017 | 26.595 | 27.544 | 1292.018 | 27.359 | 27.598 | 40.065 | 29.001 | 1.4 | 2.5 | 0.1 | 0.5 | 0.2
4250 | 30/07/2025 11:45:18.256 | 98.28 | 84 | 100 | 70 | 52 | 31.991 | 9.285 | 7.153 | 134.845 | 31.018 | 28.686 | 29.134 | 601.9 | 26.608 | 27.565 | 1298.624 | 27.332 | 27.601 | 40.192 | 25.001 | 4 | 2 | 0.6 | 0.5 | 0.2
4251 | 30/07/2025 11:45:19.891 | 98.496 | 84 | 100 | 69 | 52 | 31.951 | 9.138 | 7.151 | 134.452 | 31.014 | 28.692 | 29.131 | 601.684 | 26.595 | 27.554 | 1302.14 | 27.345 | 27.604 | 40.422 | 28.001 | 1.8 | 3.9 | 1.2 | 0.6 | 0.3
4252 | 30/07/2025 11:45:21.525 | 98.232 | 84 | 100 | 70 | 52 | 32.624 | 9.128 | 7.136 | 134.555 | 31.002 | 28.671 | 29.13 | 601.748 | 26.596 | 27.566 | 1304.301 | 27.33 | 27.6 | 40.339 | 27.001 | 2.9 | 3.8 | 0.1 | 0.6 | 0.4
4253 | 30/07/2025 11:45:23.160 | 98.112 | 84 | 100 | 71 | 52 | 29.052 | 9.195 | 7.135 | 134.292 | 30.999 | 28.695 | 29.154 | 602.166 | 26.599 | 27.563 | 1307.717 | 27.345 | 27.601 | 40.216 | 27.001 | 2.9 | 3.8 | 0.1 | 0.6 | 0.4
4254 | 30/07/2025 11:45:24.794 | 98.088 | 84 | 100 | 70 | 52 | 29.81 | 9.134 | 7.135 | 134.608 | 30.992 | 28.691 | 29.136 | 602.018 | 26.586 | 27.575 | 1301.408 | 27.347 | 27.587 | 40.05 | 29.001 | 2.3 | 2.6 | 0.6 | 0.5 | 0.3
4255 | 30/07/2025 11:45:26.434 | 97.968 | 84 | 100 | 70 | 52 | 32.452 | 9.126 | 7.135 | 134.852 | 31.025 | 28.685 | 29.127 | 601.902 | 26.603 | 27.567 | 1313.783 | 27.319 | 27.611 | 40.118 | 24.001 | 2.1 | 4.4 | 0 | 0.5 | 0.3
4256 | 30/07/2025 11:45:28.069 | 98.016 | 82 | 100 | 71 | 52 | 28.844 | 9.131 | 7.134 | 134.597 | 31.023 | 28.686 | 29.111 | 601.76 | 26.594 | 27.573 | 1316.982 | 27.323 | 27.606 | 40.274 | 29.001 | 3.8 | 3.5 | 0.6 | 0.7 | 0.3
4257 | 30/07/2025 11:45:29.705 | 98.232 | 84 | 100 | 70 | 52 | 32.235 | 9.01 | 7.133 | 134.604 | 31.031 | 28.674 | 29.149 | 601.814 | 26.602 | 27.554 | 1317.057 | 27.342 | 27.601 | 40.421 | 31.001 | 3.7 | 3.5 | 0.6 | 0.7 | 0.3
4258 | 30/07/2025 11:45:31.339 | 98.424 | 83 | 100 | 70 | 52 | 32.454 | 8.998 | 7.152 | 134.235 | 31.041 | 28.698 | 29.141 | 602 | 26.594 | 27.557 | 1314.125 | 27.374 | 27.597 | 40.274 | 26.001 | 2.5 | 3 | 0.9 | 1.2 | 0.3
4259 | 30/07/2025 11:45:32.975 | 98.16 | 84 | 100 | 71 | 52 | 28.714 | 9.019 | 7.188 | 134.523 | 31.059 | 28.69 | 29.144 | 601.793 | 26.597 | 27.554 | 1306.389 | 27.346 | 27.585 | 40.238 | 26.001 | 2.5 | 3 | 0.9 | 1.2 | 0.3
4260 | 30/07/2025 11:45:34.609 | 97.776 | 86 | 100 | 70 | 52 | 30.553 | 9.134 | 7.162 | 134.794 | 31.046 | 28.686 | 29.137 | 601.909 | 26.581 | 27.536 | 1286.651 | 27.312 | 27.619 | 40.295 | 32.001 | 4.3 | 2.3 | 0.9 | 0.6 | 0.3
4261 | 30/07/2025 11:45:36.242 | 97.416 | 84 | 100 | 70 | 52 | 32.517 | 9.134 | 7.15 | 134.538 | 31.033 | 28.672 | 29.131 | 601.821 | 26.592 | 27.561 | 1284.625 | 27.344 | 27.604 | 40.227 | 32.001 | 4.3 | 2.5 | 0.9 | 0 | 0.3
4262 | 30/07/2025 11:45:37.878 | 97.104 | 84 | 99 | 70 | 52 | 29.462 | 9.135 | 7.151 | 134.572 | 31.026 | 28.676 | 29.151 | 601.947 | 26.587 | 27.547 | 1284.955 | 27.349 | 27.605 | 40.243 | 29.001 | 2.3 | 1.8 | 1.2 | 0 | 0.3
4263 | 30/07/2025 11:45:39.512 | 97.008 | 83 | 100 | 70 | 52 | 32.37 | 9.138 | 7.153 | 134.299 | 31.032 | 28.69 | 29.142 | 601.93 | 26.581 | 27.556 | 1276.533 | 27.352 | 27.582 | 40.187 | 26.001 | 3.3 | 2 | 0.7 | 0.5 | 0.2
4264 | 30/07/2025 11:45:41.148 | 97.896 | 84 | 100 | 70 | 52 | 32.049 | 9.131 | 7.151 | 134.748 | 31.039 | 28.682 | 29.132 | 601.955 | 26.594 | 27.538 | 1266.913 | 27.335 | 27.588 | 40.104 | 26.001 | 3.3 | 2 | 0.7 | 0.5 | 0.2
4265 | 30/07/2025 11:45:42.783 | 97.56 | 82 | 100 | 70 | 51 | 28.544 | 9.399 | 7.134 | 134.541 | 31.021 | 28.682 | 29.113 | 601.987 | 26.579 | 27.534 | 1270.792 | 27.337 | 27.612 | 40.373 | 28.001 | 3.7 | 3.5 | 1 | 1.4 | 0.2
4266 | 30/07/2025 11:45:44.416 | 97.704 | 83 | 100 | 69 | 52 | 31.12 | 9.135 | 7.135 | 134.452 | 31.021 | 28.675 | 29.14 | 601.685 | 26.574 | 27.531 | 1266.987 | 27.35 | 27.593 | 40.293 | 28.001 | 3.7 | 3.9 | 1 | 0.7 | 0.2
4267 | 30/07/2025 11:45:46.068 | 97.968 | 84 | 100 | 70 | 52 | 29.284 | 9.169 | 7.134 | 134.363 | 31.024 | 28.706 | 29.152 | 601.787 | 26.577 | 27.521 | 1267.146 | 27.362 | 27.598 | 40.282 | 24.001 | 2.3 | 3.3 | 1.5 | 0.7 | 0.2
4268 | 30/07/2025 11:45:47.704 | 98.04 | 84 | 100 | 70 | 52 | 29.911 | 9.25 | 7.153 | 134.708 | 31.035 | 28.694 | 29.138 | 601.887 | 26.595 | 27.547 | 1266.445 | 27.345 | 27.579 | 40.165 | 28.001 | 3.4 | 4.9 | 0.7 | 0.5 | 0.2
4269 | 30/07/2025 11:45:49.343 | 98.376 | 86 | 100 | 71 | 52 | 32.483 | 8.965 | 7.185 | 134.766 | 31.022 | 28.694 | 29.129 | 602.021 | 26.587 | 27.536 | 1267.399 | 27.342 | 27.603 | 40.382 | 24.001 | 2.5 | 3.3 | 0 | 0.5 | 0.2
4270 | 30/07/2025 11:45:50.980 | 97.992 | 85 | 100 | 70 | 52 | 31.601 | 9.133 | 7.186 | 134.307 | 31.021 | 28.679 | 29.13 | 601.96 | 26.582 | 27.551 | 1260.009 | 27.327 | 27.604 | 40.638 | 24.001 | 2.5 | 3.3 | 0 | 0.5 | 0.2
4271 | 30/07/2025 11:45:52.617 | 98.688 | 85 | 100 | 71 | 53 | 28.443 | 9.21 | 7.186 | 134.589 | 31.024 | 28.682 | 29.153 | 601.737 | 26.604 | 27.543 | 1266.554 | 27.349 | 27.592 | 40.229 | 24.001 | 1.9 | 4.2 | 0.9 | 0.2 | 0.1
4272 | 30/07/2025 11:45:54.252 | 98.592 | 85 | 100 | 70 | 52 | 31.514 | 9.136 | 7.187 | 134.434 | 31.005 | 28.703 | 29.154 | 602.052 | 26.593 | 27.563 | 1267.013 | 27.358 | 27.589 | 40.17 | 26.001 | 2.7 | 3.8 | 0.8 | 0.2 | 0.2
4273 | 30/07/2025 11:45:55.886 | 98.592 | 83 | 100 | 70 | 52 | 28.684 | 9.132 | 7.185 | 134.555 | 31.014 | 28.691 | 29.161 | 601.991 | 26.588 | 27.558 | 1267.026 | 27.349 | 27.584 | 39.993 | 27.001 | 4.3 | 3.6 | 0.7 | 0.7 | 0.2
4274 | 30/07/2025 11:45:57.521 | 98.712 | 85 | 100 | 69 | 52 | 30.393 | 8.985 | 7.186 | 134.667 | 30.992 | 28.697 | 29.126 | 602.014 | 26.592 | 27.554 | 1276.437 | 27.344 | 27.61 | 40.351 | 23.001 | 2.3 | 3.1 | 0.9 | 0.7 | 0.2
4275 | 30/07/2025 11:45:59.155 | 98.328 | 84 | 100 | 70 | 51 | 32.538 | 9.132 | 7.186 | 134.624 | 31.023 | 28.663 | 29.121 | 601.86 | 26.601 | 27.563 | 1274.976 | 27.329 | 27.587 | 40.44 | 23.001 | 2.3 | 3.1 | 0.9 | 0.7 | 0.2
4276 | 30/07/2025 11:46:00.790 | 98.208 | 84 | 100 | 70 | 51 | 30.882 | 9.219 | 7.203 | 134.415 | 31.02 | 28.693 | 29.15 | 601.989 | 26.593 | 27.545 | 1275.423 | 27.357 | 27.597 | 40.469 | 26.001 | 3.3 | 4.7 | 1 | 0.5 | 0.2
4277 | 30/07/2025 11:46:02.426 | 98.04 | 84 | 100 | 71 | 52 | 28.434 | 9.28 | 7.187 | 134.429 | 31.013 | 28.693 | 29.132 | 601.911 | 26.601 | 27.571 | 1275.405 | 27.348 | 27.591 | 40.058 | 26.001 | 2.2 | 3.2 | 0.9 | 0.5 | 0.2
4278 | 30/07/2025 11:46:04.095 | 97.872 | 84 | 100 | 71 | 51 | 31.904 | 9.287 | 7.169 | 135.041 | 31.049 | 28.692 | 29.129 | 603.196 | 26.614 | 27.546 | 1276.393 | 27.323 | 27.609 | 40.058 | 24.001 | 2.4 | 3.6 | 0.7 | 0 | 0.1
4279 | 30/07/2025 11:46:05.731 | 98.064 | 86 | 100 | 70 | 52 | 28.372 | 9.047 | 7.134 | 134.599 | 31.029 | 28.682 | 29.12 | 602.995 | 26.592 | 27.57 | 1284.556 | 27.314 | 27.596 | 40.398 | 27.001 | 2.7 | 5.8 | 0.6 | 0.6 | 0.2
4280 | 30/07/2025 11:46:07.365 | 98.064 | 84 | 100 | 71 | 52 | 31.019 | 9.101 | 7.134 | 134.802 | 31.037 | 28.673 | 29.152 | 602.056 | 26.595 | 27.544 | 1296.92 | 27.346 | 27.595 | 40.296 | 27.001 | 2.7 | 4.1 | 0.6 | 0.3 | 0.2
4281 | 30/07/2025 11:46:08.999 | 97.896 | 84 | 100 | 70 | 52 | 32.591 | 9.134 | 7.153 | 134.334 | 31.029 | 28.696 | 29.152 | 603.141 | 26.583 | 27.558 | 1301.598 | 27.367 | 27.599 | 40.236 | 27.001 | 2.7 | 4.1 | 0.6 | 0.3 | 0.2
4282 | 30/07/2025 11:46:10.635 | 97.536 | 84 | 100 | 70 | 52 | 30.234 | 9.137 | 7.181 | 134.653 | 31.041 | 28.688 | 29.141 | 602.999 | 26.594 | 27.548 | 1294.009 | 27.337 | 27.581 | 40.047 | 26.001 | 2.4 | 5.2 | 0.2 | 0 | 0.2
4283 | 30/07/2025 11:46:12.270 | 97.44 | 84 | 100 | 70 | 52 | 28.933 | 9.289 | 7.185 | 134.765 | 31.034 | 28.69 | 29.126 | 602.072 | 26.592 | 27.551 | 1286.951 | 27.321 | 27.616 | 40.262 | 26.001 | 2.4 | 3.8 | 0.2 | 0.5 | 0.2
4284 | 30/07/2025 11:46:13.906 | 97.872 | 83 | 100 | 70 | 52 | 31.552 | 9.287 | 7.187 | 134.541 | 31.045 | 28.679 | 29.112 | 601.882 | 26.59 | 27.548 | 1290.343 | 27.305 | 27.601 | 40.356 | 28.001 | 2 | 2.6 | 0.9 | 0.5 | 0.1
4285 | 30/07/2025 11:46:15.558 | 97.44 | 84 | 100 | 70 | 52 | 28.393 | 9.134 | 7.172 | 134.508 | 31.028 | 28.683 | 29.159 | 601.956 | 26.569 | 27.542 | 1287.24 | 27.357 | 27.617 | 40.245 | 25.001 | 2 | 2.8 | 0.4 | 0.5 | 0.2
4286 | 30/07/2025 11:46:17.193 | 97.608 | 84 | 100 | 70 | 52 | 31.6 | 9.134 | 7.136 | 134.336 | 31.018 | 28.697 | 29.143 | 601.672 | 26.579 | 27.552 | 1292.154 | 27.344 | 27.585 | 40.353 | 25.001 | 2 | 2.8 | 0.4 | 0.5 | 0.2
4287 | 30/07/2025 11:46:18.832 | 97.2 | 82 | 100 | 71 | 53 | 32.697 | 9.128 | 7.121 | 134.652 | 31.028 | 28.691 | 29.152 | 601.925 | 26.587 | 27.521 | 1280.09 | 27.342 | 27.58 | 40.186 | 26.001 | 2 | 3.2 | 0.6 | 0.5 | 0.2
4288 | 30/07/2025 11:46:20.469 | 96.864 | 84 | 100 | 71 | 52 | 29.913 | 9.209 | 7.12 | 134.545 | 31.022 | 28.687 | 29.13 | 601.892 | 26.586 | 27.537 | 1277.071 | 27.333 | 27.62 | 40.457 | 26.001 | 2 | 3.5 | 0.9 | 0.6 | 0.2
4289 | 30/07/2025 11:46:22.105 | 96.912 | 82 | 100 | 70 | 52 | 29.36 | 9.228 | 7.122 | 134.562 | 31.021 | 28.672 | 29.147 | 601.847 | 26.602 | 27.539 | 1269.875 | 27.343 | 27.596 | 40.178 | 24.001 | 1.9 | 4.2 | 0.6 | 0.8 | 0.2
4290 | 30/07/2025 11:46:23.740 | 97.368 | 84 | 100 | 70 | 53 | 31.103 | 9.183 | 7.122 | 134.451 | 31.026 | 28.686 | 29.154 | 601.862 | 26.592 | 27.548 | 1270.048 | 27.356 | 27.608 | 40.191 | 24.001 | 1.9 | 2.8 | 0.6 | 0.6 | 0.2
4291 | 30/07/2025 11:46:25.375 | 97.176 | 82 | 100 | 69 | 52 | 28.583 | 9.213 | 7.151 | 134.588 | 31.017 | 28.69 | 29.143 | 601.777 | 26.61 | 27.55 | 1266.984 | 27.351 | 27.584 | 40.04 | 25.001 | 2.9 | 1.6 | 0.7 | 0.6 | 0.2
4292 | 30/07/2025 11:46:27.009 | 97.104 | 82 | 100 | 70 | 52 | 32 | 9.183 | 7.152 | 134.713 | 31.022 | 28.693 | 29.14 | 602.105 | 26.594 | 27.542 | 1264.564 | 27.339 | 27.622 | 40.203 | 25.001 | 2.9 | 1.6 | 0.7 | 0.6 | 0.2
4293 | 30/07/2025 11:46:28.644 | 97.272 | 83 | 100 | 70 | 53 | 32.731 | 9.225 | 7.149 | 134.527 | 31.013 | 28.673 | 29.121 | 601.8 | 26.595 | 27.561 | 1269.061 | 27.319 | 27.6 | 40.301 | 28.001 | 1.1 | 2.3 | 0.6 | 0.1 | 0.2
4294 | 30/07/2025 11:46:30.280 | 97.512 | 83 | 100 | 70 | 53 | 29.187 | 9.21 | 7.131 | 134.573 | 31.018 | 28.683 | 29.164 | 601.933 | 26.603 | 27.559 | 1286.259 | 27.344 | 27.595 | 40.175 | 26.001 | 1.2 | 4.3 | 0.1 | 0.1 | 0.2
4295 | 30/07/2025 11:46:31.915 | 97.368 | 84 | 100 | 70 | 52 | 32.687 | 9.275 | 7.137 | 134.375 | 31.017 | 28.693 | 29.155 | 601.88 | 26.599 | 27.578 | 1294.141 | 27.344 | 27.594 | 40.11 | 29.001 | 2.7 | 3.1 | 0.6 | 0.7 | 0.2
4296 | 30/07/2025 11:46:33.551 | 97.512 | 84 | 100 | 70 | 52 | 30.34 | 9.232 | 7.135 | 134.654 | 31.006 | 28.692 | 29.151 | 602.013 | 26.581 | 27.552 | 1301.564 | 27.351 | 27.579 | 39.88 | 25.001 | 2.6 | 4.5 | 1.3 | 0.6 | 0.2
4297 | 30/07/2025 11:46:35.187 | 97.152 | 83 | 100 | 70 | 52 | 28.766 | 8.985 | 7.147 | 134.552 | 31.013 | 28.7 | 29.128 | 601.902 | 26.584 | 27.572 | 1301.696 | 27.337 | 27.612 | 40.251 | 25.001 | 2.6 | 4.5 | 1.3 | 0.6 | 0.2
4298 | 30/07/2025 11:46:36.825 | 97.32 | 83 | 100 | 69 | 51 | 32.204 | 9.282 | 7.15 | 134.625 | 31.041 | 28.667 | 29.12 | 601.744 | 26.608 | 27.56 | 1304.778 | 27.322 | 27.598 | 40.191 | 25.001 | 2.6 | 4.2 | 1.3 | 0.1 | 0.2
4299 | 30/07/2025 11:46:38.459 | 97.032 | 82 | 100 | 71 | 52 | 32.461 | 9.14 | 7.203 | 133.033 | 31.02 | 28.689 | 29.138 | 602.073 | 26.579 | 27.552 | 1317.116 | 27.363 | 27.604 | 40.263 | 27.001 | 3.8 | 2 | 0.6 | 0.1 | 0.2
4300 | 30/07/2025 11:46:40.094 | 97.152 | 84 | 100 | 70 | 52 | 28.639 | 8.989 | 7.188 | 133.003 | 31.033 | 28.69 | 29.131 | 602.957 | 26.59 | 27.557 | 1305.87 | 27.339 | 27.571 | 40.167 | 28.001 | 1.9 | 4.9 | 0.3 | 0.5 | 0.2
4301 | 30/07/2025 11:46:41.729 | 97.584 | 84 | 100 | 70 | 52 | 32.697 | 9.212 | 7.186 | 133.154 | 31.043 | 28.698 | 29.153 | 603.08 | 26.589 | 27.546 | 1302.004 | 27.355 | 27.592 | 40.058 | 28.001 | 1.4 | 2.6 | 0 | 0.5 | 0.2
4302 | 30/07/2025 11:46:43.367 | 97.032 | 83 | 100 | 71 | 51 | 29.603 | 8.991 | 7.136 | 132.987 | 31.037 | 28.689 | 29.112 | 603.147 | 26.595 | 27.567 | 1294.195 | 27.311 | 27.603 | 40.389 | 25.001 | 4.2 | 3 | 0 | 0 | 0.2
4303 | 30/07/2025 11:46:45.002 | 97.224 | 83 | 100 | 68 | 52 | 29.352 | 9.286 | 7.133 | 133.227 | 31.023 | 28.677 | 29.141 | 603.232 | 26.586 | 27.536 | 1288.023 | 27.344 | 27.598 | 40.398 | 25.001 | 4.2 | 3 | 0 | 0 | 0.2
4304 | 30/07/2025 11:46:46.638 | 97.488 | 82 | 100 | 71 | 52 | 32.372 | 9.232 | 7.152 | 132.945 | 31.047 | 28.702 | 29.14 | 603.146 | 26.589 | 27.563 | 1282.763 | 27.353 | 27.605 | 40.108 | 28.001 | 4.2 | 3.6 | 0.9 | 0 | 0.2
4305 | 30/07/2025 11:46:48.274 | 97.128 | 83 | 100 | 70 | 52 | 32.083 | 9.224 | 7.096 | 133.119 | 31.032 | 28.69 | 29.131 | 603.031 | 26.591 | 27.555 | 1289.886 | 27.342 | 27.582 | 40.032 | 28.001 | 4.2 | 2.3 | 0.9 | 0.5 | 0.2
4306 | 30/07/2025 11:46:49.909 | 97.368 | 84 | 100 | 71 | 52 | 31.959 | 9.089 | 7.09 | 133.112 | 31.024 | 28.691 | 29.13 | 603.064 | 26.584 | 27.552 | 1300.885 | 27.34 | 27.609 | 40.108 | 20.001 | 1.8 | 2.9 | 1.8 | 0.5 | 0.2
4307 | 30/07/2025 11:46:51.544 | 98.136 | 83 | 100 | 70 | 52 | 32.725 | 8.891 | 7.085 | 133.257 | 31.038 | 28.682 | 29.117 | 603.188 | 26.589 | 27.54 | 1311.5 | 27.296 | 27.607 | 40.201 | 23.001 | 2 | 3.2 | 2 | 0.6 | 0.3
4308 | 30/07/2025 11:46:53.178 | 98.376 | 83 | 99 | 69 | 52 | 29.359 | 9.205 | 7.085 | 133.097 | 31.025 | 28.671 | 29.144 | 603.221 | 26.573 | 27.524 | 1317.253 | 27.366 | 27.604 | 40.208 | 23.001 | 2 | 3.2 | 2 | 0.6 | 0.3
4309 | 30/07/2025 11:46:54.851 | 98.376 | 84 | 100 | 70 | 53 | 30.05 | 9.133 | 7.126 | 132.884 | 31.025 | 28.699 | 29.144 | 603.05 | 26.586 | 27.543 | 1306.599 | 27.344 | 27.584 | 40.195 | 27.001 | 1.6 | 2.4 | 0.9 | 0.6 | 0.3
4310 | 30/07/2025 11:46:56.487 | 98.016 | 84 | 100 | 71 | 52 | 32.445 | 9.1 | 7.131 | 133.215 | 31.033 | 28.694 | 29.145 | 604.107 | 26.591 | 27.521 | 1300.136 | 27.341 | 27.594 | 40.113 | 29.001 | 3.2 | 3.9 | 0.8 | 0.5 | 0.3
4311 | 30/07/2025 11:46:58.121 | 97.8 | 84 | 100 | 70 | 52 | 31.681 | 8.999 | 7.134 | 133.122 | 31.028 | 28.7 | 29.131 | 605.634 | 26.601 | 27.55 | 1315.671 | 27.328 | 27.604 | 40.469 | 27.001 | 2.1 | 5.2 | 0.6 | 0.5 | 0.3
4312 | 30/07/2025 11:46:59.755 | 97.752 | 82 | 100 | 70 | 52 | 32.263 | 8.986 | 7.133 | 133.153 | 31.023 | 28.678 | 29.128 | 606.908 | 26.596 | 27.556 | 1314.709 | 27.326 | 27.615 | 40.21 | 27.001 | 2.1 | 4.7 | 0.6 | 0.9 | 0.3
4313 | 30/07/2025 11:47:01.390 | 98.352 | 84 | 100 | 71 | 52 | 32.484 | 8.994 | 7.134 | 133.087 | 31.007 | 28.683 | 29.146 | 607.916 | 26.596 | 27.565 | 1302.972 | 27.359 | 27.603 | 40.288 | 26.001 | 2.8 | 4.3 | 0.3 | 0.2 | 0.3
4314 | 30/07/2025 11:47:03.025 | 98.64 | 84 | 100 | 70 | 53 | 28.763 | 8.991 | 7.186 | 133.154 | 31.033 | 28.691 | 29.155 | 608.036 | 26.594 | 27.564 | 1289.648 | 27.343 | 27.591 | 40.006 | 26.001 | 2.8 | 4.3 | 0.3 | 0.2 | 0.3
4315 | 30/07/2025 11:47:04.701 | 98.688 | 85 | 100 | 70 | 52 | 30.475 | 8.975 | 7.188 | 133.237 | 30.999 | 28.687 | 29.142 | 606.999 | 26.587 | 27.574 | 1287.153 | 27.342 | 27.618 | 40.115 | 26.001 | 2.8 | 3.5 | 0.3 | 0 | 0.3
4316 | 30/07/2025 11:47:06.336 | 98.856 | 85 | 100 | 71 | 52 | 32.575 | 9.133 | 7.186 | 133.233 | 30.993 | 28.671 | 29.108 | 606.777 | 26.588 | 27.562 | 1279.748 | 27.305 | 27.605 | 40.249 | 23.001 | 2.6 | 3.7 | 0.6 | 0.5 | 0.3
4317 | 30/07/2025 11:47:07.970 | 99.12 | 83 | 100 | 70 | 53 | 31.081 | 8.984 | 7.185 | 133.001 | 31.022 | 28.678 | 29.152 | 606.941 | 26.597 | 27.548 | 1267.601 | 27.347 | 27.596 | 40.222 | 23.001 | 2.6 | 3.3 | 0.6 | 0.6 | 0.3
4318 | 30/07/2025 11:47:09.604 | 99.24 | 85 | 100 | 71 | 52 | 32.353 | 9.132 | 7.187 | 132.86 | 31.019 | 28.696 | 29.144 | 607.635 | 26.592 | 27.554 | 1260.058 | 27.349 | 27.581 | 40.398 | 27.001 | 3.5 | 3 | 0.9 | 0.6 | 0.3
4319 | 30/07/2025 11:47:11.242 | 99.072 | 84 | 100 | 70 | 53 | 32.119 | 9.436 | 7.186 | 133.267 | 31.034 | 28.693 | 29.142 | 608.131 | 26.575 | 27.543 | 1257.698 | 27.348 | 27.581 | 40.145 | 27.001 | 3.5 | 3 | 0.9 | 0.6 | 0.3
4320 | 30/07/2025 11:47:12.876 | 99.072 | 84 | 100 | 70 | 52 | 28.442 | 9.13 | 7.142 | 133.167 | 31.038 | 28.687 | 29.12 | 608.037 | 26.592 | 27.569 | 1262.324 | 27.344 | 27.621 | 40.421 | 29.001 | 3.3 | 3.2 | 1 | 0.5 | 0.3
4321 | 30/07/2025 11:47:14.511 | 99.192 | 84 | 100 | 70 | 52 | 30.973 | 9.137 | 7.134 | 133.238 | 31.051 | 28.669 | 29.126 | 608.035 | 26.606 | 27.561 | 1271.657 | 27.322 | 27.605 | 40.339 | 26.001 | 3.1 | 2.2 | 0.6 | 0.5 | 0.3
4322 | 30/07/2025 11:47:16.153 | 99.864 | 86 | 100 | 71 | 52 | 32.621 | 9.114 | 7.086 | 132.955 | 31.033 | 28.687 | 29.145 | 608.006 | 26.588 | 27.558 | 1274.732 | 27.371 | 27.614 | 40.337 | 25.001 | 1.4 | 2.4 | 0 | 0.5 | 0.3
4323 | 30/07/2025 11:47:17.790 | 99.816 | 84 | 100 | 70 | 52 | 29.837 | 9.029 | 7.087 | 133.046 | 31.056 | 28.701 | 29.144 | 608.1 | 26.594 | 27.54 | 1272.813 | 27.348 | 27.582 | 40.162 | 33.001 | 1.7 | 4.1 | 1.2 | 0.6 | 0.3
4324 | 30/07/2025 11:47:19.424 | 100.152 | 85 | 100 | 71 | 50 | 32.464 | 9.013 | 7.084 | 133.083 | 31.014 | 28.693 | 29.132 | 608.056 | 26.58 | 27.547 | 1276.483 | 27.364 | 27.589 | 40.105 | 33.001 | 1.7 | 5.9 | 1.2 | 0.5 | 0.3
4325 | 30/07/2025 11:47:21.060 | 99.768 | 85 | 100 | 70 | 52 | 31.424 | 8.987 | 7.09 | 133.116 | 31.043 | 28.692 | 29.121 | 607.824 | 26.576 | 27.553 | 1282.265 | 27.319 | 27.606 | 40.46 | 33.001 | 1.7 | 5.9 | 1.2 | 0.5 | 0.3
4326 | 30/07/2025 11:47:22.694 | 100.128 | 86 | 100 | 71 | 53 | 28.364 | 8.988 | 7.085 | 133.179 | 31.028 | 28.676 | 29.143 | 608.249 | 26.574 | 27.528 | 1285.128 | 27.338 | 27.601 | 40.437 | 28.001 | 2 | 4.3 | 0.9 | 0.5 | 0.2
4327 | 30/07/2025 11:47:24.331 | 100.176 | 86 | 100 | 70 | 52 | 31.54 | 9.136 | 7.134 | 132.967 | 31.035 | 28.696 | 29.138 | 607.922 | 26.595 | 27.555 | 1283.626 | 27.361 | 27.595 | 40.291 | 28.001 | 2 | 3.9 | 0.9 | 1.4 | 0.2
4328 | 30/07/2025 11:47:25.967 | 100.368 | 86 | 99 | 69 | 52 | 28.722 | 9.134 | 7.134 | 133.196 | 31.025 | 28.692 | 29.157 | 608.109 | 26.584 | 27.532 | 1279.77 | 27.358 | 27.599 | 40.166 | 30.001 | 2.9 | 5.6 | 0 | 0.3 | 0.2
4329 | 30/07/2025 11:47:27.601 | 99.744 | 85 | 100 | 70 | 52 | 30.534 | 9.133 | 7.136 | 133.229 | 31.028 | 28.691 | 29.129 | 607.926 | 26.564 | 27.529 | 1281.946 | 27.342 | 27.615 | 40.014 | 30.001 | 2.9 | 3.6 | 0 | 0 | 0.2
4330 | 30/07/2025 11:47:29.235 | 99.576 | 84 | 100 | 70 | 52 | 32.557 | 9.13 | 7.125 | 133.289 | 31.029 | 28.684 | 29.112 | 607.885 | 26.591 | 27.528 | 1284.595 | 27.32 | 27.607 | 40.253 | 30.001 | 2.9 | 3.6 | 0 | 0 | 0.2
4331 | 30/07/2025 11:47:30.870 | 99.672 | 85 | 100 | 70 | 51 | 31.092 | 9.241 | 7.12 | 133.28 | 31.024 | 28.671 | 29.151 | 609.335 | 26.581 | 27.522 | 1284.996 | 27.371 | 27.603 | 40.402 | 26.001 | 2.2 | 2.9 | 0.9 | 0 | 0.1
4332 | 30/07/2025 11:47:32.501 | 99.576 | 84 | 100 | 70 | 52 | 28.623 | 9.157 | 7.123 | 133.028 | 31.015 | 28.7 | 29.142 | 609.15 | 26.599 | 27.554 | 1282.125 | 27.346 | 27.594 | 40.218 | 26.001 | 2.2 | 3.1 | 0.9 | 0.5 | 0.1
4333 | 30/07/2025 11:47:34.135 | 99.408 | 86 | 100 | 72 | 52 | 32.014 | 9.232 | 7.132 | 133.293 | 31.025 | 28.693 | 29.146 | 609.408 | 26.596 | 27.538 | 1287.029 | 27.348 | 27.591 | 39.916 | 27.001 | 1 | 3.9 | 0.4 | 0.5 | 0.1
4334 | 30/07/2025 11:47:35.771 | 99.312 | 86 | 100 | 70 | 52 | 28.501 | 9.416 | 7.185 | 133.412 | 31.019 | 28.689 | 29.128 | 609.165 | 26.623 | 27.573 | 1286.753 | 27.335 | 27.61 | 40.141 | 27.001 | 1.1 | 3.3 | 1.3 | 0.8 | 0.1
4335 | 30/07/2025 11:47:37.407 | 99.408 | 85 | 100 | 70 | 52 | 31.085 | 9.197 | 7.185 | 133.091 | 31.018 | 28.682 | 29.115 | 609.175 | 26.591 | 27.562 | 1282.324 | 27.32 | 27.618 | 40.388 | 30.001 | 3.1 | 3.1 | 0.7 | 0.8 | 0.1
4336 | 30/07/2025 11:47:39.042 | 99.288 | 86 | 100 | 71 | 52 | 32.663 | 9.298 | 7.186 | 134.489 | 30.996 | 28.671 | 29.146 | 609.182 | 26.584 | 27.572 | 1287.189 | 27.359 | 27.601 | 40.277 | 30.001 | 3.1 | 3.1 | 0.7 | 0.8 | 0.1
4337 | 30/07/2025 11:47:40.678 | 99.168 | 84 | 100 | 68 | 51 | 30.512 | 9.134 | 7.151 | 134.522 | 31.016 | 28.689 | 29.145 | 609.297 | 26.595 | 27.556 | 1287.423 | 27.348 | 27.578 | 40.202 | 28.001 | 3.8 | 3.6 | 1.5 | 0.1 | 0.1
4338 | 30/07/2025 11:47:42.315 | 98.064 | 86 | 100 | 71 | 52 | 28.826 | 9.288 | 7.129 | 134.658 | 31.017 | 28.694 | 29.139 | 609.29 | 26.598 | 27.571 | 1283.124 | 27.357 | 27.605 | 39.863 | 25.001 | 1.6 | 1.5 | 0.3 | 0.1 | 0.1
4339 | 30/07/2025 11:47:43.950 | 97.728 | 84 | 100 | 70 | 52 | 31.73 | 9.069 | 7.069 | 134.674 | 31.016 | 28.687 | 29.136 | 609.288 | 26.59 | 27.546 | 1282.103 | 27.327 | 27.597 | 40.273 | 29.001 | 2.3 | 2.4 | 0.6 | 0.6 | 0.2
4340 | 30/07/2025 11:47:45.587 | 97.992 | 84 | 100 | 70 | 52 | 28.436 | 9.02 | 7.079 | 134.639 | 31.029 | 28.672 | 29.122 | 610.378 | 26.596 | 27.562 | 1279.622 | 27.336 | 27.607 | 40.419 | 28.001 | 2.1 | 2.9 | 1.3 | 0.6 | 0.2
4341 | 30/07/2025 11:47:47.223 | 98.088 | 84 | 100 | 72 | 52 | 31.551 | 9.133 | 7.123 | 134.609 | 31.042 | 28.687 | 29.144 | 610.528 | 26.605 | 27.56 | 1279.181 | 27.359 | 27.596 | 40.172 | 28.001 | 2.1 | 2.9 | 1.3 | 0.6 | 0.2
4342 | 30/07/2025 11:47:48.859 | 98.208 | 85 | 100 | 70 | 52 | 32.723 | 9.294 | 7.121 | 134.589 | 31.037 | 28.699 | 29.151 | 610.611 | 26.58 | 27.551 | 1274.19 | 27.345 | 27.584 | 40.018 | 27.001 | 1.1 | 3.8 | 1.3 | 0.8 | 0.2
4343 | 30/07/2025 11:47:50.495 | 97.8 | 82 | 100 | 70 | 52 | 29.679 | 8.989 | 7.122 | 134.593 | 31.024 | 28.681 | 29.128 | 610.433 | 26.591 | 27.56 | 1266.786 | 27.327 | 27.608 | 40.365 | 23.001 | 2.7 | 3.7 | 2.3 | 0.8 | 0.2
4344 | 30/07/2025 11:47:52.128 | 98.088 | 84 | 100 | 70 | 52 | 29.292 | 8.981 | 7.121 | 134.646 | 31.044 | 28.676 | 29.104 | 611.73 | 26.586 | 27.539 | 1269.636 | 27.319 | 27.602 | 40.229 | 25.001 | 1.9 | 1.1 | 1.7 | 1.2 | 0.2
4345 | 30/07/2025 11:47:53.764 | 97.68 | 82 | 100 | 70 | 52 | 30.916 | 9.087 | 7.12 | 134.378 | 31.025 | 28.673 | 29.125 | 611.6 | 26.573 | 27.552 | 1267.606 | 27.343 | 27.585 | 40.202 | 20.001 | 4 | 3.5 | 0.6 | 1.2 | 0.2
4346 | 30/07/2025 11:47:55.400 | 98.088 | 83 | 100 | 72 | 52 | 28.484 | 9.234 | 7.122 | 134.4 | 31.036 | 28.696 | 29.157 | 610.53 | 26.583 | 27.536 | 1267.265 | 27.35 | 27.582 | 40.104 | 26.001 | 3.2 | 2.3 | 0.7 | 0.5 | 0.2
4347 | 30/07/2025 11:47:57.034 | 98.088 | 86 | 100 | 70 | 52 | 31.914 | 9.135 | 7.122 | 134.616 | 31.023 | 28.702 | 29.139 | 610.59 | 26.585 | 27.536 | 1266.544 | 27.367 | 27.588 | 39.995 | 26.001 | 3.2 | 2.3 | 0.7 | 0.5 | 0.2
4348 | 30/07/2025 11:47:58.673 | 98.352 | 83 | 100 | 70 | 52 | 32.713 | 8.985 | 7.106 | 134.66 | 31.027 | 28.686 | 29.13 | 610.434 | 26.584 | 27.543 | 1267.687 | 27.322 | 27.608 | 40.396 | 27.001 | 1.9 | 4.7 | 0.9 | 0.5 | 0.2
4349 | 30/07/2025 11:48:00.310 | 98.616 | 84 | 100 | 71 | 52 | 29.238 | 9.143 | 7.081 | 134.721 | 31.036 | 28.674 | 29.14 | 610.525 | 26.571 | 27.534 | 1271.846 | 27.328 | 27.611 | 40.448 | 25.001 | 2.8 | 2.2 | 0.7 | 0 | 0.2
4350 | 30/07/2025 11:48:01.945 | 98.184 | 84 | 100 | 71 | 52 | 32.656 | 9.163 | 7.087 | 134.551 | 31.037 | 28.675 | 29.144 | 610.47 | 26.586 | 27.524 | 1274.333 | 27.352 | 27.592 | 40.451 | 25.001 | 2.1 | 3.1 | 0.6 | 0.5 | 0.2
4351 | 30/07/2025 11:48:03.580 | 98.088 | 84 | 100 | 70 | 52 | 30.403 | 9.136 | 7.085 | 134.484 | 31.013 | 28.697 | 29.14 | 611.717 | 26.575 | 27.518 | 1257.844 | 27.357 | 27.598 | 40.278 | 25.001 | 2.1 | 2.2 | 0.6 | 0.6 | 0.2
4352 | 30/07/2025 11:48:05.215 | 98.4 | 84 | 100 | 69 | 52 | 28.936 | 9.289 | 7.059 | 134.569 | 31.022 | 28.687 | 29.137 | 612.908 | 26.593 | 27.555 | 1257.295 | 27.337 | 27.603 | 40.1 | 25.001 | 2.1 | 2.2 | 0.6 | 0.6 | 0.2
4353 | 30/07/2025 11:48:06.849 | 98.544 | 84 | 100 | 70 | 52 | 32.229 | 9.134 | 7.058 | 134.692 | 31.025 | 28.689 | 29.123 | 612.903 | 26.597 | 27.553 | 1264.843 | 27.316 | 27.618 | 40.456 | 26.001 | 1.5 | 3.3 | 1.5 | 0.6 | 0.1
4354 | 30/07/2025 11:48:08.484 | 98.232 | 84 | 100 | 70 | 52 | 32.489 | 9.207 | 7.068 | 134.545 | 31.011 | 28.672 | 29.129 | 612.953 | 26.593 | 27.547 | 1267.348 | 27.364 | 27.588 | 40.343 | 27.001 | 1.1 | 3.5 | 0.9 | 0.6 | 0.3
4355 | 30/07/2025 11:48:10.122 | 98.64 | 84 | 100 | 70 | 52 | 28.719 | 8.986 | 7.086 | 134.425 | 31.013 | 28.697 | 29.135 | 612.94 | 26.616 | 27.559 | 1267.947 | 27.347 | 27.591 | 38.764 | 25.001 | 1.9 | 2.8 | 0.9 | 0.6 | 0.3
4356 | 30/07/2025 11:48:11.763 | 98.592 | 84 | 100 | 71 | 52 | 32.736 | 8.986 | 7.085 | 134.253 | 31.009 | 28.687 | 29.134 | 612.949 | 26.589 | 27.577 | 1266.704 | 27.358 | 27.595 | 38.697 | 24.001 | 3.1 | 2 | 0.6 | 0.6 | 0.2
4357 | 30/07/2025 11:48:13.395 | 98.832 | 84 | 100 | 71 | 52 | 29.806 | 8.994 | 7.171 | 134.755 | 31.012 | 28.685 | 29.124 | 612.877 | 26.604 | 27.559 | 1276.533 | 27.339 | 27.593 | 38.145 | 26.001 | 2.1 | 2.4 | 0.9 | 0.6 | 0.2
4358 | 30/07/2025 11:48:15.029 | 99.096 | 85 | 100 | 70 | 52 | 29.404 | 8.984 | 7.185 | 134.519 | 31.001 | 28.68 | 29.107 | 612.973 | 26.592 | 27.554 | 1287.498 | 27.324 | 27.6 | 38.486 | 26.001 | 2.1 | 2.4 | 0.9 | 0.6 | 0.2
4359 | 30/07/2025 11:48:16.663 | 98.28 | 84 | 100 | 70 | 53 | 32.403 | 9.137 | 7.186 | 134.531 | 31.017 | 28.673 | 29.151 | 612.879 | 26.602 | 27.57 | 1286.455 | 27.343 | 27.611 | 38.461 | 30.001 | 2.2 | 3.7 | 1 | 0 | 0.2
4360 | 30/07/2025 11:48:18.307 | 98.304 | 84 | 100 | 70 | 52 | 32.214 | 9.135 | 7.186 | 134.481 | 31.034 | 28.692 | 29.151 | 612.872 | 26.592 | 27.548 | 1287.126 | 27.342 | 27.582 | 40.093 | 26.001 | 3.1 | 3.7 | 1.2 | 0 | 0.2
4361 | 30/07/2025 11:48:19.944 | 98.232 | 84 | 100 | 70 | 52 | 31.97 | 9.265 | 7.188 | 134.629 | 31.022 | 28.686 | 29.138 | 612.874 | 26.596 | 27.558 | 1282.657 | 27.342 | 27.563 | 40.113 | 26.001 | 3.1 | 4 | 1.2 | 0.5 | 0.2
4362 | 30/07/2025 11:48:21.580 | 98.472 | 84 | 100 | 71 | 52 | 32.721 | 8.983 | 7.185 | 134.773 | 31.025 | 28.692 | 29.142 | 613.863 | 26.587 | 27.551 | 1274.231 | 27.328 | 27.609 | 40.095 | 22.001 | 2.9 | 3.5 | 1 | 0 | 0.2
4363 | 30/07/2025 11:48:23.214 | 98.496 | 84 | 100 | 70 | 52 | 29.239 | 9.131 | 7.185 | 134.626 | 31.042 | 28.682 | 29.123 | 612.905 | 26.588 | 27.555 | 1274.749 | 27.334 | 27.607 | 40.372 | 22.001 | 2.9 | 3.5 | 1 | 0 | 0.2
4364 | 30/07/2025 11:48:24.851 | 98.376 | 84 | 100 | 70 | 53 | 29.852 | 9.206 | 7.188 | 134.638 | 31.044 | 28.687 | 29.142 | 614.171 | 26.595 | 27.552 | 1269.613 | 27.348 | 27.596 | 40.281 | 22.001 | 2.9 | 4.3 | 1 | 0.5 | 0.2
4365 | 30/07/2025 11:48:26.485 | 98.376 | 83 | 100 | 70 | 52 | 32.466 | 9.136 | 7.203 | 134.552 | 31.042 | 28.703 | 29.149 | 612.991 | 26.589 | 27.548 | 1267.267 | 27.354 | 27.595 | 40.379 | 26.001 | 5.1 | 2.1 | 1 | 0.7 | 0.1
4366 | 30/07/2025 11:48:28.119 | 97.968 | 84 | 100 | 71 | 52 | 31.58 | 8.989 | 7.204 | 134.652 | 31.032 | 28.685 | 29.139 | 612.988 | 26.582 | 27.566 | 1269.396 | 27.336 | 27.61 | 40.282 | 26.001 | 5.1 | 4.2 | 1 | 1.4 | 0.1
4367 | 30/07/2025 11:48:29.750 | 97.896 | 84 | 100 | 70 | 51 | 32.225 | 8.988 | 7.188 | 134.625 | 31.033 | 28.69 | 29.126 | 612.971 | 26.579 | 27.551 | 1277.027 | 27.338 | 27.618 | 40.302 | 25.001 | 2.3 | 2.7 | 1.2 | 1.4 | 0.2
4368 | 30/07/2025 11:48:31.387 | 97.896 | 84 | 100 | 70 | 52 | 32.472 | 9.405 | 7.187 | 134.747 | 31.027 | 28.672 | 29.132 | 612.988 | 26.587 | 27.55 | 1281.447 | 27.335 | 27.599 | 40.168 | 25.001 | 2.3 | 4 | 1.2 | 0.1 | 0.2
4369 | 30/07/2025 11:48:33.021 | 97.944 | 85 | 100 | 71 | 52 | 28.832 | 8.945 | 7.151 | 134.568 | 31.03 | 28.702 | 29.156 | 612.983 | 26.579 | 27.529 | 1277.136 | 27.345 | 27.597 | 40.083 | 25.001 | 2.3 | 4 | 1.2 | 0.1 | 0.2
4370 | 30/07/2025 11:48:34.657 | 98.064 | 84 | 100 | 71 | 52 | 30.479 | 9.134 | 7.134 | 134.587 | 31.023 | 28.698 | 29.148 | 612.971 | 26.578 | 27.534 | 1274.323 | 27.352 | 27.595 | 40.007 | 27.001 | 2.7 | 3.2 | 0.6 | 0.1 | 0.1
4371 | 30/07/2025 11:48:36.290 | 97.8 | 83 | 100 | 70 | 52 | 32.563 | 8.839 | 7.136 | 134.785 | 31.028 | 28.679 | 29.114 | 612.835 | 26.6 | 27.531 | 1267.244 | 27.318 | 27.606 | 40.26 | 29.001 | 1.1 | 4.7 | 0.9 | 0.7 | 0.1
4372 | 30/07/2025 11:48:37.924 | 97.752 | 84 | 100 | 70 | 52 | 29.353 | 8.847 | 7.134 | 134.578 | 31.017 | 28.682 | 29.1 | 612.855 | 26.59 | 27.534 | 1269.76 | 27.32 | 27.594 | 40.421 | 25.001 | 2.9 | 3.7 | 0.9 | 0.5 | 0.2
4373 | 30/07/2025 11:48:39.558 | 97.416 | 83 | 100 | 71 | 52 | 32.346 | 9.134 | 7.135 | 134.659 | 31.035 | 28.677 | 29.15 | 613.04 | 26.605 | 27.549 | 1276.888 | 27.35 | 27.612 | 40.087 | 25.001 | 2.9 | 2.8 | 0.9 | 0 | 0.2
4374 | 30/07/2025 11:48:41.190 | 97.44 | 83 | 100 | 71 | 52 | 32.067 | 9.29 | 7.134 | 134.378 | 31.021 | 28.71 | 29.133 | 612.946 | 26.597 | 27.556 | 1277.01 | 27.372 | 27.595 | 40.152 | 25.001 | 2.9 | 2.8 | 0.9 | 0 | 0.2
4375 | 30/07/2025 11:48:42.825 | 97.536 | 82 | 100 | 69 | 52 | 28.429 | 8.989 | 7.136 | 134.65 | 31.017 | 28.693 | 29.135 | 611.702 | 26.599 | 27.553 | 1276.646 | 27.333 | 27.587 | 38.383 | 23.001 | 2.3 | 2 | 1 | 0.5 | 0.2
4376 | 30/07/2025 11:48:44.460 | 97.584 | 84 | 100 | 70 | 52 | 30.981 | 9.207 | 7.133 | 134.779 | 31.011 | 28.693 | 29.129 | 610.575 | 26.592 | 27.55 | 1273.103 | 27.319 | 27.626 | 38.389 | 23.001 | 2.3 | 1.1 | 1 | 0.6 | 0.2
4377 | 30/07/2025 11:48:46.095 | 97.344 | 84 | 100 | 70 | 52 | 29.219 | 9.157 | 7.136 | 134.696 | 30.999 | 28.671 | 29.124 | 610.355 | 26.606 | 27.562 | 1271.614 | 27.324 | 27.595 | 40.229 | 31.001 | 3.4 | 2.4 | 1.4 | 0.6 | 0.2
4378 | 30/07/2025 11:48:47.732 | 97.464 | 84 | 100 | 70 | 52 | 29.873 | 9.13 | 7.135 | 134.552 | 30.998 | 28.686 | 29.141 | 610.528 | 26.582 | 27.56 | 1271.687 | 27.356 | 27.596 | 40.141 | 31.001 | 3.4 | 4.4 | 1.4 | 0.5 | 0.2
4379 | 30/07/2025 11:48:49.369 | 97.008 | 82 | 100 | 71 | 52 | 32.469 | 9.214 | 7.187 | 134.42 | 31.014 | 28.697 | 29.13 | 609.247 | 26.591 | 27.571 | 1264.497 | 27.354 | 27.581 | 39.976 | 28.001 | 3.5 | 4.1 | 1.5 | 0.6 | 0.2
4380 | 30/07/2025 11:48:51.003 | 97.2 | 83 | 100 | 70 | 52 | 31.768 | 9.128 | 7.187 | 134.897 | 31.026 | 28.687 | 29.126 | 609.214 | 26.607 | 27.548 | 1267.248 | 27.331 | 27.594 | 40.045 | 28.001 | 3.5 | 4.1 | 1.5 | 0.6 | 0.2
4381 | 30/07/2025 11:48:52.636 | 96.864 | 83 | 100 | 70 | 52 | 28.429 | 8.934 | 7.185 | 134.836 | 31.026 | 28.689 | 29.119 | 609.308 | 26.586 | 27.55 | 1277.377 | 27.325 | 27.623 | 40.392 | 28.001 | 3.5 | 2.9 | 1.5 | 0.1 | 0.2
4382 | 30/07/2025 11:48:54.269 | 97.368 | 84 | 100 | 71 | 52 | 31.626 | 8.991 | 7.088 | 134.652 | 31.045 | 28.673 | 29.137 | 609.116 | 26.592 | 27.563 | 1266.049 | 27.346 | 27.604 | 40.372 | 36.001 | 2.9 | 1.7 | 1.1 | 0 | 0.2
4383 | 30/07/2025 11:48:55.901 | 96.816 | 82 | 100 | 72 | 52 | 28.829 | 9.126 | 7.086 | 133.076 | 31.029 | 28.69 | 29.152 | 609.197 | 26.587 | 27.555 | 1260.064 | 27.378 | 27.605 | 40.245 | 36.001 | 2.9 | 3.3 | 1.1 | 0 | 0.2
4384 | 30/07/2025 11:48:57.533 | 96.96 | 82 | 100 | 70 | 52 | 30.484 | 8.982 | 7.087 | 133.135 | 31.037 | 28.693 | 29.142 | 609.457 | 26.597 | 27.563 | 1257.157 | 27.344 | 27.576 | 39.945 | 22.001 | 2.2 | 5.4 | 0 | 1.7 | 0.2
4385 | 30/07/2025 11:48:59.169 | 97.056 | 82 | 100 | 70 | 52 | 32.53 | 9.21 | 7.07 | 133.168 | 31.025 | 28.69 | 29.14 | 608.14 | 26.596 | 27.535 | 1254.207 | 27.33 | 27.608 | 40.296 | 22.001 | 2.2 | 5.4 | 0 | 1.7 | 0.2
4386 | 30/07/2025 11:49:00.804 | 97.44 | 83 | 100 | 70 | 52 | 31.097 | 8.989 | 7.068 | 133.196 | 31.049 | 28.671 | 29.122 | 608.013 | 26.595 | 27.566 | 1255.882 | 27.332 | 27.61 | 40.328 | 22.001 | 2.2 | 2.6 | 0 | 0.7 | 0.2
4387 | 30/07/2025 11:49:02.440 | 97.872 | 84 | 100 | 71 | 52 | 28.491 | 9.213 | 7.087 | 133.141 | 31.039 | 28.686 | 29.142 | 607.936 | 26.586 | 27.543 | 1233.88 | 27.347 | 27.597 | 40.163 | 26.001 | 4.4 | 1.6 | 0.9 | 0.5 | 0.3
4388 | 30/07/2025 11:49:04.072 | 98.352 | 85 | 100 | 71 | 52 | 32.027 | 9.118 | 7.086 | 133.277 | 31.03 | 28.708 | 29.142 | 608.1 | 26.576 | 27.536 | 1219.5 | 27.354 | 27.576 | 40.08 | 26.001 | 4.4 | 2.3 | 0.9 | 0.1 | 0.3
4389 | 30/07/2025 11:49:05.706 | 98.616 | 84 | 100 | 71 | 51 | 28.58 | 9.147 | 7.088 | 133.297 | 31.026 | 28.692 | 29.142 | 608.125 | 26.587 | 27.542 | 1219.571 | 27.341 | 27.587 | 39.968 | 26.001 | 3.8 | 2.3 | 0.6 | 0.5 | 0.2
4390 | 30/07/2025 11:49:07.340 | 98.352 | 83 | 100 | 71 | 52 | 31.091 | 9.211 | 7.087 | 133.3 | 31.029 | 28.697 | 29.126 | 608.052 | 26.583 | 27.529 | 1217.787 | 27.346 | 27.613 | 40.354 | 26.001 | 3.8 | 2.5 | 0.6 | 0.5 | 0.2
4391 | 30/07/2025 11:49:08.978 | 98.4 | 83 | 100 | 70 | 52 | 32.708 | 9.218 | 7.087 | 133.006 | 31.028 | 28.668 | 29.124 | 608.006 | 26.59 | 27.537 | 1229.238 | 27.322 | 27.587 | 40.314 | 26.001 | 3.8 | 2.5 | 0.6 | 0.5 | 0.2
4392 | 30/07/2025 11:49:10.612 | 98.376 | 84 | 100 | 70 | 53 | 30.433 | 9.133 | 7.086 | 133.093 | 31.03 | 28.691 | 29.157 | 608.129 | 26.579 | 27.519 | 1227.912 | 27.348 | 27.596 | 40.183 | 29.001 | 2.9 | 1.7 | 0 | 0.5 | 0.2
4393 | 30/07/2025 11:49:12.246 | 97.968 | 86 | 100 | 70 | 52 | 32.533 | 9.137 | 7.089 | 133.057 | 31.033 | 28.697 | 29.139 | 607.968 | 26.611 | 27.536 | 1227.363 | 27.339 | 27.575 | 40.276 | 29.001 | 2.9 | 5.4 | 0 | 0.6 | 0.2
4394 | 30/07/2025 11:49:13.881 | 97.896 | 84 | 100 | 71 | 52 | 31.587 | 9.407 | 7.12 | 133.238 | 31.022 | 28.695 | 29.148 | 608.117 | 26.603 | 27.544 | 1234.36 | 27.348 | 27.628 | 40.024 | 32.001 | 2.4 | 3.9 | 0.6 | 0.6 | 0.2
4395 | 30/07/2025 11:49:15.515 | 98.448 | 84 | 100 | 70 | 53 | 28.428 | 8.984 | 7.123 | 132.929 | 31.009 | 28.683 | 29.12 | 606.776 | 26.588 | 27.563 | 1242.096 | 27.319 | 27.605 | 40.218 | 26.001 | 2.9 | 4.5 | 0 | 0.5 | 0.2
4396 | 30/07/2025 11:49:17.149 | 98.376 | 85 | 100 | 70 | 52 | 31.478 | 8.984 | 7.132 | 133.262 | 31.031 | 28.678 | 29.135 | 606.881 | 26.595 | 27.542 | 1247.064 | 27.344 | 27.596 | 40.202 | 26.001 | 2.9 | 4.5 | 0 | 0.5 | 0.2
4397 | 30/07/2025 11:49:18.783 | 98.832 | 84 | 100 | 71 | 52 | 32.712 | 9.135 | 7.135 | 132.84 | 31.005 | 28.706 | 29.144 | 606.756 | 26.59 | 27.55 | 1249.683 | 27.364 | 27.584 | 40.248 | 21.001 | 2.9 | 1.9 | 0.9 | 0.5 | 0.2
4398 | 30/07/2025 11:49:20.417 | 98.496 | 84 | 100 | 71 | 52 | 29.792 | 9.211 | 7.136 | 133.318 | 31.005 | 28.689 | 29.14 | 606.756 | 26.601 | 27.56 | 1244.902 | 27.353 | 27.586 | 40.051 | 26.001 | 2.5 | 5 | 1 | 0.8 | 0.3
4399 | 30/07/2025 11:49:22.048 | 98.568 | 85 | 100 | 71 | 53 | 32.581 | 9.135 | 7.134 | 133.273 | 31.002 | 28.696 | 29.135 | 606.942 | 26.603 | 27.576 | 1246.145 | 27.357 | 27.611 | 40.311 | 25.001 | 2.9 | 3.8 | 0.7 | 0 | 0.3
4400 | 30/07/2025 11:49:23.684 | 98.328 | 84 | 99 | 71 | 52 | 31.156 | 9.243 | 7.135 | 133.261 | 31.022 | 28.673 | 29.13 | 605.619 | 26.605 | 27.564 | 1254.91 | 27.307 | 27.6 | 40.485 | 25.001 | 2.9 | 4.8 | 0.7 | 0.8 | 0.3
4401 | 30/07/2025 11:49:25.318 | 98.328 | 84 | 100 | 70 | 51 | 28.542 | 9.136 | 7.151 | 133.089 | 31.021 | 28.682 | 29.149 | 604.445 | 26.594 | 27.541 | 1249.714 | 27.354 | 27.599 | 40.292 | 25.001 | 2.9 | 4.8 | 0.7 | 0.8 | 0.3
4402 | 30/07/2025 11:49:26.955 | 99.072 | 84 | 100 | 70 | 52 | 31.998 | 9.278 | 7.151 | 132.896 | 31.032 | 28.696 | 29.137 | 604.216 | 26.591 | 27.568 | 1252.322 | 27.341 | 27.576 | 40.046 | 30.001 | 2.3 | 4.2 | 0.9 | 0.4 | 0.2
4403 | 30/07/2025 11:49:28.590 | 98.76 | 84 | 100 | 71 | 53 | 32.696 | 9.126 | 7.135 | 133.327 | 31.053 | 28.696 | 29.127 | 605.361 | 26.587 | 27.54 | 1253.653 | 27.336 | 27.586 | 40.047 | 30.001 | 2.3 | 4.7 | 0.9 | 0.5 | 0.2
4404 | 30/07/2025 11:49:30.224 | 99.168 | 86 | 100 | 70 | 52 | 30.995 | 9.135 | 7.135 | 133.261 | 31.044 | 28.687 | 29.117 | 605.64 | 26.587 | 27.555 | 1257.416 | 27.325 | 27.59 | 40.291 | 30.001 | 3.1 | 2.8 | 0.8 | 0.5 | 0.2
4405 | 30/07/2025 11:49:31.858 | 99.576 | 85 | 100 | 71 | 51 | 32.581 | 9.037 | 7.127 | 133.293 | 31.033 | 28.673 | 29.137 | 605.788 | 26.583 | 27.547 | 1257.673 | 27.332 | 27.599 | 40.292 | 27.001 | 4.2 | 3.5 | 1.5 | 0.2 | 0.2
4406 | 30/07/2025 11:49:33.493 | 99.696 | 85 | 100 | 70 | 53 | 30.412 | 8.998 | 7.12 | 132.977 | 31.024 | 28.702 | 29.155 | 604.434 | 26.597 | 27.548 | 1246.546 | 27.364 | 27.609 | 40.376 | 27.001 | 3.6 | 4.6 | 0.7 | 0.8 | 0.2
4407 | 30/07/2025 11:49:35.128 | 99.624 | 85 | 100 | 70 | 51 | 28.817 | 9.201 | 7.123 | 133.005 | 31.045 | 28.69 | 29.136 | 604.258 | 26.584 | 27.555 | 1250.866 | 27.341 | 27.583 | 40.073 | 27.001 | 3.6 | 4.6 | 0.7 | 0.8 | 0.2
4408 | 30/07/2025 11:49:36.766 | 99.072 | 86 | 100 | 70 | 53 | 32.266 | 9.131 | 7.12 | 133.315 | 31.03 | 28.694 | 29.142 | 604.442 | 26.583 | 27.543 | 1247.092 | 27.339 | 27.608 | 40.036 | 27.001 | 3.6 | 2.3 | 0.7 | 1 | 0.2
4409 | 30/07/2025 11:49:38.399 | 98.928 | 84 | 100 | 70 | 52 | 32.569 | 9.132 | 7.121 | 133.268 | 31.032 | 28.674 | 29.105 | 604.271 | 26.575 | 27.544 | 1247.092 | 27.315 | 27.597 | 40.417 | 26.001 | 2.5 | 4.2 | 0.3 | 0.6 | 0.2
4410 | 30/07/2025 11:49:40.034 | 98.424 | 84 | 100 | 70 | 52 | 31.618 | 9.2 | 7.121 | 133.152 | 31.026 | 28.673 | 29.137 | 604.388 | 26.588 | 27.528 | 1254.782 | 27.35 | 27.611 | 40.254 | 26.001 | 2.5 | 4 | 0.3 | 0.8 | 0.2
4411 | 30/07/2025 11:49:41.673 | 98.304 | 84 | 100 | 70 | 52 | 32.802 | 9.207 | 7.136 | 132.903 | 31.022 | 28.692 | 29.141 | 604.407 | 26.58 | 27.547 | 1253.231 | 27.349 | 27.594 | 40.292 | 30.001 | 3.8 | 2.8 | 0.4 | 0.7 | 0.2
4412 | 30/07/2025 11:49:43.308 | 98.496 | 86 | 100 | 70 | 53 | 29.921 | 9.01 | 7.183 | 133.292 | 31.032 | 28.688 | 29.133 | 604.454 | 26.586 | 27.538 | 1249.158 | 27.338 | 27.589 | 39.88 | 30.001 | 3.8 | 2.8 | 0.4 | 0.7 | 0.2
4413 | 30/07/2025 11:49:44.949 | 98.712 | 84 | 100 | 70 | 50 | 29.328 | 8.993 | 7.158 | 133.297 | 31.023 | 28.701 | 29.13 | 604.281 | 26.59 | 27.54 | 1257.428 | 27.342 | 27.615 | 40.249 | 30.001 | 3.8 | 1.4 | 0.4 | 0.3 | 0.2
4414 | 30/07/2025 11:49:46.583 | 99.264 | 84 | 100 | 70 | 51 | 32.416 | 9.13 | 7.122 | 133.16 | 31.031 | 28.665 | 29.128 | 604.442 | 26.608 | 27.55 | 1252.375 | 27.324 | 27.606 | 40.268 | 26.001 | 3.5 | 1.8 | 0 | 0.6 | 0.2
4415 | 30/07/2025 11:49:48.219 | 98.832 | 84 | 100 | 71 | 52 | 28.575 | 8.989 | 7.077 | 133.046 | 31.018 | 28.673 | 29.132 | 604.362 | 26.597 | 27.557 | 1262.19 | 27.353 | 27.598 | 40.196 | 26.001 | 3.5 | 3.5 | 0 | 0.6 | 0.2
4416 | 30/07/2025 11:49:49.855 | 99.096 | 85 | 100 | 71 | 51 | 31.91 | 9.152 | 7.004 | 132.999 | 31.031 | 28.69 | 29.147 | 603.079 | 26.614 | 27.553 | 1269.628 | 27.343 | 27.585 | 40.203 | 25.001 | 3.4 | 5.3 | 1.2 | 0.7 | 0.2
4417 | 30/07/2025 11:49:51.490 | 99.12 | 84 | 100 | 70 | 53 | 32.708 | 9.22 | 7.003 | 133.211 | 31.006 | 28.688 | 29.137 | 603.145 | 26.601 | 27.543 | 1276.699 | 27.353 | 27.602 | 39.988 | 25.001 | 3.4 | 2.3 | 1.2 | 0 | 0.2
4418 | 30/07/2025 11:49:53.124 | 99.096 | 85 | 100 | 70 | 52 | 29.263 | 9.282 | 7.004 | 133.137 | 31.005 | 28.686 | 29.111 | 603 | 26.596 | 27.586 | 1272.001 | 27.32 | 27.608 | 40.354 | 25.001 | 3.4 | 2.3 | 1.2 | 0 | 0.2
4419 | 30/07/2025 11:49:54.759 | 99.12 | 84 | 100 | 70 | 52 | 29.795 | 9.249 | 7.002 | 133.168 | 31.011 | 28.677 | 29.149 | 603.316 | 26.594 | 27.555 | 1279.045 | 27.333 | 27.592 | 40.16 | 29.001 | 2.3 | 2.9 | 0.6 | 0.8 | 0.2
4420 | 30/07/2025 11:49:56.395 | 99.408 | 86 | 100 | 70 | 53 | 32.491 | 9.15 | 7.004 | 133.023 | 31.014 | 28.707 | 29.148 | 603.216 | 26.596 | 27.577 | 1285.038 | 27.355 | 27.598 | 40.307 | 29.001 | 2.3 | 3.9 | 0.6 | 1.2 | 0.2
4421 | 30/07/2025 11:49:58.031 | 99.144 | 84 | 100 | 70 | 52 | 28.849 | 9.187 | 7.004 | 133.177 | 31.015 | 28.687 | 29.152 | 603.307 | 26.595 | 27.549 | 1286.461 | 27.348 | 27.588 | 40.098 | 26.001 | 2.1 | 3.3 | 0 | 0.8 | 0.1
4422 | 30/07/2025 11:49:59.669 | 99.384 | 85 | 100 | 71 | 52 | 32.261 | 9.13 | 7.068 | 132.925 | 31.016 | 28.7 | 29.132 | 603.11 | 26.578 | 27.563 | 1287.529 | 27.352 | 27.608 | 40.236 | 26.001 | 2.1 | 2.4 | 0 | 0.6 | 0.1
4423 | 30/07/2025 11:50:01.303 | 99.408 | 84 | 99 | 71 | 52 | 32.573 | 8.93 | 7.07 | 133.333 | 31.031 | 28.678 | 29.111 | 602.94 | 26.608 | 27.559 | 1287.36 | 27.302 | 27.59 | 40.405 | 26.001 | 2.1 | 2.4 | 0 | 0.6 | 0.1
4424 | 30/07/2025 11:50:02.939 | 99.624 | 84 | 100 | 70 | 52 | 28.741 | 9.13 | 7.067 | 133.149 | 31.03 | 28.682 | 29.143 | 603.218 | 26.6 | 27.556 | 1294.482 | 27.363 | 27.605 | 40.239 | 25.001 | 2.7 | 3.3 | 0.6 | 0 | 0.2
4425 | 30/07/2025 11:50:04.583 | 99.936 | 86 | 100 | 71 | 51 | 30.41 | 9.137 | 7.087 | 132.834 | 31.045 | 28.695 | 29.149 | 603.155 | 26.594 | 27.568 | 1297.082 | 27.338 | 27.587 | 40.144 | 25.001 | 2.7 | 3.6 | 0.6 | 0.5 | 0.2
4426 | 30/07/2025 11:50:06.220 | 99.768 | 86 | 100 | 70 | 51 | 29.818 | 9.257 | 7.086 | 133.112 | 31.034 | 28.698 | 29.139 | 601.996 | 26.592 | 27.544 | 1289.686 | 27.36 | 27.582 | 40.185 | 28.001 | 2.5 | 4.5 | 1 | 1.1 | 0.2
4427 | 30/07/2025 11:50:07.854 | 99.672 | 84 | 99 | 70 | 52 | 29.3 | 9.257 | 7.089 | 133.26 | 31.031 | 28.69 | 29.117 | 602.538 | 26.594 | 27.558 | 1276.176 | 27.33 | 27.605 | 40.32 | 28.001 | 2.5 | 4.1 | 1 | 0.9 | 0.2
4428 | 30/07/2025 11:50:09.489 | 99.6 | 86 | 100 | 70 | 52 | 32.438 | 9.291 | 7.085 | 133.131 | 31.03 | 28.674 | 29.133 | 603.101 | 26.588 | 27.537 | 1277.19 | 27.332 | 27.616 | 40.4 | 27.001 | 1.8 | 2 | 1.3 | 0.6 | 0.2
4429 | 30/07/2025 11:50:11.133 | 99.408 | 84 | 100 | 70 | 52 | 32.247 | 9.107 | 7.134 | 133.002 | 31.038 | 28.685 | 29.148 | 603.301 | 26.588 | 27.565 | 1284.912 | 27.363 | 27.605 | 40.378 | 27.001 | 1.8 | 2 | 1.3 | 0.6 | 0.2
4430 | 30/07/2025 11:50:12.771 | 99.216 | 84 | 100 | 70 | 51 | 28.586 | 9.301 | 7.136 | 133.004 | 31.04 | 28.693 | 29.137 | 603.253 | 26.598 | 27.541 | 1284.788 | 27.346 | 27.58 | 40.258 | 27.001 | 1.8 | 4.6 | 1.3 | 0.1 | 0.2
4431 | 30/07/2025 11:50:14.405 | 99.576 | 86 | 100 | 70 | 52 | 31.158 | 9.134 | 7.134 | 133.384 | 31.035 | 28.693 | 29.14 | 603.205 | 26.576 | 27.533 | 1285.029 | 27.343 | 27.625 | 40.144 | 28.001 | 2.4 | 4.6 | 2.6 | 0.5 | 0.1
4432 | 30/07/2025 11:50:16.039 | 99.144 | 86 | 100 | 70 | 52 | 29.369 | 8.879 | 7.134 | 133.224 | 31.039 | 28.697 | 29.113 | 603.045 | 26.573 | 27.529 | 1287.168 | 27.324 | 27.615 | 40.259 | 28.001 | 2.4 | 4.2 | 2.6 | 0.6 | 0.1
4433 | 30/07/2025 11:50:17.674 | 99.36 | 85 | 100 | 70 | 52 | 30.01 | 8.987 | 7.133 | 133.097 | 31.017 | 28.678 | 29.142 | 603.086 | 26.576 | 27.532 | 1289.007 | 27.347 | 27.612 | 40.403 | 29.001 | 2.9 | 3.7 | 1.5 | 0.5 | 0.2
4434 | 30/07/2025 11:50:19.318 | 99.312 | 86 | 100 | 70 | 52 | 32.524 | 9.173 | 7.137 | 132.857 | 31.025 | 28.691 | 29.146 | 603.178 | 26.588 | 27.537 | 1290.644 | 27.354 | 27.59 | 40.234 | 29.001 | 2.9 | 3.7 | 1.5 | 0.5 | 0.2
4435 | 30/07/2025 11:50:20.953 | 98.928 | 84 | 100 | 71 | 52 | 31.69 | 9.166 | 7.134 | 133.206 | 31.027 | 28.688 | 29.149 | 603.285 | 26.574 | 27.536 | 1282.172 | 27.34 | 27.579 | 40.012 | 29.001 | 2.9 | 2.7 | 1.5 | 0.5 | 0.2
4436 | 30/07/2025 11:50:22.588 | 98.976 | 83 | 100 | 70 | 52 | 28.47 | 9.001 | 7.132 | 133.006 | 31.009 | 28.689 | 29.122 | 602.05 | 26.606 | 27.552 | 1276.425 | 27.337 | 27.606 | 40.315 | 23.001 | 4 | 4.1 | 0.6 | 0.2 | 0.1
4437 | 30/07/2025 11:50:24.222 | 98.64 | 84 | 100 | 70 | 52 | 31.462 | 8.896 | 7.121 | 133.246 | 31.018 | 28.674 | 29.131 | 601.872 | 26.612 | 27.561 | 1271.504 | 27.316 | 27.589 | 40.387 | 23.001 | 4 | 3 | 0.6 | 0.5 | 0.1
4438 | 30/07/2025 11:50:25.857 | 98.976 | 85 | 100 | 70 | 52 | 28.846 | 8.988 | 7.12 | 133.039 | 30.998 | 28.675 | 29.138 | 603.07 | 26.596 | 27.571 | 1273.165 | 27.354 | 27.608 | 40.519 | 26.001 | 2.9 | 4.5 | 0.3 | 0.6 | 0.1
4439 | 30/07/2025 11:50:27.491 | 98.832 | 84 | 100 | 71 | 52 | 30.354 | 9.293 | 7.122 | 133.257 | 31.02 | 28.694 | 29.144 | 602.169 | 26.598 | 27.545 | 1287.164 | 27.338 | 27.573 | 40.062 | 26.001 | 2.9 | 3.3 | 0.3 | 0.3 | 0.1
4440 | 30/07/2025 11:50:29.126 | 98.832 | 84 | 100 | 71 | 51 | 32.615 | 9.147 | 7.142 | 133.047 | 30.997 | 28.694 | 29.14 | 603.144 | 26.591 | 27.551 | 1294.606 | 27.357 | 27.605 | 38.243 | 26.001 | 2.9 | 3.3 | 0.3 | 0.3 | 0.1
4441 | 30/07/2025 11:50:30.760 | 98.832 | 83 | 100 | 70 | 51 | 31.161 | 9.221 | 7.151 | 133.187 | 31.024 | 28.684 | 29.127 | 603.055 | 26.599 | 27.566 | 1283.115 | 27.31 | 27.606 | 40.271 | 27.001 | 3.1 | 2.4 | 2.1 | 0 | 0.2
4442 | 30/07/2025 11:50:32.393 | 98.52 | 84 | 100 | 70 | 52 | 28.521 | 9.151 | 7.133 | 133.214 | 31.012 | 28.663 | 29.141 | 601.863 | 26.602 | 27.556 | 1280.276 | 27.334 | 27.598 | 40.17 | 27.001 | 3.1 | 4.8 | 2.1 | 0 | 0.2
4443 | 30/07/2025 11:50:34.030 | 98.568 | 84 | 100 | 70 | 52 | 32.186 | 9.132 | 7.136 | 133.085 | 31.025 | 28.688 | 29.142 | 601.904 | 26.596 | 27.566 | 1287.417 | 27.353 | 27.588 | 40.25 | 30.001 | 3.3 | 4.9 | 0.7 | 0 | 0.3
4444 | 30/07/2025 11:50:35.665 | 99.144 | 87 | 100 | 70 | 52 | 28.503 | 9.136 | 7.134 | 133.01 | 31.041 | 28.686 | 29.154 | 601.72 | 26.595 | 27.548 | 1279.833 | 27.342 | 27.595 | 40.223 | 27.001 | 2.8 | 3.3 | 1 | 0.2 | 0.3
4445 | 30/07/2025 11:50:37.301 | 99.528 | 85 | 100 | 70 | 52 | 30.941 | 9.229 | 7.167 | 132.972 | 31.027 | 28.694 | 29.129 | 601.972 | 26.604 | 27.566 | 1287.292 | 27.336 | 27.595 | 40.19 | 27.001 | 2.8 | 3.3 | 1 | 0.2 | 0.3
4446 | 30/07/2025 11:50:38.939 | 99.696 | 85 | 100 | 71 | 52 | 32.59 | 9.257 | 7.186 | 133.22 | 31.055 | 28.681 | 29.119 | 601.869 | 26.607 | 27.548 | 1287.311 | 27.305 | 27.604 | 40.198 | 28.001 | 3.1 | 2.1 | 0.6 | 0 | 0.3
4447 | 30/07/2025 11:50:40.574 | 99.48 | 85 | 100 | 70 | 51 | 30.395 | 9.135 | 7.185 | 133.117 | 31.052 | 28.676 | 29.129 | 601.853 | 26.593 | 27.545 | 1287.513 | 27.357 | 27.602 | 40.393 | 28.001 | 3.1 | 2.1 | 0.6 | 0 | 0.3
4448 | 30/07/2025 11:50:42.209 | 100.176 | 87 | 100 | 70 | 52 | 28.866 | 9.217 | 7.138 | 132.855 | 31.035 | 28.701 | 29.149 | 601.933 | 26.588 | 27.552 | 1287.422 | 27.349 | 27.585 | 40.303 | 28.001 | 3.3 | 2.4 | 1.3 | 0 | 0.3
4449 | 30/07/2025 11:50:43.843 | 99.888 | 86 | 100 | 70 | 54 | 31.639 | 9.222 | 7.134 | 133.089 | 31.036 | 28.696 | 29.149 | 602.077 | 26.587 | 27.559 | 1287.076 | 27.37 | 27.59 | 40.026 | 32.001 | 3.4 | 2.3 | 1.3 | 0.9 | 0.3
4450 | 30/07/2025 11:50:45.477 | 100.152 | 85 | 100 | 70 | 53 | 28.443 | 9.285 | 7.091 | 133.299 | 31.033 | 28.689 | 29.128 | 601.879 | 26.582 | 27.548 | 1292.081 | 27.334 | 27.608 | 40.325 | 27.001 | 5.3 | 3.4 | 0.7 | 1.1 | 0.3
4451 | 30/07/2025 11:50:47.111 | 100.104 | 86 | 100 | 70 | 52 | 31.6 | 9.287 | 7.086 | 133.168 | 31.022 | 28.674 | 29.141 | 603.239 | 26.578 | 27.533 | 1286.188 | 27.321 | 27.602 | 40.324 | 27.001 | 5.3 | 3.4 | 0.7 | 1.1 | 0.3
4452 | 30/07/2025 11:50:48.746 | 99.648 | 87 | 100 | 70 | 52 | 32.786 | 9.134 | 7.134 | 133.01 | 31.03 | 28.692 | 29.156 | 601.89 | 26.571 | 27.543 | 1292.257 | 27.364 | 27.61 | 40.387 | 27.001 | 5.3 | 3.5 | 0.7 | 0.5 | 0.3
4453 | 30/07/2025 11:50:50.380 | 99.984 | 85 | 100 | 69 | 51 | 29.936 | 9.132 | 7.135 | 133.048 | 31.048 | 28.691 | 29.144 | 603.174 | 26.598 | 27.522 | 1296.966 | 27.339 | 27.585 | 40.157 | 24.001 | 4.6 | 2.9 | 0.6 | 0 | 0.2
4454 | 30/07/2025 11:50:52.014 | 99.6 | 87 | 100 | 70 | 52 | 32.594 | 9.194 | 7.135 | 133.165 | 31.031 | 28.689 | 29.144 | 603.126 | 26.594 | 27.54 | 1303.932 | 27.34 | 27.593 | 40.087 | 24.001 | 4.6 | 3.1 | 0.6 | 0 | 0.2
4455 | 30/07/2025 11:50:53.647 | 99.744 | 87 | 100 | 70 | 53 | 31.135 | 9.285 | 7.135 | 133.346 | 31.046 | 28.693 | 29.116 | 603.218 | 26.596 | 27.525 | 1287.322 | 27.327 | 27.624 | 40.165 | 21.001 | 4.3 | 2 | 0.1 | 0.6 | 0.2
4456 | 30/07/2025 11:50:55.279 | 99.84 | 86 | 100 | 71 | 51 | 28.628 | 9.056 | 7.133 | 133.139 | 31.016 | 28.681 | 29.13 | 603.166 | 26.604 | 27.54 | 1287.175 | 27.36 | 27.603 | 40.277 | 21.001 | 4.3 | 2 | 0.1 | 0.6 | 0.2
4457 | 30/07/2025 11:50:56.913 | 99.144 | 86 | 100 | 70 | 52 | 32.011 | 9.288 | 7.136 | 134.456 | 31.006 | 28.691 | 29.128 | 602.897 | 26.59 | 27.551 | 1275.667 | 27.35 | 27.619 | 40.24 | 21.001 | 4.3 | 2.2 | 0.1 | 0.5 | 0.2
4458 | 30/07/2025 11:50:58.547 | 99.552 | 85 | 100 | 70 | 52 | 32.743 | 9.148 | 7.134 | 134.577 | 31.02 | 28.688 | 29.149 | 603.313 | 26.593 | 27.559 | 1276.935 | 27.341 | 27.59 | 40.137 | 28.001 | 3.2 | 2.7 | 0.9 | 0.2 | 0.2
4459 | 30/07/2025 11:51:00.182 | 99.816 | 88 | 100 | 71 | 51 | 29.423 | 8.997 | 7.135 | 134.653 | 31.01 | 28.705 | 29.132 | 603.146 | 26.597 | 27.574 | 1286.86 | 27.34 | 27.616 | 40.171 | 28.001 | 3.2 | 3.9 | 0.9 | 0 | 0.2
4460 | 30/07/2025 11:51:01.835 | 100.104 | 84 | 100 | 70 | 52 | 32.687 | 9.239 | 7.133 | 134.696 | 31.002 | 28.693 | 29.122 | 603.274 | 26.605 | 27.554 | 1287.115 | 27.333 | 27.728 | 40.241 | 27.001 | 2.2 | 3.7 | 1.3 | 0 | 0.1
4461 | 30/07/2025 11:51:03.469 | 100.2 | 88 | 100 | 71 | 52 | 30.649 | 9.289 | 7.134 | 134.552 | 31.006 | 28.671 | 29.135 | 601.841 | 26.59 | 27.581 | 1287.413 | 27.342 | 27.713 | 40.283 | 27.001 | 2.2 | 3.4 | 1.3 | 0.8 | 0.1
4462 | 30/07/2025 11:51:05.104 | 100.104 | 87 | 99 | 70 | 52 | 28.882 | 9.136 | 7.122 | 134.581 | 31.02 | 28.692 | 29.153 | 601.855 | 26.595 | 27.562 | 1287.421 | 27.348 | 27.599 | 40.216 | 27.001 | 2.2 | 3.4 | 1.3 | 0.8 | 0.1
4463 | 30/07/2025 11:51:06.739 | 99.96 | 86 | 100 | 71 | 53 | 32.269 | 9.135 | 7.12 | 134.687 | 31.017 | 28.701 | 29.144 | 602.093 | 26.584 | 27.552 | 1285.358 | 27.363 | 27.592 | 40.244 | 22.001 | 2.3 | 4.6 | 0.6 | 0.5 | 0.1
4464 | 30/07/2025 11:51:08.375 | 99.864 | 86 | 100 | 70 | 52 | 32.557 | 9.131 | 7.122 | 134.769 | 31.029 | 28.686 | 29.12 | 601.867 | 26.584 | 27.555 | 1283.796 | 27.321 | 27.723 | 40.31 | 22.001 | 2.3 | 3.2 | 0.6 | 0.2 | 0.1
4465 | 30/07/2025 11:51:10.011 | 99.336 | 85 | 100 | 70 | 52 | 31.43 | 9.134 | 7.121 | 134.724 | 31.031 | 28.693 | 29.118 | 602.03 | 26.598 | 27.55 | 1275.607 | 27.321 | 27.746 | 40.328 | 23.001 | 3.7 | 4.1 | 1.6 | 1.1 | 0.1
4466 | 30/07/2025 11:51:11.645 | 98.712 | 85 | 100 | 70 | 52 | 32.73 | 9.212 | 7.124 | 134.776 | 31.048 | 28.677 | 29.155 | 603.137 | 26.602 | 27.562 | 1276.804 | 27.346 | 27.603 | 40.072 | 23.001 | 3.7 | 2.8 | 1.6 | 1 | 0.1
4467 | 30/07/2025 11:51:13.281 | 98.328 | 84 | 100 | 70 | 53 | 29.785 | 9.169 | 7.135 | 134.486 | 31.043 | 28.697 | 29.145 | 603.074 | 26.583 | 27.543 | 1273.466 | 27.354 | 27.589 | 40.1 | 23.001 | 3.7 | 2.8 | 1.6 | 1 | 0.1
4468 | 30/07/2025 11:51:14.916 | 97.92 | 84 | 100 | 70 | 52 | 29.174 | 9.209 | 7.137 | 134.756 | 31.043 | 28.686 | 29.127 | 603.108 | 26.594 | 27.562 | 1269.313 | 27.343 | 27.601 | 39.95 | 23.001 | 4.5 | 3.1 | 0.3 | 0 | 0.1
4469 | 30/07/2025 11:51:16.550 | 98.016 | 86 | 100 | 69 | 51 | 32.408 | 9.184 | 7.133 | 134.746 | 31.034 | 28.686 | 29.109 | 603.232 | 26.602 | 27.547 | 1267.285 | 27.314 | 27.699 | 40.263 | 23.001 | 4.5 | 3.4 | 0.3 | 0.5 | 0.1
4470 | 30/07/2025 11:51:18.185 | 97.896 | 84 | 100 | 70 | 53 | 28.529 | 9.156 | 7.133 | 134.516 | 31.029 | 28.665 | 29.116 | 603.121 | 26.588 | 27.552 | 1267.181 | 27.326 | 27.759 | 40.432 | 23.001 | 3.5 | 3.4 | 1.2 | 0.5 | 0.2
4471 | 30/07/2025 11:51:19.820 | 97.92 | 84 | 100 | 70 | 52 | 31.927 | 9.131 | 7.134 | 134.448 | 31.043 | 28.69 | 29.165 | 603.248 | 26.589 | 27.538 | 1277.024 | 27.357 | 27.601 | 40.171 | 23.001 | 3.5 | 6.1 | 1.2 | 0.9 | 0.2
4472 | 30/07/2025 11:51:21.454 | 97.08 | 84 | 100 | 70 | 53 | 32.779 | 9.134 | 7.135 | 134.487 | 31.026 | 28.705 | 29.131 | 603.195 | 26.57 | 27.537 | 1287.603 | 27.361 | 27.593 | 40.273 | 27.001 | 3.9 | 1.9 | 0 | 0.1 | 0.2
4473 | 30/07/2025 11:51:23.089 | 96.672 | 83 | 100 | 70 | 53 | 29.286 | 9.209 | 7.136 | 134.805 | 31.021 | 28.69 | 29.128 | 603.129 | 26.598 | 27.553 | 1293.229 | 27.34 | 27.611 | 40.219 | 27.001 | 3.9 | 1.9 | 0 | 0.1 | 0.2
4474 | 30/07/2025 11:51:24.725 | 97.224 | 84 | 100 | 70 | 52 | 29.949 | 9.131 | 7.15 | 134.631 | 31.021 | 28.684 | 29.12 | 603.207 | 26.574 | 27.517 | 1278.107 | 27.32 | 27.616 | 40.337 | 27.001 | 3.9 | 3.9 | 0 | 0 | 0.2
4475 | 30/07/2025 11:51:26.359 | 96.528 | 83 | 100 | 70 | 52 | 32.515 | 8.987 | 7.136 | 134.551 | 31.028 | 28.68 | 29.139 | 603.1 | 26.573 | 27.55 | 1281.204 | 27.343 | 27.599 | 40.169 | 21.001 | 5.5 | 3.4 | 1 | 0.5 | 0.2
4476 | 30/07/2025 11:51:27.994 | 97.032 | 83 | 100 | 71 | 53 | 28.928 | 8.864 | 7.134 | 134.476 | 31.024 | 28.706 | 29.149 | 603.222 | 26.595 | 27.533 | 1285.002 | 27.369 | 27.595 | 40.115 | 21.001 | 5.5 | 4.7 | 1 | 0.8 | 0.2
4477 | 30/07/2025 11:51:29.628 | 96.96 | 82 | 100 | 70 | 52 | 32.286 | 8.996 | 7.136 | 134.675 | 31.011 | 28.684 | 29.128 | 603.082 | 26.604 | 27.55 | 1276.71 | 27.34 | 27.572 | 40.113 | 23.001 | 3 | 2.6 | 1 | 0 | 0.2
4478 | 30/07/2025 11:51:31.285 | 97.248 | 84 | 100 | 71 | 52 | 32.581 | 9.127 | 7.133 | 134.49 | 31.019 | 28.69 | 29.119 | 603.231 | 26.576 | 27.538 | 1279.424 | 27.327 | 27.753 | 40.177 | 23.001 | 3 | 2.6 | 1 | 0 | 0.2
4479 | 30/07/2025 11:51:32.919 | 97.128 | 82 | 100 | 70 | 51 | 28.899 | 9.133 | 7.133 | 134.59 | 30.998 | 28.679 | 29.123 | 603.245 | 26.58 | 27.558 | 1277.153 | 27.336 | 27.751 | 40.236 | 23.001 | 3 | 3.4 | 1 | 0.5 | 0.2
4480 | 30/07/2025 11:51:34.551 | 96.264 | 82 | 100 | 70 | 52 | 30.434 | 8.985 | 7.137 | 134.478 | 31.006 | 28.685 | 29.155 | 603.12 | 26.602 | 27.565 | 1271.991 | 27.35 | 27.746 | 40.351 | 31.001 | 2.1 | 5.6 | 0.9 | 0.6 | 0.3
4481 | 30/07/2025 11:51:36.186 | 96.048 | 81 | 100 | 70 | 53 | 30.084 | 9.141 | 7.134 | 134.446 | 31.009 | 28.706 | 29.142 | 603.113 | 26.598 | 27.585 | 1265.73 | 27.351 | 27.746 | 40.209 | 31.001 | 2.1 | 3.6 | 0.9 | 0.5 | 0.3
4482 | 30/07/2025 11:51:37.822 | 96.432 | 82 | 100 | 71 | 53 | 29.301 | 9.129 | 7.135 | 134.781 | 31.01 | 28.685 | 29.143 | 603.047 | 26.605 | 27.556 | 1257.408 | 27.341 | 27.602 | 39.959 | 29.001 | 1.2 | 3.1 | 0.5 | 0.1 | 0.2
4483 | 30/07/2025 11:51:39.455 | 96.576 | 83 | 100 | 70 | 51 | 32.417 | 9.288 | 7.134 | 134.593 | 31.015 | 28.688 | 29.124 | 603.163 | 26.594 | 27.564 | 1257.937 | 27.322 | 27.776 | 42.062 | 29.001 | 1.2 | 2.8 | 0.5 | 0 | 0.2
4484 | 30/07/2025 11:51:41.089 | 96.744 | 83 | 100 | 70 | 52 | 32.25 | 9.289 | 7.133 | 134.447 | 31.022 | 28.671 | 29.14 | 603.018 | 26.592 | 27.571 | 1257.514 | 27.343 | 27.61 | 42.12 | 29.001 | 1.2 | 2.8 | 0.5 | 0 | 0.2
4485 | 30/07/2025 11:51:42.723 | 96.6 | 83 | 100 | 71 | 51 | 28.55 | 9.13 | 7.134 | 132.865 | 31.047 | 28.696 | 29.157 | 603.117 | 26.592 | 27.555 | 1257.269 | 27.346 | 27.737 | 40.108 | 23.001 | 3.1 | 3.6 | 1.2 | 0.5 | 0.2
4486 | 30/07/2025 11:51:44.358 | 97.704 | 83 | 100 | 69 | 52 | 30.904 | 9.26 | 7.135 | 133.159 | 31.016 | 28.705 | 29.135 | 602.995 | 26.595 | 27.547 | 1266.451 | 27.355 | 27.729 | 40.094 | 23.001 | 3.1 | 2.7 | 1.2 | 0 | 0.2
4487 | 30/07/2025 11:51:45.991 | 98.016 | 84 | 100 | 70 | 52 | 29.287 | 9.14 | 7.134 | 133.311 | 31.048 | 28.688 | 29.152 | 603.198 | 26.595 | 27.535 | 1258.414 | 27.335 | 27.742 | 39.971 | 25.001 | 2.6 | 3.2 | 1.5 | 0 | 0.3
4488 | 30/07/2025 11:51:47.624 | 99.216 | 85 | 100 | 71 | 50 | 29.727 | 9.287 | 7.133 | 133.032 | 31.035 | 28.684 | 29.124 | 601.943 | 26.59 | 27.559 | 1247.417 | 27.331 | 27.61 | 40.381 | 30.001 | 3 | 4.2 | 0.6 | 0.6 | 0.2
4489 | 30/07/2025 11:51:49.258 | 98.616 | 87 | 100 | 71 | 51 | 32.546 | 9.176 | 7.135 | 133.071 | 31.042 | 28.673 | 29.14 | 601.903 | 26.601 | 27.554 | 1257.198 | 27.346 | 27.744 | 40.11 | 30.001 | 3 | 4.2 | 0.6 | 0.6 | 0.2
4490 | 30/07/2025 11:51:50.892 | 98.664 | 85 | 100 | 71 | 52 | 31.703 | 8.99 | 7.121 | 133.017 | 31.029 | 28.704 | 29.149 | 601.952 | 26.585 | 27.539 | 1262.338 | 27.361 | 27.746 | 40.172 | 31.001 | 4.1 | 2.6 | 0.9 | 1.1 | 0.2
4491 | 30/07/2025 11:51:52.526 | 99.288 | 87 | 100 | 71 | 53 | 28.42 | 9.209 | 7.121 | 133.075 | 31.033 | 28.692 | 29.133 | 601.68 | 26.59 | 27.559 | 1264.423 | 27.338 | 27.741 | 39.986 | 31.001 | 4.1 | 3.2 | 0.9 | 1.1 | 0.2
4492 | 30/07/2025 11:51:54.161 | 99.168 | 84 | 100 | 70 | 52 | 32.526 | 9.132 | 7.121 | 133.243 | 31.032 | 28.701 | 29.127 | 602.052 | 26.577 | 27.542 | 1273.694 | 27.343 | 27.767 | 40.154 | 25.001 | 3.4 | 3 | 0.7 | 1.1 | 0.2
4493 | 30/07/2025 11:51:55.796 | 99.192 | 86 | 100 | 70 | 51 | 28.856 | 9.254 | 7.12 | 133.13 | 31.03 | 28.684 | 29.101 | 601.831 | 26.584 | 27.531 | 1279.291 | 27.314 | 27.753 | 40.246 | 25.001 | 3.4 | 2.7 | 0.7 | 0 | 0.2
4494 | 30/07/2025 11:51:57.430 | 99.48 | 86 | 99 | 70 | 52 | 32.906 | 9.135 | 7.134 | 133.253 | 31.037 | 28.69 | 29.171 | 601.979 | 26.584 | 27.528 | 1277.241 | 27.359 | 27.749 | 40.128 | 22.001 | 3.5 | 3.9 | 0.9 | 0.5 | 0.2
4495 | 30/07/2025 11:51:59.064 | 99.216 | 85 | 100 | 70 | 51 | 32.593 | 9.14 | 7.087 | 132.989 | 31.027 | 28.702 | 29.138 | 601.922 | 26.593 | 27.547 | 1273.133 | 27.351 | 27.726 | 40.201 | 22.001 | 3.5 | 3.9 | 0.9 | 0.5 | 0.2
4496 | 30/07/2025 11:52:00.699 | 99.84 | 86 | 100 | 70 | 52 | 31.112 | 9.131 | 7.08 | 133.281 | 31.041 | 28.687 | 29.137 | 601.782 | 26.612 | 27.534 | 1268.147 | 27.337 | 27.755 | 40.056 | 22.001 | 3.5 | 3.4 | 0.9 | 0.5 | 0.2
4497 | 30/07/2025 11:52:02.334 | 99.648 | 86 | 100 | 70 | 52 | 32.416 | 8.962 | 7.072 | 133.083 | 31.016 | 28.684 | 29.116 | 601.869 | 26.587 | 27.542 | 1277.237 | 27.32 | 27.757 | 40.408 | 20.001 | 3.5 | 4.2 | 1.8 | 0.5 | 0.2
4498 | 30/07/2025 11:52:03.968 | 99.528 | 85 | 100 | 69 | 52 | 32.261 | 9.274 | 7.068 | 133.438 | 31.033 | 28.674 | 29.143 | 602.016 | 26.603 | 27.539 | 1278.611 | 27.332 | 27.753 | 40.182 | 24.001 | 2 | 2.7 | 1 | 0 | 0.3
4499 | 30/07/2025 11:52:05.601 | 99.288 | 85 | 100 | 70 | 52 | 28.57 | 9.126 | 7.059 | 132.992 | 31.012 | 28.703 | 29.15 | 601.979 | 26.605 | 27.547 | 1287.847 | 27.371 | 27.747 | 40.448 | 26.001 | 3 | 3.2 | 1.2 | 0 | 0.2
4500 | 30/07/2025 11:52:07.236 | 99.504 | 86 | 100 | 70 | 51 | 31.058 | 9.118 | 7.06 | 133.257 | 31.008 | 28.687 | 29.121 | 601.837 | 26.602 | 27.56 | 1287.211 | 27.352 | 27.731 | 40.118 | 26.001 | 3 | 3.2 | 1.2 | 0 | 0.2
4501 | 30/07/2025 11:52:08.871 | 99.864 | 86 | 100 | 70 | 52 | 32.684 | 9.131 | 7.058 | 133.309 | 31.01 | 28.696 | 29.139 | 601.899 | 26.591 | 27.554 | 1285.689 | 27.326 | 27.618 | 40.074 | 26.001 | 3 | 2.9 | 1.2 | 0.9 | 0.2
4502 | 30/07/2025 11:52:10.505 | 99.504 | 85 | 100 | 69 | 52 | 30.687 | 9.135 | 7.067 | 133.029 | 30.991 | 28.678 | 29.106 | 601.987 | 26.595 | 27.569 | 1287.417 | 27.333 | 27.746 | 40.254 | 23.001 | 3.3 | 1.4 | 1.8 | 0.2 | 0.2
4503 | 30/07/2025 11:52:12.138 | 99.192 | 84 | 100 | 70 | 52 | 32.487 | 9.137 | 7.073 | 133.153 | 31.009 | 28.675 | 29.148 | 601.991 | 26.599 | 27.546 | 1289.451 | 27.34 | 27.754 | 40.051 | 23.001 | 3.3 | 1.9 | 1.8 | 0.5 | 0.2
4504 | 30/07/2025 11:52:13.772 | 99.24 | 85 | 100 | 70 | 53 | 31.844 | 9.289 | 7.187 | 132.931 | 31.022 | 28.698 | 29.139 | 601.884 | 26.587 | 27.579 | 1291.563 | 27.353 | 27.74 | 40.176 | 27.001 | 2.1 | 4.3 | 0.8 | 1.1 | 0.2
4505 | 30/07/2025 11:52:15.407 | 98.808 | 86 | 100 | 71 | 52 | 28.485 | 9.136 | 7.136 | 133.292 | 31.025 | 28.693 | 29.149 | 601.793 | 26.608 | 27.562 | 1287.05 | 27.345 | 27.741 | 40.06 | 27.001 | 2.1 | 3 | 0.8 | 0.9 | 0.2
4506 | 30/07/2025 11:52:17.041 | 98.928 | 84 | 100 | 70 | 52 | 31.561 | 9.2 | 7.134 | 133.114 | 31.04 | 28.687 | 29.128 | 601.997 | 26.589 | 27.547 | 1292.278 | 27.338 | 27.762 | 40.358 | 27.001 | 2.1 | 3 | 0.8 | 0.9 | 0.2
4507 | 30/07/2025 11:52:18.676 | 98.904 | 86 | 100 | 70 | 52 | 32.748 | 8.986 | 7.133 | 134.574 | 31.032 | 28.664 | 29.146 | 603.226 | 26.589 | 27.552 | 1279.71 | 27.334 | 27.751 | 40.317 | 26.001 | 3.3 | 3.5 | 1.2 | 0.2 | 0.2
4508 | 30/07/2025 11:52:20.313 | 98.856 | 84 | 100 | 70 | 52 | 29.919 | 9.135 | 7.134 | 134.572 | 31.045 | 28.691 | 29.161 | 603.308 | 26.589 | 27.544 | 1272.247 | 27.345 | 27.749 | 40.135 | 26.001 | 3.3 | 2.9 | 1.2 | 0 | 0.2
4509 | 30/07/2025 11:52:21.947 | 98.472 | 84 | 100 | 72 | 50 | 32.622 | 8.99 | 7.137 | 134.363 | 31.043 | 28.701 | 29.139 | 601.798 | 26.586 | 27.556 | 1271.857 | 27.344 | 27.73 | 40.221 | 25.001 | 2.4 | 1.9 | 0.1 | 0 | 0.2
4510 | 30/07/2025 11:52:23.585 | 98.4 | 84 | 100 | 72 | 52 | 31.12 | 9.212 | 7.134 | 134.857 | 31.038 | 28.694 | 29.144 | 601.929 | 26.58 | 27.544 | 1274.61 | 27.342 | 27.739 | 40.198 | 25.001 | 2.4 | 2.2 | 0.1 | 0.5 | 0.2
4511 | 30/07/2025 11:52:25.219 | 98.4 | 84 | 100 | 72 | 52 | 28.542 | 9.138 | 7.134 | 134.492 | 31.043 | 28.678 | 29.098 | 601.824 | 26.595 | 27.565 | 1268.078 | 27.321 | 27.759 | 40.433 | 25.001 | 2.4 | 2.2 | 0.1 | 0.5 | 0.2
4512 | 30/07/2025 11:52:26.853 | 98.304 | 84 | 100 | 70 | 51 | 31.923 | 9.285 | 7.186 | 134.779 | 31.057 | 28.672 | 29.145 | 602.101 | 26.599 | 27.54 | 1284.894 | 27.341 | 27.761 | 40.204 | 28.001 | 1.5 | 5.1 | 0.6 | 0.7 | 0.2
4513 | 30/07/2025 11:52:28.489 | 98.328 | 84 | 100 | 70 | 52 | 32.782 | 9.18 | 7.186 | 134.515 | 31.029 | 28.702 | 29.142 | 602.067 | 26.566 | 27.532 | 1285.008 | 27.364 | 27.751 | 40.227 | 28.001 | 1.5 | 5.7 | 0.6 | 0.5 | 0.2
4514 | 30/07/2025 11:52:30.123 | 98.664 | 85 | 100 | 70 | 53 | 31.011 | 9.132 | 7.187 | 134.808 | 31.033 | 28.693 | 29.151 | 602.038 | 26.59 | 27.535 | 1273.34 | 27.338 | 27.729 | 40.225 | 23.001 | 2.9 | 3 | 1.5 | 0.5 | 0.2
4515 | 30/07/2025 11:52:31.758 | 98.232 | 83 | 100 | 72 | 51 | 32.746 | 9.284 | 7.151 | 134.752 | 31.028 | 28.702 | 29.14 | 601.986 | 26.583 | 27.533 | 1274.155 | 27.348 | 27.767 | 40.155 | 29.001 | 3.2 | 3.3 | 1.5 | 0.5 | 0.2
4516 | 30/07/2025 11:52:33.392 | 98.184 | 86 | 100 | 70 | 52 | 30.436 | 9.238 | 7.152 | 134.585 | 31.027 | 28.682 | 29.113 | 601.833 | 26.591 | 27.537 | 1274.352 | 27.312 | 27.754 | 40.414 | 25.001 | 1.6 | 4.3 | 0 | 1.4 | 0.2
4517 | 30/07/2025 11:52:35.028 | 97.848 | 84 | 100 | 70 | 52 | 28.867 | 9.219 | 7.202 | 134.572 | 31.021 | 28.687 | 29.144 | 602.058 | 26.579 | 27.517 | 1286.297 | 27.359 | 27.755 | 40.378 | 25.001 | 1.6 | 4.3 | 0 | 1.4 | 0.2
4518 | 30/07/2025 11:52:36.662 | 97.032 | 84 | 100 | 70 | 52 | 32.223 | 9.135 | 7.189 | 134.445 | 31.016 | 28.69 | 29.14 | 601.929 | 26.59 | 27.556 | 1277.123 | 27.352 | 27.724 | 40.325 | 25.001 | 1.6 | 4.4 | 0 | 0.3 | 0.2
4519 | 30/07/2025 11:52:38.295 | 97.152 | 83 | 100 | 68 | 52 | 28.483 | 9.211 | 7.186 | 134.695 | 31.009 | 28.695 | 29.138 | 602.135 | 26.594 | 27.539 | 1277.23 | 27.346 | 27.744 | 40.182 | 30.001 | 3.5 | 3.8 | 0.6 | 0.8 | 0.3
4520 | 30/07/2025 11:52:39.941 | 97.08 | 83 | 100 | 72 | 53 | 31.506 | 9.131 | 7.188 | 134.6 | 31.01 | 28.685 | 29.124 | 601.787 | 26.601 | 27.552 | 1277.437 | 27.321 | 27.749 | 40.421 | 30.001 | 3.5 | 4.7 | 0.6 | 1.1 | 0.3
4521 | 30/07/2025 11:52:41.576 | 97.488 | 83 | 100 | 71 | 52 | 32.747 | 9.344 | 7.182 | 134.662 | 31.019 | 28.665 | 29.135 | 601.889 | 26.601 | 27.56 | 1278.931 | 27.318 | 27.75 | 40.333 | 30.001 | 5.1 | 4.6 | 1.2 | 0.6 | 0.3
4522 | 30/07/2025 11:52:43.210 | 97.032 | 82 | 100 | 71 | 53 | 29.988 | 8.923 | 7.133 | 134.379 | 31.003 | 28.695 | 29.143 | 602.04 | 26.591 | 27.563 | 1275.631 | 27.38 | 27.735 | 40.291 | 30.001 | 5.1 | 4.6 | 1.2 | 0.6 | 0.3
4523 | 30/07/2025 11:52:44.847 | 97.152 | 82 | 100 | 70 | 52 | 29.377 | 9.194 | 7.137 | 134.52 | 31.003 | 28.687 | 29.137 | 601.828 | 26.601 | 27.564 | 1299.221 | 27.349 | 27.736 | 40.255 | 30.001 | 5.1 | 4.8 | 1.2 | 0.9 | 0.3
4524 | 30/07/2025 11:52:46.481 | 97.32 | 83 | 100 | 70 | 52 | 32.406 | 8.981 | 7.134 | 134.531 | 31.02 | 28.694 | 29.132 | 602.002 | 26.58 | 27.543 | 1284.917 | 27.329 | 27.761 | 40.247 | 29.001 | 1.1 | 3.2 | 1 | 0.5 | 0.3
4525 | 30/07/2025 11:52:48.112 | 97.104 | 82 | 100 | 70 | 53 | 28.567 | 8.981 | 7.136 | 134.779 | 31.027 | 28.688 | 29.117 | 601.874 | 26.605 | 27.552 | 1280.17 | 27.307 | 27.757 | 40.431 | 29.001 | 1.1 | 2.1 | 1 | 0.6 | 0.3
4526 | 30/07/2025 11:52:49.748 | 96.912 | 83 | 100 | 70 | 52 | 31.946 | 9.061 | 7.131 | 134.555 | 31.023 | 28.675 | 29.141 | 603.294 | 26.59 | 27.548 | 1267.496 | 27.34 | 27.759 | 40.454 | 29.001 | 3.7 | 3.1 | 0.6 | 0.1 | 0.3
4527 | 30/07/2025 11:52:51.382 | 97.392 | 84 | 100 | 70 | 52 | 32.719 | 9.135 | 7.153 | 134.211 | 31.038 | 28.697 | 29.126 | 603.268 | 26.595 | 27.56 | 1267.66 | 27.347 | 27.736 | 40.405 | 29.001 | 3.7 | 3 | 0.6 | 1 | 0.3
4528 | 30/07/2025 11:52:53.017 | 97.632 | 84 | 100 | 70 | 52 | 29.371 | 8.983 | 7.152 | 134.713 | 31.044 | 28.699 | 29.148 | 603.13 | 26.589 | 27.545 | 1264.085 | 27.35 | 27.729 | 40.089 | 29.001 | 3.7 | 3 | 0.6 | 1 | 0.3
4529 | 30/07/2025 11:52:54.653 | 97.848 | 84 | 100 | 70 | 52 | 29.769 | 9.135 | 7.152 | 134.679 | 31.024 | 28.683 | 29.126 | 603.115 | 26.589 | 27.562 | 1267.279 | 27.347 | 27.771 | 40.36 | 29.001 | 3.5 | 2.3 | 0.6 | 0.2 | 0.2
4530 | 30/07/2025 11:52:56.370 | 98.184 | 84 | 100 | 70 | 52 | 32.528 | 8.985 | 7.135 | 134.67 | 31.043 | 28.669 | 29.116 | 601.708 | 26.587 | 27.561 | 1266.908 | 27.327 | 27.749 | 40.232 | 29.001 | 3.5 | 4.7 | 0.6 | 0.5 | 0.2
4531 | 30/07/2025 11:52:58.004 | 98.016 | 84 | 100 | 70 | 52 | 28.8 | 8.984 | 7.134 | 134.499 | 31.033 | 28.683 | 29.139 | 601.889 | 26.57 | 27.557 | 1262.095 | 27.36 | 27.756 | 40.36 | 26.001 | 3.7 | 5.6 | 0.6 | 0.5 | 0.2
4532 | 30/07/2025 11:52:59.641 | 97.992 | 84 | 100 | 69 | 52 | 32.307 | 9.133 | 7.136 | 134.368 | 31.04 | 28.7 | 29.138 | 603.045 | 26.59 | 27.552 | 1271.816 | 27.351 | 27.727 | 39.991 | 26.001 | 3.7 | 3.3 | 0.6 | 0 | 0.2
4533 | 30/07/2025 11:53:01.275 | 98.016 | 84 | 100 | 70 | 51 | 32.668 | 9.13 | 7.119 | 134.761 | 31.038 | 28.699 | 29.142 | 601.965 | 26.58 | 27.531 | 1273.604 | 27.344 | 27.749 | 40.228 | 26.001 | 3.7 | 3.3 | 0.6 | 0 | 0.2
4534 | 30/07/2025 11:53:02.911 | 98.016 | 84 | 100 | 71 | 52 | 28.931 | 9.234 | 7.124 | 134.766 | 31.026 | 28.686 | 29.098 | 601.9 | 26.587 | 27.54 | 1265.033 | 27.32 | 27.749 | 40.522 | 30.001 | 3.1 | 5.4 | 0.4 | 0.6 | 0.2
4535 | 30/07/2025 11:53:04.559 | 98.064 | 84 | 100 | 71 | 52 | 30.42 | 9.205 | 7.119 | 134.736 | 31.043 | 28.678 | 29.149 | 601.896 | 26.58 | 27.539 | 1262.93 | 27.344 | 27.762 | 40.117 | 30.001 | 3.1 | 4.3 | 0.4 | 0.5 | 0.2
4536 | 30/07/2025 11:53:06.194 | 98.088 | 84 | 100 | 71 | 53 | 32.656 | 9.06 | 7.135 | 134.535 | 31.034 | 28.71 | 29.14 | 603.062 | 26.58 | 27.523 | 1266.875 | 27.35 | 27.74 | 40.151 | 26.001 | 3.1 | 1.9 | 0 | 0.5 | 0.2
4537 | 30/07/2025 11:53:07.829 | 98.16 | 84 | 100 | 71 | 52 | 29.28 | 8.871 | 7.15 | 134.597 | 31.02 | 28.692 | 29.141 | 603.199 | 26.584 | 27.509 | 1266.723 | 27.348 | 27.722 | 40.172 | 28.001 | 2.7 | 2.5 | 0 | 0.7 | 0.2
4538 | 30/07/2025 11:53:09.464 | 98.28 | 86 | 100 | 70 | 52 | 32.416 | 9.181 | 7.164 | 134.555 | 31.017 | 28.704 | 29.124 | 603.218 | 26.591 | 27.547 | 1267.238 | 27.342 | 27.748 | 40.144 | 25.001 | 1.6 | 2.4 | 0.7 | 0.1 | 0.3
4539 | 30/07/2025 11:53:11.099 | 98.256 | 85 | 100 | 70 | 53 | 32.185 | 9.275 | 7.186 | 134.705 | 31.024 | 28.675 | 29.101 | 603.124 | 26.625 | 27.554 | 1264.906 | 27.315 | 27.748 | 40.244 | 25.001 | 1.6 | 2.4 | 0.7 | 0.1 | 0.3
4540 | 30/07/2025 11:53:12.734 | 98.136 | 86 | 100 | 70 | 52 | 28.557 | 9.199 | 7.133 | 134.696 | 31.014 | 28.686 | 29.145 | 603.316 | 26.6 | 27.545 | 1264.894 | 27.346 | 27.767 | 40.239 | 25.001 | 1.6 | 4.7 | 0.7 | 0.8 | 0.3
4541 | 30/07/2025 11:53:14.370 | 97.968 | 84 | 100 | 71 | 53 | 30.96 | 8.996 | 7.135 | 134.451 | 31.001 | 28.685 | 29.137 | 602.994 | 26.595 | 27.573 | 1273.045 | 27.347 | 27.731 | 40.329 | 28.001 | 2.7 | 3.7 | 0.3 | 0.8 | 0.3
4542 | 30/07/2025 11:53:16.014 | 98.016 | 84 | 100 | 70 | 52 | 29.398 | 9.015 | 7.151 | 134.535 | 31.013 | 28.694 | 29.148 | 603.163 | 26.602 | 27.562 | 1270.301 | 27.347 | 27.742 | 40.125 | 26.001 | 2.2 | 3.1 | 0.6 | 0.9 | 0.3
4543 | 30/07/2025 11:53:17.649 | 97.656 | 84 | 100 | 71 | 52 | 29.837 | 9.203 | 7.133 | 134.639 | 31.001 | 28.693 | 29.124 | 603.152 | 26.59 | 27.566 | 1271.647 | 27.317 | 27.752 | 40.342 | 24.001 | 2.9 | 3.3 | 0.7 | 0 | 0.3
4544 | 30/07/2025 11:53:19.284 | 97.752 | 84 | 100 | 70 | 52 | 32.532 | 9.13 | 7.12 | 134.588 | 31.015 | 28.673 | 29.143 | 603.233 | 26.582 | 27.547 | 1282.695 | 27.33 | 27.741 | 40.3 | 24.001 | 2.9 | 3.3 | 0.7 | 0 | 0.3
4545 | 30/07/2025 11:53:20.922 | 97.296 | 82 | 100 | 70 | 53 | 31.839 | 8.987 | 7.085 | 134.368 | 31.01 | 28.694 | 29.135 | 603.153 | 26.592 | 27.568 | 1279.898 | 27.366 | 27.747 | 40.486 | 24.001 | 2.9 | 3.5 | 0.7 | 0 | 0.3
4546 | 30/07/2025 11:53:22.557 | 97.656 | 83 | 100 | 70 | 52 | 28.407 | 9.134 | 7.098 | 134.737 | 31.036 | 28.688 | 29.141 | 603.002 | 26.597 | 27.575 | 1277.922 | 27.342 | 27.73 | 40.19 | 26.001 | 4.4 | 3.3 | 0.6 | 0.5 | 0.3
4547 | 30/07/2025 11:53:24.205 | 97.752 | 84 | 100 | 70 | 51 | 32.577 | 9.216 | 7.133 | 134.538 | 31.023 | 28.694 | 29.139 | 602.996 | 26.589 | 27.568 | 1284.679 | 27.347 | 27.748 | 39.909 | 26.001 | 4.4 | 3.3 | 0.6 | 0.8 | 0.3
4548 | 30/07/2025 11:53:25.845 | 97.704 | 84 | 100 | 70 | 52 | 28.829 | 9.127 | 7.135 | 134.857 | 31.044 | 28.691 | 29.119 | 603.213 | 26.602 | 27.56 | 1282.195 | 27.311 | 27.745 | 40.257 | 28.001 | 2.8 | 5.2 | 0 | 0.1 | 0.3
4549 | 30/07/2025 11:53:27.481 | 97.608 | 83 | 100 | 70 | 52 | 30.385 | 9.204 | 7.132 | 134.491 | 31.032 | 28.675 | 29.135 | 603.281 | 26.589 | 27.547 | 1284.804 | 27.346 | 27.751 | 40.196 | 28.001 | 2.8 | 3.5 | 0 | 0 | 0.3
4550 | 30/07/2025 11:53:29.116 | 97.056 | 83 | 99 | 70 | 52 | 32.628 | 9.134 | 7.188 | 134.482 | 31.045 | 28.694 | 29.142 | 603.067 | 26.593 | 27.553 | 1271.968 | 27.346 | 27.745 | 40.499 | 28.001 | 2.8 | 3.5 | 0 | 0 | 0.3
4551 | 30/07/2025 11:53:30.839 | 97.56 | 84 | 100 | 72 | 52 | 31.294 | 9.292 | 7.185 | 134.684 | 31.032 | 28.691 | 29.133 | 603.24 | 26.579 | 27.536 | 1272.86 | 27.341 | 27.719 | 39.95 | 32.001 | 2.1 | 4.7 | 0.1 | 1.6 | 0.4
4552 | 30/07/2025 11:53:32.474 | 97.656 | 84 | 100 | 70 | 50 | 28.597 | 9.134 | 7.186 | 134.503 | 31.028 | 28.697 | 29.125 | 603.104 | 26.581 | 27.545 | 1277.205 | 27.345 | 27.752 | 40.325 | 32.001 | 2.1 | 2.2 | 0.1 | 0.7 | 0.4
4553 | 30/07/2025 11:53:34.110 | 97.368 | 84 | 100 | 72 | 51 | 31.969 | 8.986 | 7.186 | 133.329 | 31.039 | 28.664 | 29.119 | 603.192 | 26.591 | 27.548 | 1279.274 | 27.324 | 27.754 | 40.317 | 29.001 | 1.5 | 4.5 | 0.6 | 1.1 | 0.3
4554 | 30/07/2025 11:53:35.747 | 97.488 | 84 | 100 | 71 | 52 | 28.674 | 8.985 | 7.186 | 133.024 | 31.032 | 28.674 | 29.14 | 603.288 | 26.589 | 27.553 | 1282.272 | 27.355 | 27.757 | 40.272 | 29.001 | 1.5 | 3.4 | 0.6 | 0.6 | 0.3
4555 | 30/07/2025 11:53:37.381 | 97.992 | 84 | 100 | 71 | 52 | 30.979 | 9 | 7.122 | 133.001 | 31.03 | 28.692 | 29.14 | 603.155 | 26.591 | 27.537 | 1269.942 | 27.339 | 27.728 | 40.238 | 28.001 | 2.4 | 2.2 | 0.7 | 0.5 | 0.3
4556 | 30/07/2025 11:53:39.017 | 98.592 | 83 | 100 | 70 | 52 | 32.726 | 9.131 | 7.094 | 133.28 | 31.035 | 28.696 | 29.152 | 603.212 | 26.578 | 27.532 | 1261.473 | 27.35 | 27.753 | 40.152 | 28.001 | 2.4 | 2.2 | 0.7 | 0.5 | 0.3
4557 | 30/07/2025 11:53:40.654 | 98.304 | 84 | 100 | 71 | 52 | 30.589 | 9.004 | 7.071 | 133.063 | 31.033 | 28.685 | 29.121 | 603.072 | 26.581 | 27.541 | 1257.556 | 27.33 | 27.767 | 40.388 | 28.001 | 2.4 | 3 | 0.7 | 0.6 | 0.3
4558 | 30/07/2025 11:53:42.291 | 98.52 | 84 | 100 | 68 | 52 | 28.823 | 9.067 | 7.058 | 133.133 | 31.028 | 28.673 | 29.139 | 604.199 | 26.599 | 27.518 | 1266.445 | 27.332 | 27.742 | 40.142 | 26.001 | 4.3 | 4.9 | 0.4 | 1.6 | 0.2
4559 | 30/07/2025 11:53:43.927 | 99.264 | 85 | 100 | 70 | 53 | 31.735 | 8.985 | 7.062 | 133.045 | 31.019 | 28.683 | 29.144 | 603.165 | 26.59 | 27.547 | 1274.468 | 27.355 | 27.747 | 40.223 | 26.001 | 4.3 | 4.8 | 0.4 | 0.4 | 0.2
4560 | 30/07/2025 11:53:45.564 | 99.192 | 86 | 99 | 70 | 52 | 28.487 | 9.13 | 7.058 | 133.181 | 31.024 | 28.695 | 29.151 | 603.298 | 26.594 | 27.539 | 1285.553 | 27.337 | 27.737 | 40.079 | 25.001 | 1 | 4.5 | 0.9 | 0.5 | 0.2
4561 | 30/07/2025 11:53:47.200 | 98.784 | 84 | 100 | 71 | 52 | 31.445 | 9.131 | 7.06 | 133.205 | 31.015 | 28.706 | 29.122 | 603.116 | 26.598 | 27.568 | 1289.851 | 27.34 | 27.745 | 40.188 | 25.001 | 1 | 4.5 | 0.9 | 0.5 | 0.2
4562 | 30/07/2025 11:53:48.833 | 98.448 | 84 | 100 | 69 | 52 | 32.761 | 8.988 | 7.07 | 133.367 | 31.011 | 28.68 | 29.118 | 603.128 | 26.61 | 27.568 | 1285.177 | 27.305 | 27.756 | 40.313 | 25.001 | 1 | 3.7 | 0.9 | 0.6 | 0.2
4563 | 30/07/2025 11:53:50.473 | 98.616 | 85 | 100 | 71 | 52 | 29.969 | 8.985 | 7.068 | 133.034 | 31.01 | 28.68 | 29.144 | 603.207 | 26.597 | 27.557 | 1284.773 | 27.365 | 27.764 | 40.145 | 27.001 | 1.8 | 2.4 | 0.2 | 1.2 | 0.1
4564 | 30/07/2025 11:53:52.105 | 98.16 | 84 | 100 | 69 | 53 | 32.577 | 9.02 | 7.071 | 132.929 | 31.032 | 28.687 | 29.15 | 603.183 | 26.6 | 27.559 | 1282.56 | 27.338 | 27.744 | 40.134 | 27.001 | 1.8 | 3.5 | 0.2 | 0.3 | 0.1
4565 | 30/07/2025 11:53:53.739 | 98.28 | 84 | 100 | 71 | 52 | 31.13 | 9.177 | 7.069 | 133.087 | 31.005 | 28.689 | 29.142 | 603.128 | 26.599 | 27.555 | 1287.255 | 27.363 | 27.74 | 39.984 | 26.001 | 2.9 | 4.3 | 0.6 | 0.5 | 0.2
4566 | 30/07/2025 11:53:55.374 | 98.136 | 84 | 100 | 70 | 51 | 28.531 | 9.132 | 7.076 | 133.323 | 31.007 | 28.685 | 29.115 | 603.206 | 26.599 | 27.564 | 1282.431 | 27.329 | 27.748 | 40.175 | 26.001 | 2.9 | 3 | 0.6 | 0.6 | 0.2
4567 | 30/07/2025 11:53:57.010 | 98.328 | 84 | 100 | 70 | 53 | 31.865 | 9.174 | 7.12 | 133.264 | 31.026 | 28.674 | 29.13 | 603.239 | 26.588 | 27.544 | 1276.886 | 27.315 | 27.752 | 40.372 | 26.001 | 2.9 | 3 | 0.6 | 0.6 | 0.2
4568 | 30/07/2025 11:53:58.642 | 98.016 | 83 | 100 | 70 | 52 | 32.683 | 8.989 | 7.133 | 134.265 | 31.028 | 28.682 | 29.15 | 603.166 | 26.583 | 27.558 | 1267.734 | 27.366 | 27.75 | 40.495 | 30.001 | 3.6 | 2.4 | 0.7 | 1.3 | 0.2
4569 | 30/07/2025 11:54:00.286 | 98.112 | 84 | 100 | 71 | 52 | 29.413 | 9.199 | 7.136 | 134.625 | 31.044 | 28.687 | 29.129 | 603.194 | 26.614 | 27.552 | 1262.154 | 27.347 | 27.721 | 40.282 | 30.001 | 3.6 | 4.1 | 0.7 | 0.7 | 0.2
4570 | 30/07/2025 11:54:01.921 | 98.856 | 84 | 100 | 72 | 52 | 32.706 | 9.287 | 7.136 | 134.596 | 31.032 | 28.689 | 29.134 | 603.208 | 26.591 | 27.551 | 1262.303 | 27.345 | 27.742 | 40.068 | 26.001 | 2.3 | 5.7 | 1.1 | 0.6 | 0.1
4571 | 30/07/2025 11:54:03.662 | 98.376 | 83 | 100 | 71 | 53 | 30.65 | 9.134 | 7.13 | 134.774 | 31.041 | 28.685 | 29.128 | 603.208 | 26.6 | 27.539 | 1262.337 | 27.31 | 27.752 | 40.244 | 26.001 | 2.3 | 2.6 | 1.1 | 0.5 | 0.1
4572 | 30/07/2025 11:54:05.458 | 98.04 | 84 | 100 | 70 | 52 | 28.85 | 9.074 | 7.12 | 134.623 | 31.02 | 28.67 | 29.138 | 603.176 | 26.587 | 27.544 | 1267.149 | 27.346 | 27.756 | 40.189 | 28.001 | 4.4 | 4.6 | 0.5 | 0.8 | 0.2
4573 | 30/07/2025 11:54:07.095 | 97.416 | 84 | 100 | 69 | 52 | 32.261 | 9.139 | 7.09 | 134.421 | 31.036 | 28.692 | 29.145 | 603.075 | 26.592 | 27.555 | 1256.27 | 27.353 | 27.744 | 40.332 | 28.001 | 4.4 | 4.6 | 0.5 | 0.8 | 0.2
4574 | 30/07/2025 11:54:08.729 | 97.224 | 84 | 100 | 70 | 52 | 32.679 | 8.968 | 7.089 | 134.695 | 31.042 | 28.695 | 29.153 | 603.274 | 26.569 | 27.536 | 1254.787 | 27.339 | 27.732 | 40.047 | 28.001 | 4.4 | 2.9 | 0.5 | 0.5 | 0.2
4575 | 30/07/2025 11:54:10.365 | 97.608 | 83 | 100 | 69 | 52 | 28.958 | 9.133 | 7.088 | 134.7 | 31.021 | 28.698 | 29.113 | 603.151 | 26.588 | 27.543 | 1260.16 | 27.333 | 27.752 | 40.29 | 26.001 | 3 | 3.7 | 0.3 | 0.2 | 0.1
4576 | 30/07/2025 11:54:12.000 | 97.776 | 84 | 100 | 70 | 52 | 30.473 | 9.28 | 7.087 | 134.868 | 31.025 | 28.664 | 29.131 | 603.14 | 26.596 | 27.533 | 1276.384 | 27.32 | 27.744 | 40.27 | 26.001 | 3 | 2.5 | 0.3 | 0.6 | 0.1
4577 | 30/07/2025 11:54:13.635 | 97.776 | 84 | 100 | 70 | 52 | 30.029 | 9.148 | 7.087 | 134.319 | 31.025 | 28.671 | 29.125 | 603.048 | 26.591 | 27.538 | 1282.953 | 27.342 | 27.754 | 40.381 | 22.001 | 3.8 | 3.2 | 0 | 0.8 | 0.2
4578 | 30/07/2025 11:54:15.274 | 97.32 | 83 | 100 | 70 | 52 | 29.313 | 8.921 | 7.133 | 134.504 | 31.029 | 28.695 | 29.15 | 603.046 | 26.596 | 27.532 | 1286.952 | 27.336 | 27.726 | 40.198 | 22.001 | 3.8 | 3.2 | 0 | 0.8 | 0.2
4579 | 30/07/2025 11:54:16.909 | 96.96 | 84 | 100 | 71 | 52 | 32.459 | 9.087 | 7.134 | 134.948 | 31.019 | 28.69 | 29.147 | 603.064 | 26.59 | 27.534 | 1292.059 | 27.349 | 27.767 | 40.032 | 22.001 | 3.8 | 3.9 | 0 | 0 | 0.2
4580 | 30/07/2025 11:54:18.545 | 97.344 | 83 | 100 | 71 | 52 | 32.233 | 9.209 | 7.152 | 134.683 | 31.024 | 28.686 | 29.112 | 603.078 | 26.594 | 27.539 | 1288.742 | 27.322 | 27.753 | 40.348 | 29.001 | 3.1 | 3.7 | 1 | 0.8 | 0.2
4581 | 30/07/2025 11:54:20.180 | 97.704 | 83 | 100 | 71 | 52 | 28.628 | 9.129 | 7.169 | 133.147 | 31.017 | 28.672 | 29.143 | 603.311 | 26.588 | 27.543 | 1295.671 | 27.339 | 27.742 | 38.79 | 29.001 | 3.1 | 4 | 1 | 0.5 | 0.2
4582 | 30/07/2025 11:54:21.815 | 97.608 | 83 | 100 | 70 | 51 | 32.756 | 9.212 | 7.187 | 133.193 | 31.027 | 28.685 | 29.158 | 603.056 | 26.618 | 27.564 | 1303.687 | 27.345 | 27.743 | 38.492 | 26.001 | 1.8 | 3.8 | 1.4 | 1.1 | 0.2
4583 | 30/07/2025 11:54:23.449 | 97.872 | 83 | 100 | 70 | 53 | 29.466 | 9.134 | 7.151 | 133.126 | 31.016 | 28.691 | 29.148 | 603.329 | 26.604 | 27.555 | 1294.578 | 27.343 | 27.745 | 38.259 | 26.001 | 1.8 | 3.3 | 1.4 | 1.1 | 0.2
4584 | 30/07/2025 11:54:25.085 | 97.248 | 83 | 100 | 70 | 52 | 29.787 | 9.286 | 7.152 | 133.19 | 31 | 28.699 | 29.127 | 603.268 | 26.595 | 27.568 | 1287.036 | 27.349 | 27.751 | 39.976 | 26.001 | 1.8 | 3.3 | 1.4 | 1.1 | 0.2
4585 | 30/07/2025 11:54:26.720 | 97.776 | 83 | 100 | 70 | 52 | 32.487 | 9.135 | 7.185 | 133.308 | 31.007 | 28.683 | 29.108 | 603.099 | 26.597 | 27.557 | 1295.972 | 27.303 | 27.752 | 40.297 | 32.001 | 3.2 | 4.1 | 0.5 | 0.5 | 0.1
4586 | 30/07/2025 11:54:28.356 | 97.536 | 82 | 100 | 70 | 53 | 31.742 | 8.99 | 7.151 | 133.226 | 30.997 | 28.666 | 29.144 | 603.112 | 26.6 | 27.55 | 1297.195 | 27.365 | 27.755 | 40.333 | 32.001 | 3.2 | 3.2 | 0.5 | 0.2 | 0.1
4587 | 30/07/2025 11:54:29.989 | 97.512 | 84 | 100 | 70 | 52 | 28.415 | 9.022 | 7.153 | 133.034 | 31.023 | 28.691 | 29.13 | 603.027 | 26.6 | 27.558 | 1295.552 | 27.345 | 27.73 | 40.127 | 28.001 | 1.6 | 3.8 | 0.7 | 0 | 0.1
4588 | 30/07/2025 11:54:31.625 | 97.704 | 84 | 100 | 70 | 52 | 32.546 | 9.136 | 7.134 | 133.058 | 31.021 | 28.691 | 29.134 | 603.233 | 26.589 | 27.56 | 1292.042 | 27.369 | 27.735 | 40.096 | 28.001 | 1.6 | 3.1 | 0.7 | 0.5 | 0.1
4589 | 30/07/2025 11:54:33.265 | 97.296 | 84 | 100 | 71 | 52 | 28.876 | 9.142 | 7.135 | 133.2 | 31.032 | 28.686 | 29.125 | 603.07 | 26.598 | 27.563 | 1285.303 | 27.323 | 27.76 | 40.225 | 28.001 | 1.6 | 3.1 | 0.7 | 0.5 | 0.1
4590 | 30/07/2025 11:54:34.900 | 97.008 | 84 | 100 | 70 | 52 | 30.238 | 9.215 | 7.133 | 133.249 | 31.054 | 28.676 | 29.131 | 603.362 | 26.585 | 27.534 | 1282.565 | 27.312 | 27.757 | 40.535 | 28.001 | 1.1 | 3.4 | 0.6 | 0.5 | 0.1
4591 | 30/07/2025 11:54:36.534 | 96.528 | 82 | 100 | 70 | 52 | 32.622 | 9.23 | 7.122 | 132.891 | 31.034 | 28.682 | 29.158 | 603.037 | 26.586 | 27.562 | 1281.348 | 27.357 | 27.754 | 40.317 | 28.001 | 1.1 | 3.4 | 0.6 | 0.1 | 0.1
4592 | 30/07/2025 11:54:38.169 | 95.856 | 82 | 100 | 70 | 52 | 31.305 | 8.987 | 7.121 | 133.098 | 31.051 | 28.692 | 29.14 | 603.157 | 26.612 | 27.545 | 1284.355 | 27.339 | 27.737 | 40.031 | 29.001 | 2.7 | 2.7 | 0.2 | 0 | 0.1
4593 | 30/07/2025 11:54:39.808 | 95.688 | 82 | 100 | 68 | 52 | 28.561 | 9.284 | 7.122 | 133.241 | 31.03 | 28.697 | 29.135 | 603.292 | 26.586 | 27.538 | 1283.53 | 27.364 | 27.757 | 40.049 | 29.001 | 2.7 | 2.6 | 0.2 | 0 | 0.1
4594 | 30/07/2025 11:54:41.444 | 95.688 | 82 | 100 | 70 | 52 | 32.372 | 9.424 | 7.12 | 133.375 | 31.04 | 28.688 | 29.132 | 603.16 | 26.583 | 27.536 | 1279.751 | 27.322 | 27.75 | 40.243 | 26.001 | 2.3 | 5.1 | 1.1 | 0 | 0.2
4595 | 30/07/2025 11:54:43.079 | 95.856 | 81 | 100 | 70 | 53 | 28.601 | 9.286 | 7.121 | 133.158 | 31.024 | 28.66 | 29.136 | 603.271 | 26.576 | 27.543 | 1277.167 | 27.343 | 27.754 | 40.384 | 26.001 | 2.3 | 5.1 | 1.1 | 0 | 0.2
4596 | 30/07/2025 11:54:44.720 | 96.456 | 83 | 100 | 71 | 52 | 31.048 | 9.133 | 7.128 | 132.9 | 31.026 | 28.691 | 29.143 | 603.12 | 26.582 | 27.546 | 1276.652 | 27.349 | 27.744 | 40.247 | 26.001 | 2.3 | 3 | 1.1 | 0.6 | 0.2
4597 | 30/07/2025 11:54:46.354 | 96.888 | 83 | 100 | 70 | 52 | 32.727 | 8.988 | 7.134 | 133.214 | 31.021 | 28.697 | 29.145 | 603.213 | 26.579 | 27.531 | 1269.396 | 27.349 | 27.725 | 39.938 | 28.001 | 2 | 3.3 | 0.7 | 0.1 | 0.2
4598 | 30/07/2025 11:54:47.991 | 97.176 | 84 | 100 | 70 | 52 | 30.609 | 9.236 | 7.134 | 133.181 | 31.036 | 28.683 | 29.129 | 603.186 | 26.585 | 27.536 | 1273.221 | 27.334 | 27.755 | 40.269 | 28.001 | 2 | 3.9 | 0.7 | 0.5 | 0.2
4599 | 30/07/2025 11:54:49.627 | 97.44 | 84 | 99 | 70 | 53 | 32.517 | 9.267 | 7.134 | 133.276 | 31.025 | 28.687 | 29.118 | 603.335 | 26.583 | 27.519 | 1267.257 | 27.32 | 27.76 | 40.155 | 24.001 | 2.1 | 3.7 | 1.3 | 0 | 0.2
4600 | 30/07/2025 11:54:51.262 | 97.32 | 84 | 100 | 70 | 52 | 31.81 | 9.129 | 7.12 | 132.939 | 31.028 | 28.669 | 29.135 | 603.232 | 26.592 | 27.541 | 1267.654 | 27.342 | 27.745 | 40.536 | 24.001 | 2.1 | 3.7 | 1.3 | 0 | 0.2
4601 | 30/07/2025 11:54:52.897 | 97.488 | 84 | 100 | 70 | 52 | 28.519 | 8.914 | 7.09 | 133.083 | 31.029 | 28.695 | 29.153 | 603.245 | 26.602 | 27.541 | 1267.256 | 27.344 | 27.746 | 40.206 | 24.001 | 2.1 | 4.2 | 1.3 | 0.6 | 0.2
4602 | 30/07/2025 11:54:54.533 | 97.848 | 83 | 100 | 70 | 52 | 31.525 | 9.136 | 7.087 | 133.24 | 31.004 | 28.705 | 29.133 | 603.124 | 26.597 | 27.564 | 1267.136 | 27.366 | 27.739 | 40.004 | 35.001 | 2.7 | 2.5 | 0.1 | 0.3 | 0.2
4603 | 30/07/2025 11:54:56.172 | 97.656 | 84 | 100 | 70 | 52 | 32.798 | 9.186 | 7.123 | 131.847 | 31.009 | 28.683 | 29.114 | 603.176 | 26.604 | 27.557 | 1276.935 | 27.319 | 27.756 | 40.225 | 35.001 | 2.7 | 3.6 | 0.1 | 0 | 0.2
4604 | 30/07/2025 11:54:57.807 | 98.328 | 84 | 100 | 71 | 52 | 30.387 | 9.216 | 7.121 | 131.623 | 31.008 | 28.682 | 29.117 | 603.109 | 26.601 | 27.581 | 1279.233 | 27.323 | 27.755 | 40.363 | 33.001 | 2.7 | 3.9 | 1.1 | 0.5 | 0.1
4605 | 30/07/2025 11:54:59.441 | 98.064 | 82 | 100 | 70 | 52 | 32.647 | 9.135 | 7.086 | 131.655 | 31.005 | 28.676 | 29.144 | 603.108 | 26.601 | 27.566 | 1279.556 | 27.34 | 27.751 | 40.18 | 33.001 | 2.7 | 3.1 | 1.1 | 0.1 | 0.1
4606 | 30/07/2025 11:55:01.077 | 98.496 | 85 | 100 | 71 | 52 | 31.264 | 9.174 | 7.104 | 131.523 | 31.004 | 28.694 | 29.145 | 603.161 | 26.58 | 27.549 | 1281.348 | 27.352 | 27.748 | 40.23 | 33.001 | 2.7 | 3.1 | 1.1 | 0.1 | 0.1
4607 | 30/07/2025 11:55:02.712 | 98.16 | 84 | 100 | 70 | 52 | 28.566 | 9.209 | 7.135 | 131.734 | 31.023 | 28.693 | 29.142 | 603.236 | 26.589 | 27.576 | 1292.743 | 27.34 | 27.746 | 40.076 | 30.001 | 3.1 | 2.8 | 1.2 | 1.9 | 0.1
4608 | 30/07/2025 11:55:04.348 | 98.4 | 84 | 100 | 71 | 52 | 31.851 | 9.054 | 7.134 | 131.98 | 31.045 | 28.68 | 29.112 | 603.281 | 26.585 | 27.551 | 1287.752 | 27.317 | 27.745 | 40.404 | 30.001 | 3.1 | 3.6 | 1.2 | 0.9 | 0.1
4609 | 30/07/2025 11:55:05.992 | 98.352 | 84 | 100 | 70 | 52 | 32.759 | 9.202 | 7.12 | 131.702 | 31.026 | 28.67 | 29.154 | 603.125 | 26.586 | 27.554 | 1277.077 | 27.364 | 27.756 | 40.278 | 26.001 | 2 | 2.8 | 0.9 | 0.5 | 0.1
4610 | 30/07/2025 11:55:07.627 | 98.52 | 84 | 100 | 71 | 52 | 30.807 | 9.22 | 7.119 | 131.644 | 31.035 | 28.687 | 29.167 | 603.216 | 26.59 | 27.532 | 1277.139 | 27.348 | 27.74 | 40.168 | 26.001 | 2 | 2.5 | 0.9 | 0.2 | 0.1
4611 | 30/07/2025 11:55:09.262 | 98.832 | 85 | 100 | 70 | 52 | 32.712 | 8.994 | 7.084 | 131.573 | 31.039 | 28.707 | 29.153 | 603.102 | 26.593 | 27.548 | 1282.584 | 27.368 | 27.739 | 40.204 | 26.001 | 2 | 2.5 | 0.9 | 0.2 | 0.1
4612 | 30/07/2025 11:55:10.898 | 99.48 | 85 | 100 | 70 | 52 | 30.565 | 9.133 | 7.07 | 131.839 | 31.044 | 28.69 | 29.134 | 603.125 | 26.598 | 27.566 | 1277.171 | 27.337 | 27.762 | 40.066 | 26.001 | 3.7 | 3.1 | 1.2 | 1 | 0.2
4613 | 30/07/2025 11:55:12.533 | 98.976 | 84 | 100 | 69 | 52 | 28.786 | 9.215 | 7.066 | 133.145 | 31.025 | 28.681 | 29.125 | 603.151 | 26.575 | 27.55 | 1279.245 | 27.307 | 27.754 | 40.497 | 26.001 | 3.7 | 2.5 | 1.2 | 1 | 0.2
4614 | 30/07/2025 11:55:14.170 | 98.976 | 84 | 99 | 70 | 52 | 32.276 | 9.131 | 7.073 | 133.065 | 31.033 | 28.678 | 29.128 | 603.095 | 26.577 | 27.566 | 1291.701 | 27.358 | 27.752 | 40.314 | 27.001 | 1.8 | 2.8 | 0.7 | 0 | 0.2
4615 | 30/07/2025 11:55:15.805 | 99.048 | 88 | 100 | 70 | 52 | 32.651 | 9.131 | 7.088 | 133.058 | 31.027 | 28.697 | 29.143 | 603.112 | 26.587 | 27.539 | 1285.527 | 27.341 | 27.722 | 39.938 | 27.001 | 1.8 | 1.2 | 0.7 | 0 | 0.2
4616 | 30/07/2025 11:55:17.442 | 99.24 | 84 | 100 | 71 | 52 | 31.502 | 9.13 | 7.089 | 133.04 | 31.03 | 28.691 | 29.134 | 602.984 | 26.581 | 27.544 | 1282.19 | 27.329 | 27.733 | 40.018 | 31.001 | 2.7 | 3.7 | 0.3 | 0 | 0.1
4617 | 30/07/2025 11:55:19.077 | 98.856 | 85 | 100 | 70 | 52 | 32.798 | 8.986 | 7.086 | 133.289 | 31.036 | 28.688 | 29.127 | 603.199 | 26.586 | 27.523 | 1277.425 | 27.321 | 27.743 | 40.216 | 31.001 | 2.7 | 3.7 | 0.3 | 0 | 0.1
4618 | 30/07/2025 11:55:20.715 | 98.784 | 84 | 100 | 70 | 52 | 30.024 | 9.289 | 7.119 | 133.197 | 31.03 | 28.674 | 29.138 | 603.257 | 26.565 | 27.532 | 1267.559 | 27.347 | 27.748 | 40.308 | 31.001 | 2.7 | 5.6 | 0.3 | 1 | 0.1
4619 | 30/07/2025 11:55:22.351 | 99.072 | 85 | 100 | 70 | 53 | 29.35 | 8.985 | 7.099 | 133.017 | 31.034 | 28.692 | 29.146 | 603.051 | 26.596 | 27.561 | 1271.69 | 27.351 | 27.74 | 40.091 | 28.001 | 1.9 | 4.2 | 0.7 | 0 | 0.2
4620 | 30/07/2025 11:55:23.985 | 98.784 | 84 | 100 | 71 | 52 | 32.423 | 8.991 | 7.086 | 133.03 | 31.026 | 28.696 | 29.139 | 603.093 | 26.589 | 27.518 | 1269.398 | 27.352 | 27.734 | 40.127 | 28.001 | 1.9 | 4.4 | 0.7 | 0.5 | 0.2
4621 | 30/07/2025 11:55:25.619 | 98.832 | 84 | 100 | 69 | 52 | 28.63 | 9.131 | 7.091 | 133.291 | 31.034 | 28.683 | 29.132 | 603.044 | 26.606 | 27.537 | 1266.994 | 27.335 | 27.739 | 40.089 | 22.001 | 2.8 | 4.7 | 0.6 | 1.1 | 0.2
4622 | 30/07/2025 11:55:27.253 | 98.496 | 86 | 100 | 71 | 52 | 31.978 | 9.132 | 7.121 | 133.158 | 31.021 | 28.691 | 29.125 | 603.27 | 26.592 | 27.546 | 1272.229 | 27.327 | 27.771 | 40.512 | 22.001 | 2.8 | 4.7 | 0.6 | 1.1 | 0.2
4623 | 30/07/2025 11:55:28.889 | 98.736 | 86 | 100 | 70 | 51 | 32.8 | 9.051 | 7.187 | 133.269 | 31.031 | 28.666 | 29.149 | 603.155 | 26.602 | 27.57 | 1278.496 | 27.338 | 27.755 | 40.292 | 22.001 | 2.8 | 4 | 0.6 | 0.9 | 0.2
4624 | 30/07/2025 11:55:30.524 | 98.328 | 84 | 100 | 70 | 52 | 29.53 | 8.989 | 7.158 | 132.956 | 31.013 | 28.697 | 29.144 | 603.204 | 26.6 | 27.546 | 1278.131 | 27.346 | 27.751 | 40.189 | 27.001 | 4.1 | 5.1 | 0.5 | 0.9 | 0.2
4625 | 30/07/2025 11:55:32.158 | 98.472 | 85 | 100 | 71 | 52 | 29.882 | 9.433 | 7.134 | 133.044 | 30.997 | 28.703 | 29.145 | 603.115 | 26.599 | 27.576 | 1273.895 | 27.358 | 27.73 | 39.841 | 27.001 | 4.1 | 2.3 | 0.5 | 0.6 | 0.2
4626 | 30/07/2025 11:55:33.795 | 98.496 | 86 | 100 | 70 | 53 | 30.671 | 9.295 | 7.135 | 133.308 | 31.005 | 28.686 | 29.14 | 603.254 | 26.586 | 27.567 | 1277.085 | 27.342 | 27.756 | 39.992 | 22.001 | 3.4 | 2.4 | 0.6 | 0.5 | 0.2
4627 | 30/07/2025 11:55:35.429 | 98.4 | 84 | 100 | 70 | 52 | 28.833 | 9.208 | 7.134 | 133.12 | 31.001 | 28.686 | 29.11 | 603.136 | 26.599 | 27.575 | 1266.36 | 27.322 | 27.756 | 40.367 | 22.001 | 3.4 | 3.7 | 0.6 | 0.6 | 0.2
4628 | 30/07/2025 11:55:37.067 | 98.544 | 83 | 100 | 70 | 52 | 32.174 | 9.132 | 7.124 | 133.11 | 31.011 | 28.674 | 29.152 | 603.127 | 26.613 | 27.551 | 1267.148 | 27.346 | 27.75 | 40.213 | 22.001 | 3.4 | 3.7 | 0.6 | 0.6 | 0.2
4629 | 30/07/2025 11:55:38.701 | 98.304 | 84 | 100 | 71 | 51 | 32.577 | 9.226 | 7.122 | 132.976 | 31.026 | 28.705 | 29.14 | 603.209 | 26.589 | 27.55 | 1274.404 | 27.353 | 27.751 | 40.282 | 26.001 | 3.5 | 5 | 1 | 0.7 | 0.2
4630 | 30/07/2025 11:55:40.336 | 98.736 | 83 | 100 | 70 | 52 | 29.021 | 9.433 | 7.122 | 133.186 | 31.038 | 28.692 | 29.145 | 603.076 | 26.598 | 27.574 | 1278.166 | 27.337 | 27.74 | 40.016 | 26.001 | 3.5 | 3.1 | 1 | 0.8 | 0.2
4631 | 30/07/2025 11:55:41.974 | 98.808 | 85 | 100 | 71 | 52 | 30.213 | 9.206 | 7.133 | 133.383 | 31.049 | 28.68 | 29.12 | 603.337 | 26.598 | 27.55 | 1277.442 | 27.31 | 27.749 | 40.468 | 33.001 | 2.8 | 4.6 | 1.2 | 0.5 | 0.2
4632 | 30/07/2025 11:55:43.608 | 97.992 | 85 | 100 | 70 | 51 | 30.043 | 8.988 | 7.133 | 133.211 | 31.045 | 28.67 | 29.122 | 603.054 | 26.6 | 27.572 | 1282.285 | 27.31 | 27.754 | 40.284 | 33.001 | 2.8 | 3.7 | 1.2 | 0.5 | 0.2
4633 | 30/07/2025 11:55:45.243 | 98.208 | 83 | 100 | 70 | 52 | 30.265 | 9.292 | 7.135 | 133.218 | 31.037 | 28.689 | 29.164 | 603.287 | 26.591 | 27.545 | 1276.748 | 27.345 | 27.752 | 40.152 | 33.001 | 2.8 | 3.7 | 1.2 | 0.5 | 0.2
4634 | 30/07/2025 11:55:46.876 | 97.872 | 83 | 99 | 69 | 52 | 32.45 | 9.289 | 7.128 | 132.861 | 31.032 | 28.711 | 29.137 | 603.061 | 26.582 | 27.555 | 1267.127 | 27.356 | 27.738 | 40.239 | 27.001 | 2.4 | 3.4 | 0.6 | 0.8 | 0.2
4635 | 30/07/2025 11:55:48.512 | 98.304 | 85 | 100 | 71 | 52 | 32.317 | 9.214 | 7.124 | 133.285 | 31.036 | 28.69 | 29.136 | 603.152 | 26.592 | 27.542 | 1255.911 | 27.332 | 27.751 | 39.876 | 27.001 | 2.4 | 4.8 | 0.6 | 0.4 | 0.2
4636 | 30/07/2025 11:55:50.148 | 98.4 | 83 | 100 | 70 | 52 | 28.597 | 9.131 | 7.12 | 133.218 | 31.025 | 28.686 | 29.123 | 603.262 | 26.572 | 27.529 | 1264.749 | 27.322 | 27.764 | 38.602 | 29.001 | 1 | 3.3 | 0.1 | 0 | 0.2
4637 | 30/07/2025 11:55:51.782 | 98.304 | 86 | 100 | 70 | 53 | 32.764 | 9.131 | 7.119 | 133.327 | 31.046 | 28.667 | 29.137 | 603.214 | 26.587 | 27.542 | 1267.128 | 27.336 | 27.758 | 38.34 | 29.001 | 1 | 4.5 | 0.1 | 0 | 0.2
4638 | 30/07/2025 11:55:53.415 | 98.496 | 85 | 100 | 70 | 52 | 29.354 | 9.134 | 7.121 | 132.958 | 31.021 | 28.7 | 29.149 | 603.214 | 26.579 | 27.535 | 1262.635 | 27.36 | 27.754 | 40.304 | 28.001 | 4.9 | 4.8 | 1 | 0.8 | 0.3
4639 | 30/07/2025 11:55:55.049 | 98.376 | 85 | 100 | 70 | 53 | 29.81 | 9.212 | 7.123 | 133.003 | 31.031 | 28.693 | 29.138 | 603 | 26.581 | 27.524 | 1264.603 | 27.336 | 27.731 | 38.5 | 28.001 | 4.9 | 4.8 | 1 | 0.8 | 0.3
4640 | 30/07/2025 11:55:56.689 | 97.992 | 84 | 100 | 70 | 52 | 32.502 | 9.287 | 7.133 | 133.207 | 31.032 | 28.688 | 29.142 | 603.319 | 26.58 | 27.518 | 1265.723 | 27.334 | 27.752 | 38.232 | 28.001 | 4.9 | 2.5 | 1 | 0.2 | 0.3
4641 | 30/07/2025 11:55:58.321 | 98.376 | 83 | 100 | 70 | 54 | 31.844 | 8.991 | 7.132 | 133.112 | 31.027 | 28.679 | 29.128 | 603.184 | 26.589 | 27.527 | 1265.235 | 27.338 | 27.747 | 38.591 | 35.001 | 3.1 | 2.4 | 0.9 | 0.6 | 0.3
4642 | 30/07/2025 11:55:59.956 | 98.52 | 84 | 100 | 71 | 52 | 28.478 | 9.289 | 7.136 | 133.035 | 31.025 | 28.69 | 29.136 | 603.009 | 26.608 | 27.539 | 1254.914 | 27.346 | 27.741 | 40.145 | 35.001 | 3.1 | 3.7 | 0.9 | 0.6 | 0.3
4643 | 30/07/2025 11:56:01.590 | 98.016 | 83 | 100 | 70 | 53 | 32.645 | 9.222 | 7.135 | 132.899 | 31.011 | 28.704 | 29.142 | 603.093 | 26.599 | 27.562 | 1250.148 | 27.347 | 27.74 | 40.328 | 29.001 | 2.3 | 2.9 | 0.7 | 1.3 | 0.2
4644 | 30/07/2025 11:56:03.226 | 98.664 | 85 | 100 | 70 | 53 | 29.015 | 9.285 | 7.135 | 133.134 | 31.036 | 28.692 | 29.148 | 603.102 | 26.618 | 27.557 | 1247.675 | 27.344 | 27.737 | 40.165 | 29.001 | 2.3 | 2.9 | 0.7 | 1.3 | 0.2
4645 | 30/07/2025 11:56:04.863 | 98.28 | 85 | 100 | 71 | 52 | 30.493 | 9.211 | 7.134 | 133.185 | 31.014 | 28.687 | 29.129 | 603.405 | 26.594 | 27.544 | 1247.846 | 27.339 | 27.756 | 40.573 | 29.001 | 2.3 | 3.1 | 0.7 | 0.8 | 0.2
4646 | 30/07/2025 11:56:06.498 | 98.04 | 84 | 100 | 70 | 52 | 32.651 | 8.996 | 7.15 | 133.287 | 30.996 | 28.672 | 29.144 | 603.111 | 26.594 | 27.56 | 1267.416 | 27.333 | 27.753 | 40.46 | 23.001 | 3.3 | 2.4 | 0.8 | 0.8 | 0.3
4647 | 30/07/2025 11:56:08.132 | 98.448 | 84 | 100 | 70 | 51 | 31.344 | 9.13 | 7.151 | 133.042 | 31.008 | 28.692 | 29.146 | 603.17 | 26.59 | 27.551 | 1261.649 | 27.356 | 27.748 | 40.103 | 23.001 | 3.3 | 4.3 | 0.8 | 0.6 | 0.3
4648 | 30/07/2025 11:56:09.768 | 98.208 | 85 | 100 | 70 | 52 | 32.48 | 9.133 | 7.154 | 133.111 | 31.009 | 28.695 | 29.131 | 603.063 | 26.598 | 27.572 | 1256.631 | 27.345 | 27.737 | 40.192 | 24.001 | 2.7 | 1.9 | 0.7 | 0.5 | 0.3
4649 | 30/07/2025 11:56:11.403 | 98.304 | 84 | 100 | 71 | 52 | 32.281 | 8.863 | 7.151 | 133.234 | 31.03 | 28.7 | 29.154 | 603.198 | 26.587 | 27.548 | 1248.773 | 27.347 | 27.757 | 39.979 | 24.001 | 2.7 | 3.9 | 0.7 | 0.8 | 0.3
4650 | 30/07/2025 11:56:13.038 | 97.224 | 83 | 100 | 70 | 52 | 28.699 | 9.132 | 7.186 | 133.002 | 31.021 | 28.683 | 29.117 | 603.237 | 26.592 | 27.577 | 1253.294 | 27.323 | 27.751 | 40.31 | 24.001 | 2.7 | 3.9 | 0.7 | 0.8 | 0.3
4651 | 30/07/2025 11:56:14.674 | 97.584 | 84 | 100 | 70 | 52 | 30.847 | 9.133 | 7.202 | 133.194 | 31.055 | 28.674 | 29.148 | 603.152 | 26.591 | 27.544 | 1265.095 | 27.337 | 27.748 | 40.347 | 35.001 | 2.7 | 2.8 | 0.9 | 0.5 | 0.3
4652 | 30/07/2025 11:56:16.310 | 97.728 | 84 | 100 | 70 | 52 | 32.742 | 9.292 | 7.203 | 132.824 | 31.047 | 28.695 | 29.141 | 603.225 | 26.59 | 27.543 | 1269.427 | 27.36 | 27.732 | 40.411 | 35.001 | 2.7 | 3.2 | 0.9 | 0.8 | 0.3
4653 | 30/07/2025 11:56:17.946 | 97.8 | 84 | 100 | 70 | 52 | 30.765 | 9.127 | 7.204 | 133.167 | 31.018 | 28.694 | 29.142 | 603.031 | 26.605 | 27.615 | 1267.023 | 27.343 | 27.744 | 40.088 | 20.001 | 3.2 | 2.1 | 1.2 | 0.1 | 0.2
4654 | 30/07/2025 11:56:19.581 | 97.536 | 85 | 100 | 70 | 52 | 32.533 | 8.988 | 7.203 | 132.986 | 31.032 | 28.69 | 29.129 | 603.237 | 26.586 | 27.693 | 1267.527 | 27.351 | 27.758 | 40.303 | 20.001 | 3.2 | 4 | 1.2 | 0 | 0.2
4655 | 30/07/2025 11:56:21.215 | 97.536 | 84 | 100 | 70 | 52 | 31.915 | 8.987 | 7.203 | 133.174 | 31.034 | 28.678 | 29.117 | 603.14 | 26.599 | 27.705 | 1270.469 | 27.309 | 27.75 | 40.429 | 20.001 | 3.2 | 4 | 1.2 | 0 | 0.2
4656 | 30/07/2025 11:56:22.858 | 97.344 | 84 | 100 | 70 | 52 | 28.486 | 9.176 | 7.203 | 133.175 | 31.028 | 28.682 | 29.159 | 603.213 | 26.586 | 27.69 | 1278.461 | 27.36 | 27.764 | 40.339 | 24.001 | 4.3 | 2.2 | 1.2 | 0.5 | 0.2
4657 | 30/07/2025 11:56:24.494 | 97.656 | 84 | 100 | 70 | 53 | 31.447 | 9.136 | 7.203 | 132.889 | 31.03 | 28.703 | 29.143 | 603.044 | 26.591 | 27.706 | 1269.787 | 27.357 | 27.737 | 40.378 | 24.001 | 4.3 | 4.6 | 1.2 | 0.7 | 0.2
4658 | 30/07/2025 11:56:26.131 | 97.512 | 84 | 100 | 71 | 52 | 32.8 | 9.284 | 7.187 | 133.188 | 31.043 | 28.692 | 29.133 | 603.198 | 26.575 | 27.675 | 1274.597 | 27.337 | 27.735 | 40.142 | 24.001 | 2.6 | 4.6 | 0.6 | 0.1 | 0.3
4659 | 30/07/2025 11:56:27.765 | 97.872 | 84 | 100 | 71 | 52 | 30.37 | 9.176 | 7.188 | 133.265 | 31.027 | 28.684 | 29.111 | 603.127 | 26.58 | 27.687 | 1274.357 | 27.334 | 27.753 | 40.196 | 24.001 | 2.6 | 4.5 | 0.6 | 0.5 | 0.3
4660 | 30/07/2025 11:56:29.399 | 97.776 | 83 | 100 | 70 | 52 | 32.658 | 9.147 | 7.201 | 133.452 | 31.027 | 28.672 | 29.142 | 603.256 | 26.575 | 27.67 | 1283.577 | 27.323 | 27.759 | 40.175 | 31.001 | 2.8 | 4.1 | 1 | 0.5 | 0.2
4661 | 30/07/2025 11:56:31.034 | 97.56 | 86 | 100 | 70 | 52 | 31.255 | 9.137 | 7.205 | 132.967 | 31.026 | 28.698 | 29.145 | 603.2 | 26.588 | 27.672 | 1276.851 | 27.367 | 27.748 | 40.053 | 31.001 | 2.8 | 4.1 | 1 | 0.5 | 0.2
4662 | 30/07/2025 11:56:32.669 | 97.632 | 84 | 100 | 70 | 52 | 28.552 | 9.134 | 7.204 | 133.063 | 31.029 | 28.696 | 29.142 | 603.062 | 26.604 | 27.692 | 1277.778 | 27.349 | 27.742 | 40.057 | 31.001 | 2.8 | 3.7 | 1 | 1.1 | 0.2
4663 | 30/07/2025 11:56:34.308 | 97.392 | 84 | 100 | 70 | 52 | 31.894 | 9.226 | 7.186 | 133.199 | 31.033 | 28.695 | 29.141 | 603.093 | 26.602 | 27.69 | 1277.119 | 27.336 | 27.757 | 40.14 | 26.001 | 1.8 | 3.1 | 1.9 | 0.8 | 0.2
4664 | 30/07/2025 11:56:35.946 | 97.632 | 84 | 100 | 70 | 52 | 32.77 | 9.136 | 7.151 | 133.12 | 31.01 | 28.678 | 29.134 | 603.227 | 26.606 | 27.713 | 1277.208 | 27.322 | 27.753 | 40.485 | 26.001 | 1.8 | 4 | 1.9 | 0.1 | 0.2
4665 | 30/07/2025 11:56:37.580 | 97.896 | 85 | 100 | 70 | 51 | 30.928 | 9.139 | 7.15 | 133.137 | 31.012 | 28.676 | 29.149 | 603.174 | 26.586 | 27.686 | 1277.347 | 27.344 | 27.762 | 40.353 | 26.001 | 2.7 | 2.8 | 0.9 | 0.5 | 0.2
4666 | 30/07/2025 11:56:39.215 | 98.28 | 83 | 100 | 70 | 52 | 32.677 | 9.136 | 7.136 | 132.887 | 31.004 | 28.697 | 29.14 | 603.071 | 26.601 | 27.715 | 1281.844 | 27.346 | 27.749 | 40.296 | 26.001 | 2.7 | 2.8 | 0.9 | 0.5 | 0.2
4667 | 30/07/2025 11:56:40.851 | 99 | 84 | 100 | 71 | 51 | 30.648 | 9.192 | 7.135 | 133.212 | 31.008 | 28.692 | 29.135 | 603.058 | 26.595 | 27.706 | 1284.491 | 27.351 | 27.732 | 39.748 | 26.001 | 2.7 | 2.5 | 0.9 | 0.5 | 0.2
4668 | 30/07/2025 11:56:42.487 | 98.52 | 85 | 100 | 71 | 52 | 28.924 | 9.142 | 7.134 | 133.125 | 31.002 | 28.699 | 29.127 | 603.2 | 26.606 | 27.714 | 1290.167 | 27.357 | 27.754 | 40.269 | 31.001 | 3.3 | 3.1 | 0.6 | 0 | 0.2
4669 | 30/07/2025 11:56:44.238 | 98.808 | 85 | 100 | 70 | 52 | 32.228 | 9.14 | 7.139 | 133.054 | 31.023 | 28.665 | 29.126 | 603.097 | 26.605 | 27.709 | 1283.836 | 27.327 | 27.738 | 40.284 | 31.001 | 3.3 | 3.2 | 0.6 | 0.5 | 0.2
4670 | 30/07/2025 11:56:45.873 | 99.288 | 86 | 100 | 70 | 52 | 32.625 | 9.206 | 7.152 | 132.988 | 31.033 | 28.689 | 29.158 | 603.251 | 26.588 | 27.687 | 1285.958 | 27.351 | 27.75 | 40.151 | 22.001 | 4 | 3.9 | 1.3 | 0.5 | 0.2
4671 | 30/07/2025 11:56:47.508 | 98.376 | 85 | 100 | 71 | 52 | 31.472 | 9.293 | 7.17 | 133.193 | 31.03 | 28.694 | 29.135 | 603.133 | 26.602 | 27.695 | 1294.345 | 27.349 | 27.729 | 40.194 | 22.001 | 4 | 4.7 | 1.3 | 0.5 | 0.2
4672 | 30/07/2025 11:56:49.144 | 98.184 | 84 | 100 | 71 | 52 | 32.764 | 9.003 | 7.186 | 133.239 | 31.035 | 28.699 | 29.133 | 603.16 | 26.588 | 27.692 | 1294.721 | 27.348 | 27.751 | 40.146 | 22.001 | 4 | 4.7 | 1.3 | 0.5 | 0.2
4673 | 30/07/2025 11:56:50.794 | 98.76 | 85 | 100 | 71 | 52 | 30.095 | 9.135 | 7.185 | 133.023 | 31.045 | 28.691 | 29.112 | 603.065 | 26.592 | 27.706 | 1287.905 | 27.321 | 27.751 | 40.337 | 25.001 | 3 | 3 | 1.2 | 0.5 | 0.2
4674 | 30/07/2025 11:56:52.429 | 98.304 | 84 | 100 | 71 | 52 | 29.16 | 9.13 | 7.201 | 133.229 | 31.045 | 28.672 | 29.15 | 603.216 | 26.612 | 27.69 | 1299.163 | 27.334 | 27.75 | 40.196 | 25.001 | 3 | 3.9 | 1.2 | 0.2 | 0.2
4675 | 30/07/2025 11:56:54.064 | 98.64 | 84 | 100 | 70 | 52 | 32.439 | 9.138 | 7.221 | 132.725 | 31.028 | 28.706 | 29.143 | 603.174 | 26.597 | 27.698 | 1302.013 | 27.368 | 27.743 | 40.247 | 26.001 | 3.2 | 4.1 | 1.3 | 0.6 | 0.2
4676 | 30/07/2025 11:56:55.699 | 98.328 | 84 | 99 | 71 | 52 | 32.367 | 9.153 | 7.187 | 133.179 | 31.032 | 28.689 | 29.135 | 603.203 | 26.588 | 27.702 | 1296.709 | 27.345 | 27.731 | 40.063 | 26.001 | 3.2 | 3.3 | 1.3 | 0.3 | 0.2
4677 | 30/07/2025 11:56:57.335 | 97.248 | 83 | 100 | 71 | 52 | 31.91 | 8.985 | 7.187 | 133.095 | 31.029 | 28.706 | 29.133 | 603.045 | 26.582 | 27.709 | 1288.591 | 27.352 | 27.754 | 40.123 | 26.001 | 3.2 | 3.3 | 1.3 | 0.3 | 0.2
4678 | 30/07/2025 11:56:58.971 | 97.272 | 84 | 100 | 71 | 52 | 32.797 | 9.213 | 7.185 | 133.184 | 31.039 | 28.67 | 29.118 | 603.105 | 26.6 | 27.694 | 1281.234 | 27.303 | 27.742 | 40.258 | 29.001 | 4.3 | 5 | 1.6 | 0.5 | 0.2
4679 | 30/07/2025 11:57:00.611 | 96.168 | 84 | 100 | 70 | 52 | 29.466 | 8.95 | 7.14 | 133.046 | 31.031 | 28.684 | 29.153 | 603.221 | 26.577 | 27.689 | 1287.037 | 27.345 | 27.76 | 40.31 | 29.001 | 4.3 | 4.7 | 1.6 | 0.8 | 0.2
4680 | 30/07/2025 11:57:02.247 | 95.544 | 82 | 100 | 69 | 54 | 29.705 | 9.216 | 7.136 | 134.339 | 31.015 | 28.691 | 29.125 | 603.234 | 26.579 | 27.689 | 1286.787 | 27.347 | 27.731 | 40.168 | 25.001 | 2.9 | 4.8 | 0.3 | 0.2 | 0.2
4681 | 30/07/2025 11:57:03.882 | 95.736 | 83 | 100 | 72 | 53 | 32.531 | 9.023 | 7.185 | 134.84 | 31.033 | 28.693 | 29.133 | 603.194 | 26.595 | 27.673 | 1273.018 | 27.338 | 27.742 | 39.962 | 25.001 | 2.9 | 3.7 | 0.3 | 0.5 | 0.2
4682 | 30/07/2025 11:57:06.433 | 95.616 | 83 | 100 | 70 | 52 | 31.858 | 9.135 | 7.185 | 134.685 | 31.012 | 28.681 | 29.113 | 602.431 | 26.585 | 27.674 | 1267.357 | 27.332 | 27.757 | 40.325 | 23.001 | 2.7 | 3.9 | 0.6 | 0.6 | 0.2
4683 | 30/07/2025 11:57:08.070 | 95.568 | 84 | 100 | 71 | 52 | 28.432 | 9.132 | 7.188 | 134.72 | 31.025 | 28.677 | 29.137 | 603.117 | 26.597 | 27.696 | 1266.316 | 27.344 | 27.758 | 40.282 | 23.001 | 2.7 | 4.6 | 0.6 | 0.8 | 0.2
4684 | 30/07/2025 11:57:09.704 | 96.408 | 82 | 100 | 70 | 52 | 31.472 | 8.99 | 7.135 | 133.963 | 31.025 | 28.7 | 29.155 | 603.241 | 26.6 | 27.694 | 1257.794 | 27.352 | 27.747 | 40.26 | 28.001 | 2.1 | 2.7 | 0.8 | 0.7 | 0.1
4685 | 30/07/2025 11:57:11.342 | 96.504 | 82 | 100 | 70 | 51 | 32.771 | 8.983 | 7.135 | 133.238 | 31.01 | 28.702 | 29.129 | 603.115 | 26.589 | 27.699 | 1252.729 | 27.354 | 27.74 | 40.22 | 28.001 | 2.1 | 6 | 0.8 | 1.4 | 0.1
4686 | 30/07/2025 11:57:12.985 | 96.936 | 83 | 100 | 71 | 52 | 30.096 | 9.129 | 7.135 | 133.415 | 31.015 | 28.684 | 29.115 | 601.877 | 26.616 | 27.697 | 1245.29 | 27.316 | 27.753 | 40.275 | 28.001 | 2.1 | 6 | 0.8 | 1.4 | 0.1
4687 | 30/07/2025 11:57:14.620 | 97.464 | 82 | 100 | 70 | 52 | 32.655 | 9.263 | 7.134 | 133 | 31 | 28.676 | 29.122 | 601.945 | 26.593 | 27.729 | 1242.378 | 27.32 | 27.75 | 40.683 | 23.001 | 2.9 | 2.9 | 1 | 0.3 | 0.2
4688 | 30/07/2025 11:57:16.260 | 97.896 | 85 | 100 | 72 | 52 | 31.32 | 9.126 | 7.136 | 133.031 | 31.014 | 28.684 | 29.144 | 602.025 | 26.588 | 27.694 | 1247.195 | 27.355 | 27.743 | 40.316 | 23.001 | 2.9 | 4.8 | 1 | 0.5 | 0.2
4689 | 30/07/2025 11:57:17.894 | 98.016 | 84 | 100 | 71 | 53 | 28.625 | 9.138 | 7.134 | 133.12 | 31.019 | 28.7 | 29.144 | 601.986 | 26.593 | 27.696 | 1250.831 | 27.37 | 27.751 | 40.248 | 29.001 | 2.6 | 4.9 | 0.6 | 0.5 | 0.2
4690 | 30/07/2025 11:57:19.535 | 98.616 | 86 | 100 | 70 | 52 | 31.895 | 8.989 | 7.135 | 133.436 | 31.023 | 28.696 | 29.134 | 601.828 | 26.593 | 27.698 | 1252.551 | 27.34 | 27.73 | 40.165 | 29.001 | 2.6 | 3.6 | 0.6 | 0.7 | 0.2
4691 | 30/07/2025 11:57:21.171 | 99.024 | 85 | 100 | 70 | 52 | 32.773 | 9.127 | 7.151 | 133.243 | 31.034 | 28.689 | 29.113 | 601.935 | 26.594 | 27.691 | 1257.844 | 27.308 | 27.752 | 40.302 | 29.001 | 2.6 | 3.6 | 0.6 | 0.7 | 0.2
4692 | 30/07/2025 11:57:22.806 | 99.12 | 85 | 100 | 71 | 52 | 29.592 | 8.987 | 7.152 | 132.968 | 31.038 | 28.674 | 29.137 | 603.229 | 26.589 | 27.715 | 1247.721 | 27.353 | 27.755 | 40.48 | 22.001 | 2.1 | 2.8 | 1.5 | 0.9 | 0.2
4693 | 30/07/2025 11:57:24.442 | 99 | 85 | 100 | 70 | 52 | 32.721 | 9.14 | 7.15 | 133.014 | 31.029 | 28.693 | 29.143 | 603.292 | 26.584 | 27.685 | 1249.757 | 27.358 | 27.744 | 40.344 | 22.001 | 2.1 | 1.9 | 1.5 | 0.7 | 0.2
4694 | 30/07/2025 11:57:26.081 | 98.568 | 86 | 100 | 71 | 52 | 30.858 | 9.138 | 7.151 | 133.041 | 31.037 | 28.692 | 29.129 | 603.135 | 26.592 | 27.71 | 1264.564 | 27.346 | 27.728 | 40.101 | 24.001 | 3.1 | 3.3 | 1.1 | 1.4 | 0.3
4695 | 30/07/2025 11:57:27.716 | 98.232 | 84 | 100 | 71 | 52 | 28.858 | 9.207 | 7.152 | 133.407 | 31.043 | 28.685 | 29.136 | 603.11 | 26.595 | 27.701 | 1274.135 | 27.33 | 27.759 | 40.054 | 24.001 | 3.1 | 3.2 | 1.1 | 0.7 | 0.3
4696 | 30/07/2025 11:57:29.352 | 98.328 | 85 | 100 | 70 | 51 | 32.343 | 8.988 | 7.149 | 133.244 | 31.031 | 28.682 | 29.11 | 603.2 | 26.579 | 27.695 | 1271.893 | 27.329 | 27.767 | 40.36 | 22.001 | 1.7 | 1.6 | 0.6 | 0 | 0.2
4697 | 30/07/2025 11:57:30.995 | 98.16 | 84 | 100 | 72 | 52 | 32.697 | 8.988 | 7.186 | 132.961 | 31.049 | 28.688 | 29.153 | 603.153 | 26.589 | 27.701 | 1276.933 | 27.352 | 27.755 | 40.299 | 22.001 | 1.7 | 1.6 | 0.6 | 0 | 0.2
4698 | 30/07/2025 11:57:32.631 | 98.04 | 86 | 100 | 70 | 52 | 29.107 | 9.13 | 7.185 | 133.014 | 31.031 | 28.697 | 29.144 | 603.174 | 26.575 | 27.69 | 1277.218 | 27.345 | 27.726 | 40.299 | 22.001 | 1.7 | 3.2 | 0.6 | 0.5 | 0.2
4699 | 30/07/2025 11:57:34.266 | 97.8 | 85 | 100 | 71 | 52 | 32.828 | 9.13 | 7.188 | 133.394 | 31.034 | 28.694 | 29.14 | 603.107 | 26.597 | 27.692 | 1276.038 | 27.336 | 27.728 | 40.102 | 29.001 | 2.2 | 2 | 0.9 | 0.6 | 0.3
4700 | 30/07/2025 11:57:35.899 | 97.632 | 84 | 100 | 70 | 51 | 30.145 | 9.131 | 7.186 | 133.396 | 31.038 | 28.692 | 29.145 | 602.619 | 26.58 | 27.669 | 1268.126 | 27.324 | 27.77 | 38.409 | 29.001 | 2.2 | 4.3 | 0.9 | 0.8 | 0.3
4701 | 30/07/2025 11:57:37.535 | 97.704 | 84 | 100 | 71 | 52 | 29.221 | 9.282 | 7.185 | 133.272 | 31.03 | 28.675 | 29.129 | 601.733 | 26.563 | 27.684 | 1267.388 | 27.333 | 27.742 | 40.469 | 29.001 | 3 | 4.3 | 0.9 | 0.6 | 0.3
4702 | 30/07/2025 11:57:39.170 | 97.68 | 84 | 100 | 71 | 52 | 32.432 | 9.217 | 7.134 | 133.117 | 31.029 | 28.693 | 29.146 | 602.062 | 26.597 | 27.684 | 1267.265 | 27.343 | 27.744 | 38.604 | 29.001 | 3 | 4.3 | 0.9 | 0.6 | 0.3
4703 | 30/07/2025 11:57:40.806 | 97.512 | 83 | 100 | 70 | 52 | 32.428 | 9.211 | 7.134 | 133.012 | 31.02 | 28.703 | 29.141 | 602.045 | 26.594 | 27.679 | 1276.442 | 27.358 | 27.741 | 38.354 | 29.001 | 3 | 3.1 | 0.9 | 0.5 | 0.3
4704 | 30/07/2025 11:57:42.444 | 97.368 | 83 | 100 | 70 | 53 | 31.854 | 9.214 | 7.15 | 133.35 | 31.035 | 28.687 | 29.143 | 601.862 | 26.595 | 27.673 | 1276.922 | 27.337 | 27.746 | 38.164 | 27.001 | 2.4 | 4.5 | 0.8 | 0.5 | 0.2
4705 | 30/07/2025 11:57:44.080 | 97.44 | 86 | 100 | 70 | 52 | 32.803 | 8.988 | 7.135 | 133.149 | 31.02 | 28.692 | 29.122 | 601.761 | 26.595 | 27.694 | 1282.594 | 27.342 | 27.753 | 40.301 | 27.001 | 2.4 | 2.9 | 0.8 | 0.6 | 0.2
4706 | 30/07/2025 11:57:45.714 | 96.528 | 84 | 100 | 70 | 52 | 29.416 | 8.984 | 7.135 | 133.207 | 31.012 | 28.672 | 29.128 | 601.952 | 26.611 | 27.711 | 1279.085 | 27.349 | 27.74 | 40.452 | 29.001 | 3.3 | 5.1 | 0.7 | 1.1 | 0.3
4707 | 30/07/2025 11:57:47.348 | 96.84 | 83 | 100 | 71 | 50 | 29.791 | 9.135 | 7.134 | 134.36 | 31.015 | 28.699 | 29.157 | 602.114 | 26.594 | 27.691 | 1262.668 | 27.349 | 27.746 | 40.314 | 29.001 | 3.3 | 4.5 | 0.7 | 0.5 | 0.3
4708 | 30/07/2025 11:57:48.987 | 96.936 | 82 | 100 | 71 | 52 | 32.56 | 9.133 | 7.134 | 134.641 | 31.005 | 28.7 | 29.133 | 601.908 | 26.591 | 27.726 | 1263.893 | 27.346 | 27.748 | 40.046 | 29.001 | 3.3 | 4.5 | 0.7 | 0.5 | 0.3
4709 | 30/07/2025 11:57:50.623 | 97.416 | 85 | 100 | 70 | 52 | 31.854 | 8.991 | 7.134 | 133.203 | 31.019 | 28.691 | 29.113 | 601.951 | 26.611 | 27.703 | 1260.623 | 27.331 | 27.759 | 40.328 | 22.001 | 2 | 2.9 | 0.6 | 0.5 | 0.3
4710 | 30/07/2025 11:57:52.259 | 97.344 | 84 | 100 | 70 | 53 | 32.209 | 8.989 | 7.135 | 133.059 | 31.017 | 28.68 | 29.119 | 601.753 | 26.601 | 27.72 | 1257.271 | 27.317 | 27.755 | 40.33 | 22.001 | 2 | 3.6 | 0.6 | 0.7 | 0.3
4711 | 30/07/2025 11:57:53.901 | 97.104 | 84 | 100 | 70 | 53 | 32.591 | 9.286 | 7.185 | 133.237 | 31.02 | 28.683 | 29.161 | 603.27 | 26.603 | 27.697 | 1248.079 | 27.344 | 27.757 | 38.433 | 23.001 | 1.9 | 4.3 | 0.6 | 0.1 | 0.2
4712 | 30/07/2025 11:57:55.536 | 97.176 | 84 | 100 | 70 | 52 | 28.929 | 9.137 | 7.186 | 132.875 | 31.033 | 28.702 | 29.142 | 603.1 | 26.588 | 27.704 | 1237.223 | 27.358 | 27.741 | 38.357 | 23.001 | 1.9 | 5.7 | 0.6 | 0 | 0.2
4713 | 30/07/2025 11:57:57.172 | 96.984 | 83 | 100 | 70 | 52 | 30.284 | 9.128 | 7.171 | 133.325 | 31.038 | 28.691 | 29.144 | 603.075 | 26.6 | 27.706 | 1254.998 | 27.341 | 27.743 | 38.408 | 23.001 | 1.9 | 5.7 | 0.6 | 0 | 0.2
4714 | 30/07/2025 11:57:58.809 | 97.32 | 83 | 100 | 68 | 52 | 32.657 | 9.216 | 7.133 | 133.165 | 31.031 | 28.682 | 29.13 | 603.167 | 26.582 | 27.684 | 1247.631 | 27.313 | 27.747 | 40.405 | 24.001 | 1.6 | 2.6 | 1.7 | 0.5 | 0.2
4715 | 30/07/2025 11:58:00.452 | 97.68 | 85 | 100 | 71 | 52 | 29.232 | 9.212 | 7.127 | 133.111 | 31.044 | 28.666 | 29.116 | 603.044 | 26.608 | 27.706 | 1237.485 | 27.318 | 27.759 | 38.957 | 24.001 | 1.6 | 3 | 1.7 | 0.5 | 0.2
4716 | 30/07/2025 11:58:02.087 | 97.488 | 84 | 100 | 71 | 52 | 32.492 | 9.204 | 7.121 | 132.871 | 31.033 | 28.69 | 29.156 | 603.191 | 26.586 | 27.698 | 1240.594 | 27.362 | 27.76 | 38.432 | 29.001 | 2.2 | 3.2 | 0.6 | 0.5 | 0.2
4717 | 30/07/2025 11:58:03.722 | 97.872 | 83 | 100 | 70 | 52 | 32.457 | 9.137 | 7.123 | 132.859 | 31.029 | 28.695 | 29.14 | 601.848 | 26.583 | 27.706 | 1246.732 | 27.341 | 27.734 | 38.443 | 29.001 | 2.2 | 3.3 | 0.6 | 1.4 | 0.2
4718 | 30/07/2025 11:58:05.359 | 97.824 | 84 | 100 | 70 | 52 | 28.732 | 9.154 | 7.11 | 133.149 | 31.046 | 28.689 | 29.141 | 603.267 | 26.583 | 27.677 | 1237.088 | 27.336 | 27.758 | 38.177 | 33.001 | 2.6 | 3.7 | 0.7 | 0.3 | 0.3
4719 | 30/07/2025 11:58:06.991 | 98.088 | 84 | 100 | 70 | 52 | 31.031 | 8.991 | 7.084 | 133.228 | 31.022 | 28.671 | 29.127 | 603.237 | 26.718 | 27.683 | 1247.121 | 27.332 | 27.757 | 40.371 | 33.001 | 2.6 | 3.7 | 0.7 | 0.3 | 0.3
4720 | 30/07/2025 11:58:08.626 | 98.28 | 84 | 100 | 70 | 50 | 32.739 | 9.216 | 7.072 | 133.182 | 31.024 | 28.678 | 29.142 | 602.954 | 26.581 | 27.691 | 1256.942 | 27.357 | 27.741 | 40.192 | 33.001 | 2.6 | 3.7 | 0.7 | 0 | 0.3
4721 | 30/07/2025 11:58:10.262 | 98.832 | 84 | 100 | 70 | 51 | 29.702 | 9.214 | 7.07 | 132.816 | 31.024 | 28.708 | 29.153 | 603.184 | 26.736 | 27.687 | 1255.2 | 27.359 | 27.753 | 40.182 | 27.001 | 2.3 | 5.3 | 0 | 0 | 0.2
4722 | 30/07/2025 11:58:11.898 | 98.496 | 86 | 99 | 70 | 52 | 32.597 | 9.132 | 7.071 | 133.074 | 31.044 | 28.689 | 29.145 | 601.856 | 26.637 | 27.678 | 1252.193 | 27.34 | 27.728 | 40.116 | 27.001 | 2.3 | 5.7 | 0 | 0 | 0.2
4723 | 30/07/2025 11:58:13.532 | 98.4 | 84 | 100 | 70 | 52 | 31.95 | 9.211 | 7.07 | 133.22 | 31.026 | 28.693 | 29.128 | 603.288 | 26.596 | 27.664 | 1253.515 | 27.335 | 27.765 | 40.341 | 26.001 | 1.5 | 4.9 | 1.3 | 0.5 | 0.2
4724 | 30/07/2025 11:58:15.174 | 98.688 | 85 | 100 | 71 | 51 | 28.529 | 9.199 | 7.069 | 133.144 | 31.028 | 28.668 | 29.129 | 603.121 | 26.744 | 27.685 | 1266.608 | 27.323 | 27.753 | 40.542 | 26.001 | 1.5 | 4.9 | 1.3 | 0.5 | 0.2
4725 | 30/07/2025 11:58:16.810 | 98.376 | 84 | 99 | 71 | 53 | 31.526 | 8.91 | 7.059 | 133.022 | 31.013 | 28.695 | 29.145 | 603.095 | 26.604 | 27.692 | 1265.928 | 27.353 | 27.745 | 40.37 | 26.001 | 1.5 | 2.3 | 1.3 | 0.6 | 0.2
4726 | 30/07/2025 11:58:18.446 | 98.28 | 84 | 100 | 71 | 52 | 29.028 | 8.912 | 7.062 | 132.957 | 31.01 | 28.702 | 29.127 | 603.071 | 26.743 | 27.701 | 1269.388 | 27.349 | 27.725 | 40.372 | 27.001 | 2.1 | 2.6 | 2.7 | 1.1 | 0.2
4727 | 30/07/2025 11:58:20.080 | 97.8 | 85 | 100 | 70 | 52 | 30.382 | 9.133 | 7.058 | 133.184 | 31.019 | 28.692 | 29.15 | 603.256 | 26.756 | 27.705 | 1273.615 | 27.344 | 27.744 | 39.947 | 27.001 | 2.1 | 3.6 | 2.7 | 0.6 | 0.2
4728 | 30/07/2025 11:58:21.716 | 98.136 | 86 | 100 | 70 | 53 | 32.691 | 9.111 | 7.059 | 132.987 | 30.989 | 28.694 | 29.123 | 603.1 | 26.748 | 27.712 | 1275.209 | 27.329 | 27.746 | 40.377 | 25.001 | 2.6 | 4.3 | 0.6 | 0.7 | 0.3
4729 | 30/07/2025 11:58:23.352 | 98.328 | 84 | 100 | 69 | 53 | 31.209 | 8.995 | 7.087 | 134.628 | 30.992 | 28.663 | 29.125 | 603.044 | 26.612 | 27.703 | 1279.403 | 27.338 | 27.743 | 40.22 | 25.001 | 2.6 | 5.3 | 0.6 | 0.5 | 0.3
4730 | 30/07/2025 11:58:24.990 | 97.968 | 84 | 100 | 70 | 52 | 28.534 | 9.286 | 7.131 | 134.382 | 31.017 | 28.696 | 29.142 | 603.185 | 26.755 | 27.698 | 1282.538 | 27.362 | 27.749 | 40.342 | 25.001 | 2.6 | 5.3 | 0.6 | 0.5 | 0.3
4731 | 30/07/2025 11:58:26.626 | 97.848 | 84 | 100 | 70 | 52 | 31.835 | 8.998 | 7.135 | 134.753 | 31.027 | 28.692 | 29.126 | 603.134 | 26.752 | 27.713 | 1279.504 | 27.347 | 27.72 | 40.149 | 23.001 | 2.4 | 3.5 | 1.2 | 0.9 | 0.3
4732 | 30/07/2025 11:58:28.264 | 97.392 | 84 | 100 | 71 | 52 | 28.636 | 9.197 | 7.142 | 134.593 | 31.023 | 28.697 | 29.125 | 603.139 | 26.742 | 27.7 | 1277.046 | 27.36 | 27.758 | 40.097 | 23.001 | 2.4 | 2.3 | 1.2 | 0.8 | 0.3
4733 | 30/07/2025 11:58:29.900 | 97.728 | 83 | 100 | 71 | 52 | 30.813 | 9.132 | 7.152 | 134.511 | 31.028 | 28.681 | 29.107 | 603.115 | 26.744 | 27.709 | 1274.65 | 27.29 | 27.744 | 40.164 | 29.001 | 1.8 | 2.7 | 0.6 | 2 | 0.2
4734 | 30/07/2025 11:58:31.533 | 97.944 | 86 | 100 | 71 | 52 | 32.72 | 9.214 | 7.151 | 134.628 | 31.046 | 28.676 | 29.155 | 603.09 | 26.747 | 27.698 | 1276.953 | 27.347 | 27.754 | 40.083 | 29.001 | 1.8 | 3.8 | 0.6 | 0.8 | 0.2
4735 | 30/07/2025 11:58:33.168 | 97.992 | 84 | 100 | 71 | 52 | 30.802 | 9.208 | 7.09 | 134.395 | 31.03 | 28.704 | 29.136 | 603.078 | 26.74 | 27.695 | 1279.421 | 27.358 | 27.74 | 40.244 | 29.001 | 1.8 | 3.8 | 0.6 | 0.8 | 0.2
4736 | 30/07/2025 11:58:34.802 | 97.416 | 84 | 100 | 71 | 52 | 28.852 | 9.179 | 7.085 | 134.646 | 31.047 | 28.691 | 29.138 | 603.252 | 26.734 | 27.708 | 1274.225 | 27.339 | 27.737 | 39.921 | 27.001 | 4.4 | 5 | 0.6 | 0.9 | 0.2
4737 | 30/07/2025 11:58:36.437 | 97.128 | 84 | 100 | 70 | 52 | 32.011 | 8.986 | 7.087 | 134.569 | 31.042 | 28.691 | 29.121 | 603.185 | 26.589 | 27.711 | 1266.996 | 27.34 | 27.766 | 40.202 | 27.001 | 4.4 | 3.6 | 0.6 | 0.3 | 0.2
4738 | 30/07/2025 11:58:38.072 | 97.008 | 84 | 100 | 69 | 52 | 28.581 | 8.983 | 7.086 | 134.596 | 31.041 | 28.669 | 29.127 | 603.103 | 26.722 | 27.688 | 1277.771 | 27.306 | 27.745 | 38.516 | 24.001 | 3.1 | 3.3 | 0.3 | 0 | 0.2
4739 | 30/07/2025 11:58:39.707 | 97.104 | 84 | 100 | 70 | 51 | 31.535 | 8.991 | 7.086 | 134.514 | 31.031 | 28.691 | 29.151 | 603.057 | 26.605 | 27.68 | 1281.387 | 27.367 | 27.759 | 40.25 | 24.001 | 3.1 | 3.8 | 0.3 | 0 | 0.2
4740 | 30/07/2025 11:58:41.343 | 97.44 | 85 | 100 | 71 | 52 | 32.806 | 9.136 | 7.07 | 134.361 | 31.026 | 28.686 | 29.143 | 603.106 | 26.58 | 27.689 | 1276.838 | 27.347 | 27.739 | 40.062 | 22.001 | 1.5 | 2.5 | 0.7 | 0.6 | 0.2
4741 | 30/07/2025 11:58:42.994 | 97.464 | 83 | 100 | 70 | 52 | 30.171 | 9.264 | 7.07 | 134.83 | 31.03 | 28.691 | 29.142 | 603.291 | 26.584 | 27.684 | 1267.157 | 27.342 | 27.755 | 40.009 | 22.001 | 1.5 | 2.5 | 0.7 | 0.6 | 0.2
4742 | 30/07/2025 11:58:44.628 | 97.368 | 83 | 100 | 70 | 52 | 29.285 | 9.137 | 7.07 | 134.584 | 31.028 | 28.677 | 29.119 | 603.155 | 26.729 | 27.692 | 1269.827 | 27.326 | 27.756 | 40.432 | 22.001 | 1.5 | 2.7 | 0.7 | 0.1 | 0.2
4743 | 30/07/2025 11:58:46.260 | 97.248 | 84 | 100 | 70 | 52 | 31.455 | 9.214 | 7.067 | 134.621 | 31.026 | 28.68 | 29.146 | 603.298 | 26.729 | 27.667 | 1267.981 | 27.333 | 27.75 | 40.139 | 23.001 | 2.6 | 2.5 | 0.8 | 0 | 0.2
4744 | 30/07/2025 11:58:47.898 | 96.72 | 84 | 100 | 71 | 53 | 28.563 | 9.282 | 7.088 | 134.428 | 31.031 | 28.695 | 29.138 | 602.978 | 26.594 | 27.689 | 1267.02 | 27.363 | 27.75 | 40.36 | 23.001 | 2.6 | 2 | 0.8 | 1 | 0.2
4745 | 30/07/2025 11:58:49.531 | 96.24 | 82 | 100 | 70 | 54 | 31.932 | 9.287 | 7.088 | 134.671 | 31.026 | 28.686 | 29.132 | 603.108 | 26.764 | 27.692 | 1264.424 | 27.335 | 27.718 | 40.001 | 24.001 | 4.3 | 2.2 | 0.3 | 1 | 0.2
4746 | 30/07/2025 11:58:51.164 | 96.48 | 83 | 100 | 70 | 52 | 32.82 | 9.129 | 7.086 | 134.794 | 31.014 | 28.696 | 29.139 | 603.207 | 26.612 | 27.696 | 1259.822 | 27.345 | 27.767 | 40.1 | 24.001 | 4.3 | 2.2 | 0.3 | 1 | 0.2
4747 | 30/07/2025 11:58:52.797 | 95.856 | 82 | 100 | 70 | 52 | 29.653 | 9.216 | 7.086 | 134.471 | 31.007 | 28.674 | 29.125 | 603.051 | 26.6 | 27.703 | 1247.199 | 27.323 | 27.745 | 40.467 | 24.001 | 4.3 | 3.4 | 0.3 | 0.3 | 0.2
4748 | 30/07/2025 11:58:54.433 | 96.096 | 83 | 100 | 70 | 52 | 32.792 | 8.996 | 7.085 | 134.752 | 31.001 | 28.67 | 29.15 | 603.224 | 26.725 | 27.698 | 1246.219 | 27.365 | 27.759 | 40.432 | 25.001 | 2.8 | 3.1 | 0 | 0.5 | 0.2
4749 | 30/07/2025 11:58:56.068 | 96.36 | 82 | 100 | 70 | 52 | 30.762 | 9.132 | 7.09 | 134.582 | 31.005 | 28.699 | 29.144 | 602.99 | 26.614 | 27.71 | 1248.574 | 27.349 | 27.735 | 40.421 | 25.001 | 2.8 | 4.2 | 0 | 0.5 | 0.2
4750 | 30/07/2025 11:58:57.702 | 95.736 | 82 | 100 | 71 | 53 | 28.813 | 9.137 | 7.088 | 134.667 | 31.004 | 28.695 | 29.145 | 604.495 | 26.743 | 27.709 | 1249.261 | 27.347 | 27.759 | 39.888 | 25.001 | 2 | 3.5 | 0.6 | 0.1 | 0.2
4751 | 30/07/2025 11:58:59.339 | 96.864 | 83 | 100 | 70 | 52 | 32.196 | 9.063 | 7.088 | 133.144 | 31.004 | 28.694 | 29.122 | 604.455 | 26.594 | 27.708 | 1249.383 | 27.324 | 27.749 | 40.355 | 25.001 | 2 | 2.1 | 0.6 | 0.5 | 0.2
4752 | 30/07/2025 11:59:00.994 | 97.2 | 82 | 100 | 70 | 53 | 32.63 | 9.136 | 7.084 | 133.348 | 31.032 | 28.662 | 29.135 | 604.441 | 26.608 | 27.692 | 1252.148 | 27.321 | 27.741 | 40.144 | 25.001 | 2 | 2.1 | 0.6 | 0.5 | 0.2
4753 | 30/07/2025 11:59:02.660 | 97.224 | 83 | 100 | 70 | 52 | 31.322 | 9.163 | 7.088 | 132.96 | 31.022 | 28.671 | 29.15 | 604.133 | 26.587 | 27.71 | 1256.927 | 27.341 | 27.743 | 40.321 | 22.001 | 3.1 | 2.6 | 0.7 | 0 | 0.2
4754 | 30/07/2025 11:59:04.294 | 97.344 | 84 | 100 | 70 | 52 | 32.772 | 9.241 | 7.086 | 133.03 | 31.056 | 28.7 | 29.143 | 604.236 | 26.686 | 27.701 | 1260.237 | 27.341 | 27.748 | 40.034 | 22.001 | 3.1 | 4.5 | 0.7 | 0 | 0.2
4755 | 30/07/2025 11:59:05.929 | 97.608 | 84 | 100 | 71 | 52 | 30.13 | 8.986 | 7.069 | 133.208 | 31.022 | 28.699 | 29.134 | 604.531 | 26.733 | 27.698 | 1270.06 | 27.36 | 27.749 | 40.1 | 23.001 | 2 | 5.4 | 0.7 | 0.5 | 0.2
4756 | 30/07/2025 11:59:07.565 | 97.584 | 83 | 100 | 70 | 52 | 29.172 | 9.131 | 7.069 | 133.144 | 31.036 | 28.68 | 29.119 | 605.563 | 26.744 | 27.705 | 1259.804 | 27.305 | 27.762 | 40.423 | 23.001 | 2 | 4.4 | 0.7 | 0.6 | 0.2
4757 | 30/07/2025 11:59:09.200 | 97.32 | 84 | 100 | 70 | 52 | 32.435 | 8.981 | 7.083 | 133.138 | 31.039 | 28.678 | 29.154 | 606.958 | 26.58 | 27.694 | 1254.922 | 27.339 | 27.746 | 40.203 | 23.001 | 2 | 4.4 | 0.7 | 0.6 | 0.2
4758 | 30/07/2025 11:59:10.835 | 97.128 | 84 | 100 | 71 | 52 | 32.377 | 8.987 | 7.095 | 132.902 | 31.022 | 28.708 | 29.132 | 606.819 | 26.722 | 27.698 | 1260.752 | 27.346 | 27.736 | 40.229 | 23.001 | 2.2 | 4.5 | 0.7 | 0 | 0.1
4759 | 30/07/2025 11:59:12.469 | 97.272 | 84 | 100 | 70 | 53 | 31.922 | 9.273 | 7.122 | 133.16 | 31.03 | 28.7 | 29.144 | 606.828 | 26.579 | 27.684 | 1264.744 | 27.343 | 27.733 | 40.018 | 23.001 | 2.2 | 3.6 | 0.7 | 0.5 | 0.1
4760 | 30/07/2025 11:59:14.104 | 97.392 | 84 | 100 | 70 | 52 | 32.777 | 9.131 | 7.122 | 133.107 | 31.028 | 28.691 | 29.125 | 606.83 | 26.588 | 27.706 | 1261.826 | 27.338 | 27.76 | 40.204 | 20.001 | 2.1 | 3.7 | 1 | 0.1 | 0.1
4761 | 30/07/2025 11:59:15.737 | 97.416 | 83 | 100 | 70 | 52 | 29.555 | 9.304 | 7.12 | 133.288 | 31.037 | 28.675 | 29.107 | 605.648 | 26.722 | 27.69 | 1261.852 | 27.309 | 27.753 | 40.254 | 20.001 | 2.1 | 1.9 | 1 | 0 | 0.1
4762 | 30/07/2025 11:59:17.372 | 97.104 | 82 | 100 | 71 | 52 | 29.726 | 9.136 | 7.121 | 133.125 | 31.017 | 28.684 | 29.152 | 604.365 | 26.575 | 27.678 | 1268.409 | 27.368 | 27.748 | 40.279 | 23.001 | 2.9 | 1.3 | 0 | 1 | 0.2
4763 | 30/07/2025 11:59:19.006 | 96.912 | 84 | 100 | 71 | 52 | 32.574 | 9.165 | 7.123 | 132.996 | 31.029 | 28.695 | 29.128 | 604.2 | 26.587 | 27.69 | 1264.681 | 27.346 | 27.729 | 40.309 | 23.001 | 2.9 | 1.3 | 0 | 1 | 0.2
4764 | 30/07/2025 11:59:20.640 | 96.624 | 82 | 100 | 70 | 53 | 28.838 | 9.132 | 7.122 | 133.161 | 31.019 | 28.704 | 29.134 | 604.335 | 26.732 | 27.686 | 1260.927 | 27.36 | 27.735 | 40.09 | 23.001 | 2.9 | 3 | 0 | 1 | 0.2
4765 | 30/07/2025 11:59:22.274 | 96.12 | 84 | 100 | 70 | 51 | 32.268 | 9.274 | 7.122 | 133.377 | 31.031 | 28.681 | 29.113 | 603.194 | 26.752 | 27.687 | 1257.604 | 27.325 | 27.753 | 40.388 | 23.001 | 4.1 | 2.9 | 1.2 | 0.2 | 0.3
4766 | 30/07/2025 11:59:23.908 | 96 | 82 | 100 | 71 | 52 | 32.73 | 9.229 | 7.132 | 133.185 | 31.013 | 28.675 | 29.139 | 603.294 | 26.686 | 27.679 | 1256.141 | 27.328 | 27.762 | 40.281 | 23.001 | 4.1 | 2.3 | 1.2 | 0 | 0.3
4767 | 30/07/2025 11:59:25.542 | 96.024 | 83 | 100 | 71 | 52 | 29.056 | 9.002 | 7.123 | 132.987 | 31.114 | 28.686 | 29.133 | 603.069 | 26.749 | 27.71 | 1254.249 | 27.36 | 27.75 | 40.187 | 25.001 | 1.9 | 3.2 | 1.6 | 1.5 | 0.2
4768 | 30/07/2025 11:59:27.178 | 95.784 | 83 | 100 | 70 | 52 | 30.429 | 9.205 | 7.098 | 132.961 | 31.145 | 28.696 | 29.148 | 603.116 | 26.763 | 27.706 | 1246.819 | 27.346 | 27.734 | 39.919 | 25.001 | 1.9 | 3.2 | 1.6 | 1.5 | 0.2
4769 | 30/07/2025 11:59:28.813 | 95.856 | 82 | 100 | 70 | 52 | 32.716 | 8.985 | 7.071 | 133.18 | 30.999 | 28.699 | 29.125 | 603.167 | 26.594 | 27.701 | 1247.29 | 27.496 | 27.753 | 40.142 | 25.001 | 1.9 | 3.4 | 1.6 | 0.7 | 0.2
4770 | 30/07/2025 11:59:30.447 | 95.736 | 82 | 100 | 70 | 52 | 29.235 | 9.13 | 7.068 | 133.255 | 31.052 | 28.69 | 29.122 | 603.32 | 26.592 | 27.695 | 1249.489 | 27.321 | 27.759 | 40.143 | 26.001 | 2.7 | 2.9 | 1.2 | 0.5 | 0.2
4771 | 30/07/2025 11:59:32.082 | 95.736 | 81 | 100 | 70 | 52 | 32.54 | 9.135 | 7.068 | 133.105 | 31.136 | 28.675 | 29.141 | 603.095 | 26.753 | 27.719 | 1255.283 | 27.349 | 27.76 | 40.186 | 26.001 | 2.7 | 2.4 | 1.2 | 0.5 | 0.2
4772 | 30/07/2025 11:59:33.717 | 95.496 | 83 | 100 | 71 | 52 | 32.394 | 9.005 | 7.061 | 132.906 | 31.155 | 28.701 | 29.136 | 602.985 | 26.745 | 27.706 | 1262 | 27.342 | 27.737 | 40.318 | 26.001 | 4.4 | 4.7 | 1.5 | 0.6 | 0.2
4773 | 30/07/2025 11:59:35.348 | 95.688 | 84 | 100 | 70 | 52 | 28.698 | 9.131 | 7.062 | 133.247 | 31.163 | 28.689 | 29.153 | 602.098 | 26.743 | 27.694 | 1267.422 | 27.343 | 27.732 | 40.24 | 26.001 | 4.4 | 4.6 | 1.5 | 1.1 | 0.2
4774 | 30/07/2025 11:59:36.985 | 95.88 | 82 | 98 | 70 | 53 | 30.835 | 9.132 | 7.089 | 132.962 | 31.173 | 28.686 | 29.124 | 603.031 | 26.74 | 27.719 | 1257.724 | 27.327 | 27.743 | 40.157 | 26.001 | 4.4 | 4.6 | 1.5 | 1.1 | 0.2
4775 | 30/07/2025 11:59:38.620 | 96.216 | 84 | 100 | 70 | 52 | 32.743 | 9.134 | 7.12 | 133.332 | 31.196 | 28.678 | 29.15 | 603.191 | 26.747 | 27.694 | 1249.971 | 27.326 | 27.744 | 40.283 | 30.001 | 2.4 | 4.3 | 0.7 | 0.5 | 0.2
4776 | 30/07/2025 11:59:40.254 | 96.648 | 84 | 100 | 70 | 52 | 29.653 | 9.219 | 7.121 | 132.995 | 31.039 | 28.678 | 29.136 | 603.084 | 26.737 | 27.713 | 1249.179 | 27.448 | 27.756 | 40.163 | 30.001 | 2.4 | 3.9 | 0.7 | 0.1 | 0.2
4777 | 30/07/2025 11:59:41.890 | 96.504 | 84 | 100 | 71 | 52 | 32.586 | 9.243 | 7.134 | 133.15 | 31.171 | 28.694 | 29.158 | 603.195 | 26.736 | 27.694 | 1256.531 | 27.362 | 27.73 | 40.075 | 27.001 | 2.6 | 4.5 | 0.6 | 0 | 0.2
4778 | 30/07/2025 11:59:43.523 | 97.056 | 85 | 100 | 71 | 52 | 31.929 | 9.107 | 7.135 | 133.169 | 31.181 | 28.703 | 29.142 | 603.163 | 26.732 | 27.701 | 1264.584 | 27.353 | 27.747 | 40.096 | 27.001 | 2.6 | 3.1 | 0.6 | 1 | 0.2
4779 | 30/07/2025 11:59:45.157 | 97.368 | 84 | 100 | 72 | 52 | 28.566 | 9.13 | 7.136 | 133.039 | 31.19 | 28.681 | 29.115 | 603.066 | 26.745 | 27.693 | 1262.258 | 27.307 | 27.747 | 40.286 | 27.001 | 2.6 | 3.1 | 0.6 | 1 | 0.2
4780 | 30/07/2025 11:59:46.791 | 96.96 | 85 | 100 | 70 | 52 | 31.44 | 9.189 | 7.133 | 133.256 | 31.179 | 28.673 | 29.165 | 603.232 | 26.721 | 27.682 | 1267.125 | 27.336 | 27.757 | 40.269 | 21.001 | 2.2 | 4 | 0.9 | 0.9 | 0.2
4781 | 30/07/2025 11:59:48.424 | 96.336 | 85 | 100 | 71 | 52 | 28.972 | 9.123 | 7.135 | 133.149 | 31.187 | 28.687 | 29.145 | 603.175 | 26.74 | 27.692 | 1271.639 | 27.353 | 27.749 | 40.223 | 21.001 | 2.2 | 4.7 | 0.9 | 1 | 0.2
4782 | 30/07/2025 11:59:50.058 | 96.888 | 84 | 100 | 70 | 52 | 30.28 | 9.205 | 7.07 | 133.086 | 31.171 | 28.7 | 29.147 | 603.147 | 26.725 | 27.676 | 1257.465 | 27.355 | 27.73 | 40.235 | 25.001 | 1.3 | 3.5 | 1.5 | 0.3 | 0.3
4783 | 30/07/2025 11:59:51.696 | 97.392 | 84 | 100 | 71 | 52 | 32.663 | 9.129 | 7.064 | 133.24 | 31.175 | 28.694 | 29.111 | 603.111 | 26.735 | 27.685 | 1259.428 | 27.482 | 27.753 | 40.268 | 25.001 | 1.3 | 4 | 1.5 | 0.8 | 0.3
4784 | 30/07/2025 11:59:53.330 | 97.608 | 85 | 100 | 70 | 52 | 31.509 | 9.284 | 7.058 | 133.245 | 31.192 | 28.682 | 29.119 | 603.24 | 26.736 | 27.665 | 1248.925 | 27.314 | 27.757 | 40.328 | 25.001 | 1.3 | 4 | 1.5 | 0.8 | 0.3
4785 | 30/07/2025 11:59:54.964 | 97.776 | 84 | 100 | 70 | 52 | 28.544 | 9.189 | 7.057 | 133.015 | 31.163 | 28.688 | 29.149 | 603.108 | 26.731 | 27.682 | 1246.571 | 27.375 | 27.756 | 40.347 | 22.001 | 1.1 | 3.3 | 1.2 | 0.7 | 0.2
4786 | 30/07/2025 11:59:56.599 | 97.536 | 84 | 100 | 71 | 52 | 32.483 | 9.29 | 7.06 | 133.072 | 31.166 | 28.698 | 29.153 | 602.355 | 26.741 | 27.674 | 1240.247 | 27.452 | 27.738 | 40.502 | 22.001 | 1.1 | 3.5 | 1.2 | 0.5 | 0.2
4787 | 30/07/2025 11:59:58.233 | 97.632 | 84 | 100 | 71 | 52 | 28.705 | 8.989 | 7.068 | 133.231 | 31.148 | 28.699 | 29.138 | 601.883 | 26.753 | 27.694 | 1246.37 | 27.359 | 27.742 | 40.254 | 25.001 | 2.1 | 3.7 | 1.2 | 1.3 | 0.2
4788 | 30/07/2025 11:59:59.866 | 97.032 | 85 | 100 | 70 | 52 | 31.051 | 9.097 | 7.071 | 133.353 | 31.167 | 28.685 | 29.121 | 602.996 | 26.76 | 27.697 | 1258.886 | 27.322 | 27.743 | 40.377 | 25.001 | 2.1 | 3.7 | 1.2 | 0.8 | 0.2
4789 | 30/07/2025 12:00:01.504 | 96.672 | 85 | 99 | 70 | 53 | 32.77 | 9.138 | 7.065 | 133.217 | 31.152 | 28.685 | 29.127 | 603.267 | 26.747 | 27.692 | 1257.889 | 27.332 | 27.762 | 40.35 | 31.001 | 1.2 | 3.1 | 0.9 | 0.1 | 0.2
4790 | 30/07/2025 12:00:03.141 | 96.768 | 84 | 100 | 70 | 53 | 30.806 | 8.914 | 7.088 | 133.102 | 31.158 | 28.681 | 29.15 | 603.11 | 26.74 | 27.727 | 1247.343 | 27.363 | 27.758 | 40.337 | 31.001 | 1.2 | 3.1 | 0.9 | 0.1 | 0.2
4791 | 30/07/2025 12:00:04.777 | 97.224 | 84 | 100 | 70 | 52 | 28.781 | 9.133 | 7.085 | 133.028 | 31.157 | 28.699 | 29.154 | 603.121 | 26.755 | 27.711 | 1246.662 | 27.342 | 27.738 | 40.046 | 31.001 | 1.2 | 3 | 0.9 | 0 | 0.2
4792 | 30/07/2025 12:00:06.411 | 96.144 | 84 | 100 | 71 | 52 | 31.942 | 8.988 | 7.09 | 133.221 | 31.16 | 28.695 | 29.147 | 602.912 | 26.76 | 27.708 | 1249.705 | 27.347 | 27.745 | 40.039 | 26.001 | 4.3 | 2 | 1.2 | 0 | 0.3
4793 | 30/07/2025 12:00:08.048 | 96.84 | 84 | 100 | 72 | 52 | 28.549 | 9.187 | 7.081 | 133.189 | 31.164 | 28.689 | 29.12 | 603.118 | 26.744 | 27.697 | 1258.289 | 27.32 | 27.76 | 40.167 | 26.001 | 4.3 | 3.6 | 1.2 | 1 | 0.3
4794 | 30/07/2025 12:00:09.683 | 97.176 | 86 | 100 | 70 | 52 | 31.43 | 9.21 | 7.068 | 133.041 | 31.166 | 28.664 | 29.133 | 603.25 | 26.739 | 27.701 | 1248.994 | 27.468 | 27.751 | 40.298 | 30.001 | 2.8 | 4.3 | 1.3 | 0.5 | 0.2
4795 | 30/07/2025 12:00:11.316 | 97.44 | 86 | 100 | 70 | 53 | 32.821 | 9.12 | 7.086 | 132.998 | 31.19 | 28.697 | 29.143 | 603.132 | 26.752 | 27.707 | 1246.241 | 27.342 | 27.743 | 40.162 | 30.001 | 2.8 | 4.3 | 1.3 | 0.5 | 0.2
4796 | 30/07/2025 12:00:12.951 | 97.608 | 85 | 100 | 70 | 52 | 30.22 | 9.038 | 7.086 | 133.176 | 31.189 | 28.705 | 29.146 | 602.063 | 26.735 | 27.686 | 1247.44 | 27.35 | 27.74 | 40.185 | 30.001 | 2.8 | 2.7 | 1.3 | 0.1 | 0.2
4797 | 30/07/2025 12:00:14.587 | 98.352 | 84 | 100 | 71 | 52 | 32.686 | 8.908 | 7.087 | 133.345 | 31.205 | 28.694 | 29.132 | 601.871 | 26.748 | 27.688 | 1249.337 | 27.339 | 27.742 | 40.068 | 27.001 | 3.3 | 4.6 | 0.6 | 0.5 | 0.2
4798 | 30/07/2025 12:00:16.222 | 98.472 | 86 | 100 | 70 | 52 | 31.418 | 9.131 | 7.082 | 133.303 | 31.181 | 28.687 | 29.121 | 601.92 | 26.746 | 27.694 | 1259.489 | 27.332 | 27.772 | 40.455 | 27.001 | 3.3 | 3.5 | 0.6 | 0.6 | 0.2
4799 | 30/07/2025 12:00:17.857 | 99.048 | 88 | 100 | 70 | 52 | 28.608 | 9.051 | 7.088 | 133.052 | 31.2 | 28.673 | 29.154 | 603.125 | 26.738 | 27.708 | 1259.901 | 27.348 | 27.757 | 40.338 | 29.001 | 1.9 | 1.6 | 0 | 0.7 | 0.1
4800 | 30/07/2025 12:00:19.490 | 99.312 | 85 | 100 | 71 | 52 | 31.901 | 8.988 | 7.087 | 133.14 | 31.195 | 28.69 | 29.151 | 603.253 | 26.717 | 27.683 | 1247.141 | 27.501 | 27.737 | 40.35 | 29.001 | 1.9 | 4 | 0 | 0.1 | 0.1
4801 | 30/07/2025 12:00:21.124 | 99.672 | 87 | 100 | 70 | 52 | 32.819 | 8.983 | 7.085 | 133.19 | 31.188 | 28.708 | 29.145 | 603.213 | 26.729 | 27.704 | 1255.144 | 27.356 | 27.753 | 40.116 | 29.001 | 1.9 | 4 | 0 | 0.1 | 0.1
4802 | 30/07/2025 12:00:22.759 | 99.336 | 84 | 100 | 70 | 51 | 29.483 | 9.131 | 7.068 | 133.22 | 31.195 | 28.684 | 29.108 | 602.946 | 26.724 | 27.681 | 1245.545 | 27.446 | 27.756 | 39.806 | 27.001 | 2.3 | 3.5 | 0 | 1.3 | 0.1
4803 | 30/07/2025 12:00:24.394 | 99.72 | 87 | 100 | 70 | 52 | 32.761 | 9.137 | 7.07 | 133.157 | 31.162 | 28.676 | 29.109 | 603.132 | 26.722 | 27.682 | 1238.496 | 27.357 | 27.74 | 40.51 | 27.001 | 2.3 | 3.2 | 0 | 0.8 | 0.1
4804 | 30/07/2025 12:00:26.028 | 99.648 | 86 | 100 | 71 | 52 | 30.783 | 9.282 | 7.121 | 133.217 | 31.174 | 28.689 | 29.248 | 603.258 | 26.736 | 27.682 | 1243.364 | 27.354 | 27.749 | 40.2 | 22.001 | 3.9 | 3.5 | 1.2 | 0.5 | 0.1
4805 | 30/07/2025 12:00:27.664 | 99.528 | 85 | 100 | 70 | 52 | 28.727 | 8.991 | 7.121 | 133.098 | 31.159 | 28.706 | 29.136 | 602.185 | 26.715 | 27.658 | 1247.184 | 27.364 | 27.725 | 40.31 | 22.001 | 3.9 | 3.8 | 1.2 | 0 | 0.1
4806 | 30/07/2025 12:00:29.300 | 99.456 | 87 | 100 | 70 | 52 | 32.243 | 9.253 | 7.122 | 133.147 | 31.161 | 28.682 | 29.131 | 601.932 | 26.732 | 27.683 | 1256.468 | 27.341 | 27.742 | 40.048 | 22.001 | 3.9 | 3.8 | 1.2 | 0 | 0.1
4807 | 30/07/2025 12:00:30.934 | 99.48 | 89 | 100 | 70 | 53 | 32.696 | 9.133 | 7.121 | 133.351 | 31.17 | 28.684 | 29.116 | 601.944 | 26.732 | 27.683 | 1254.881 | 27.462 | 27.754 | 40.177 | 32.001 | 3.3 | 3.4 | 0.6 | 0 | 0.2
4808 | 30/07/2025 12:00:32.568 | 98.856 | 85 | 100 | 70 | 51 | 31.468 | 9.127 | 7.123 | 133.275 | 31.161 | 28.68 | 29.137 | 601.858 | 26.753 | 27.701 | 1250.525 | 27.474 | 27.741 | 40.263 | 32.001 | 3.3 | 3.1 | 0.6 | 0 | 0.2
4809 | 30/07/2025 12:00:34.202 | 98.448 | 85 | 100 | 71 | 52 | 32.795 | 8.985 | 7.186 | 133.084 | 31.179 | 28.704 | 29.154 | 602.092 | 26.742 | 27.696 | 1240.262 | 27.506 | 27.755 | 40.073 | 23.001 | 3.2 | 3.9 | 2.2 | 0.5 | 0.2
4810 | 30/07/2025 12:00:35.841 | 98.376 | 84 | 100 | 70 | 51 | 30.212 | 9.131 | 7.137 | 132.943 | 31.14 | 28.703 | 29.156 | 601.969 | 26.742 | 27.709 | 1242.182 | 27.498 | 27.733 | 40.316 | 23.001 | 3.2 | 3.8 | 2.2 | 0.2 | 0.2
4811 | 30/07/2025 12:00:37.476 | 98.544 | 86 | 100 | 71 | 52 | 29.324 | 9.131 | 7.135 | 133.325 | 31.156 | 28.694 | 29.113 | 601.983 | 26.752 | 27.7 | 1265.869 | 27.332 | 27.756 | 40.134 | 22.001 | 3.7 | 4.5 | 0.6 | 1.1 | 0.3
4812 | 30/07/2025 12:00:39.111 | 98.592 | 86 | 99 | 71 | 52 | 32.425 | 9.133 | 7.149 | 133.215 | 31.156 | 28.677 | 29.118 | 601.871 | 26.738 | 27.709 | 1249.114 | 27.33 | 27.763 | 40.287 | 22.001 | 3.7 | 4.5 | 0.6 | 1.1 | 0.3
4813 | 30/07/2025 12:00:40.746 | 98.376 | 86 | 100 | 71 | 53 | 28.583 | 9.126 | 7.152 | 133.227 | 31.166 | 28.676 | 29.143 | 601.91 | 26.755 | 27.692 | 1251.218 | 27.329 | 27.739 | 40.236 | 22.001 | 3.7 | 5.7 | 0.6 | 1 | 0.3
4814 | 30/07/2025 12:00:42.379 | 98.76 | 87 | 100 | 71 | 53 | 31.966 | 9.141 | 7.151 | 132.825 | 31.169 | 28.707 | 29.145 | 601.93 | 26.744 | 27.707 | 1247.912 | 27.375 | 27.741 | 40.196 | 25.001 | 2.4 | 4.1 | 0.9 | 0.1 | 0.2
4815 | 30/07/2025 12:00:44.013 | 98.928 | 87 | 100 | 71 | 51 | 32.8 | 9.129 | 7.153 | 133.259 | 31.18 | 28.693 | 29.16 | 601.907 | 26.75 | 27.707 | 1245.963 | 27.353 | 27.737 | 39.944 | 25.001 | 2.4 | 5.5 | 0.9 | 0.5 | 0.2
4816 | 30/07/2025 12:00:45.647 | 99.048 | 85 | 100 | 71 | 52 | 29.689 | 9.21 | 7.15 | 133.084 | 31.184 | 28.69 | 29.133 | 602.114 | 26.729 | 27.695 | 1246.804 | 27.329 | 27.771 | 40.25 | 25.001 | 2.7 | 6.5 | 1.5 | 0.9 | 0.3
4817 | 30/07/2025 12:00:47.281 | 99.624 | 87 | 100 | 70 | 52 | 29.725 | 8.982 | 7.15 | 133.018 | 31.182 | 28.667 | 29.267 | 601.702 | 26.731 | 27.714 | 1252.994 | 27.335 | 27.755 | 40.254 | 25.001 | 2.7 | 6.5 | 1.5 | 0.9 | 0.3
4818 | 30/07/2025 12:00:48.912 | 99.504 | 84 | 100 | 70 | 52 | 32.596 | 8.927 | 7.136 | 133.178 | 31.2 | 28.695 | 29.293 | 601.965 | 26.755 | 27.702 | 1257.183 | 27.343 | 27.745 | 40.189 | 25.001 | 2.7 | 2.2 | 1.5 | 0.5 | 0.3
4819 | 30/07/2025 12:00:50.547 | 99 | 84 | 100 | 70 | 52 | 28.847 | 8.98 | 7.136 | 132.912 | 31.187 | 28.703 | 29.294 | 601.898 | 26.737 | 27.7 | 1252.581 | 27.348 | 27.74 | 40.337 | 26.001 | 2.8 | 3.7 | 0.6 | 0.5 | 0.2
4820 | 30/07/2025 12:00:52.181 | 98.76 | 86 | 100 | 70 | 52 | 32.216 | 9.269 | 7.121 | 134.945 | 31.188 | 28.695 | 29.286 | 602.047 | 26.737 | 27.685 | 1250.258 | 27.339 | 27.741 | 40.12 | 26.001 | 2.8 | 3.1 | 0.6 | 0.5 | 0.2
4821 | 30/07/2025 12:00:53.816 | 98.04 | 86 | 100 | 69 | 51 | 32.706 | 9.139 | 7.119 | 134.431 | 31.175 | 28.686 | 29.263 | 601.914 | 26.722 | 27.691 | 1237.703 | 27.328 | 27.766 | 40.306 | 22.001 | 1.4 | 4.3 | 0.6 | 0.2 | 0.1
4822 | 30/07/2025 12:00:55.448 | 97.704 | 84 | 100 | 71 | 52 | 29.08 | 9.133 | 7.136 | 134.547 | 31.18 | 28.674 | 29.275 | 601.601 | 26.734 | 27.702 | 1251.671 | 27.347 | 27.75 | 40.374 | 22.001 | 1.4 | 5.3 | 0.6 | 0.8 | 0.1
4823 | 30/07/2025 12:00:57.084 | 97.92 | 85 | 100 | 70 | 52 | 30.204 | 9.021 | 7.134 | 134.388 | 31.183 | 28.697 | 29.303 | 602.2 | 26.731 | 27.678 | 1261.382 | 27.495 | 27.742 | 40.217 | 22.001 | 1.4 | 5.3 | 0.6 | 0.8 | 0.1
4824 | 30/07/2025 12:00:58.718 | 97.944 | 85 | 100 | 70 | 52 | 32.678 | 8.996 | 7.134 | 134.696 | 31.182 | 28.706 | 29.289 | 601.997 | 26.722 | 27.692 | 1254.855 | 27.499 | 27.744 | 39.862 | 26.001 | 1.4 | 3 | 0.1 | 0.2 | 0.2
4825 | 30/07/2025 12:01:00.354 | 97.992 | 84 | 100 | 70 | 52 | 29.121 | 8.938 | 7.135 | 134.77 | 31.172 | 28.691 | 29.281 | 602.003 | 26.729 | 27.666 | 1256.541 | 27.484 | 27.763 | 40.123 | 26.001 | 1.4 | 3.7 | 0.1 | 0.5 | 0.2
4826 | 30/07/2025 12:01:01.988 | 97.944 | 83 | 100 | 71 | 52 | 32.429 | 9.203 | 7.133 | 134.632 | 31.169 | 28.676 | 29.26 | 601.839 | 26.738 | 27.683 | 1248.927 | 27.462 | 27.755 | 40.427 | 25.001 | 2 | 4.4 | 0 | 0.1 | 0.1
4827 | 30/07/2025 12:01:03.623 | 98.208 | 84 | 100 | 71 | 52 | 32.419 | 9.129 | 7.086 | 134.669 | 31.173 | 28.687 | 29.291 | 601.807 | 26.746 | 27.665 | 1257.274 | 27.494 | 27.746 | 40.307 | 25.001 | 2 | 2.4 | 0 | 0 | 0.1
4828 | 30/07/2025 12:01:05.259 | 98.184 | 85 | 100 | 71 | 51 | 28.673 | 9.136 | 7.086 | 134.072 | 31.166 | 28.704 | 29.178 | 601.859 | 26.731 | 27.694 | 1257.224 | 27.509 | 27.731 | 40.312 | 25.001 | 2 | 2.4 | 0 | 0 | 0.1
4829 | 30/07/2025 12:01:06.894 | 98.568 | 87 | 100 | 71 | 53 | 30.922 | 9.127 | 7.087 | 133.301 | 31.156 | 28.694 | 29.284 | 601.952 | 26.758 | 27.715 | 1262.166 | 27.346 | 27.76 | 40.139 | 26.001 | 4.1 | 3.3 | 0.6 | 0.8 | 0.2
4830 | 30/07/2025 12:01:08.533 | 98.544 | 85 | 100 | 70 | 53 | 29.544 | 9.14 | 7.087 | 134.693 | 31.158 | 28.703 | 29.273 | 601.937 | 26.749 | 27.715 | 1264.914 | 27.48 | 27.759 | 40.237 | 26.001 | 4.1 | 2.9 | 0.6 | 0.2 | 0.2
4831 | 30/07/2025 12:01:10.169 | 98.376 | 83 | 100 | 71 | 52 | 29.784 | 9.131 | 7.087 | 133.124 | 31.154 | 28.671 | 29.28 | 601.77 | 26.748 | 27.706 | 1267.094 | 27.474 | 27.748 | 40.307 | 28.001 | 2.9 | 3.5 | 0.6 | 0.5 | 0.2
4832 | 30/07/2025 12:01:11.803 | 98.136 | 85 | 100 | 70 | 52 | 32.531 | 9.133 | 7.086 | 133.231 | 31.158 | 28.699 | 29.294 | 602.453 | 26.73 | 27.713 | 1269.629 | 27.491 | 27.756 | 40.387 | 28.001 | 2.9 | 2.9 | 0.6 | 0.5 | 0.2
4833 | 30/07/2025 12:01:13.437 | 98.448 | 85 | 100 | 70 | 52 | 31.987 | 9.29 | 7.097 | 133.067 | 31.143 | 28.7 | 29.264 | 602.008 | 26.739 | 27.734 | 1274.062 | 27.497 | 27.722 | 40.05 | 19 | 2.2 | 3.7 | 0.7 | 0.6 | 0.2
4834 | 30/07/2025 12:01:15.072 | 98.64 | 84 | 100 | 70 | 52 | 28.526 | 9.286 | 7.134 | 134.306 | 31.162 | 28.684 | 29.272 | 601.936 | 26.749 | 27.695 | 1277.137 | 27.483 | 27.754 | 40.084 | 19 | 2.2 | 3.7 | 0.7 | 0.6 | 0.2
4835 | 30/07/2025 12:01:16.706 | 98.496 | 85 | 100 | 71 | 52 | 31.474 | 9.217 | 7.134 | 134.69 | 31.161 | 28.683 | 29.273 | 602.014 | 26.741 | 27.703 | 1276.825 | 27.479 | 27.752 | 40.281 | 19 | 2.2 | 3 | 0.7 | 0.5 | 0.2
4836 | 30/07/2025 12:01:18.342 | 98.04 | 84 | 100 | 70 | 52 | 29.133 | 9.129 | 7.133 | 134.615 | 31.184 | 28.672 | 29.155 | 601.844 | 26.746 | 27.695 | 1276.38 | 27.487 | 27.749 | 40.13 | 25.001 | 3.8 | 3.5 | 0.9 | 0.6 | 0.2
4837 | 30/07/2025 12:01:19.975 | 97.68 | 84 | 100 | 70 | 52 | 30.37 | 9.232 | 7.151 | 134.373 | 31.175 | 28.706 | 29.283 | 603.195 | 26.75 | 27.712 | 1257.269 | 27.518 | 27.755 | 40.287 | 25.001 | 3.8 | 4.2 | 0.9 | 0.1 | 0.2
4838 | 30/07/2025 12:01:21.612 | 97.368 | 83 | 100 | 70 | 51 | 32.662 | 9.13 | 7.154 | 134.739 | 31.183 | 28.697 | 29.277 | 603.249 | 26.743 | 27.697 | 1257.319 | 27.492 | 27.715 | 40.064 | 23.001 | 1.1 | 4.9 | 0.7 | 0 | 0.2
4839 | 30/07/2025 12:01:23.243 | 97.656 | 84 | 100 | 70 | 52 | 31.505 | 9.132 | 7.186 | 134.668 | 31.18 | 28.698 | 29.275 | 603.259 | 26.739 | 27.7 | 1255.324 | 27.48 | 27.767 | 40.281 | 23.001 | 1.1 | 4.9 | 0.7 | 0 | 0.2
4840 | 30/07/2025 12:01:24.878 | 97.752 | 84 | 100 | 71 | 52 | 28.656 | 8.987 | 7.151 | 134.379 | 31.192 | 28.661 | 29.283 | 603.042 | 26.727 | 27.714 | 1259.094 | 27.475 | 27.763 | 38.562 | 23.001 | 1.1 | 3.6 | 0.7 | 0 | 0.2
4841 | 30/07/2025 12:01:26.514 | 97.512 | 84 | 100 | 70 | 52 | 32.469 | 8.985 | 7.149 | 134.591 | 31.182 | 28.68 | 29.282 | 603.106 | 26.722 | 27.698 | 1264.76 | 27.508 | 27.762 | 38.551 | 23.001 | 2.4 | 6.8 | 0.6 | 0.5 | 0.3
4842 | 30/07/2025 12:01:28.149 | 97.464 | 84 | 100 | 70 | 52 | 28.783 | 9.133 | 7.152 | 134.499 | 31.174 | 28.696 | 29.301 | 603.129 | 26.733 | 27.698 | 1273.868 | 27.481 | 27.738 | 39.856 | 23.001 | 2.4 | 3.5 | 0.6 | 0.1 | 0.3
4843 | 30/07/2025 12:01:29.785 | 97.896 | 83 | 100 | 70 | 52 | 30.756 | 9.27 | 7.151 | 133.431 | 31.186 | 28.687 | 29.287 | 603.309 | 26.732 | 27.686 | 1277.033 | 27.487 | 27.739 | 39.948 | 23.001 | 3 | 3.1 | 0.6 | 0 | 0.2
4844 | 30/07/2025 12:01:31.421 | 97.872 | 84 | 100 | 70 | 52 | 32.767 | 9.135 | 7.185 | 133.19 | 31.169 | 28.685 | 29.263 | 603.194 | 26.73 | 27.701 | 1277.355 | 27.476 | 27.763 | 40.393 | 23.001 | 3 | 2.4 | 0.6 | 0 | 0.2
4845 | 30/07/2025 12:01:33.056 | 98.112 | 86 | 100 | 70 | 52 | 30.915 | 9.131 | 7.187 | 133.15 | 31.18 | 28.673 | 29.273 | 603.044 | 26.737 | 27.689 | 1276.831 | 27.487 | 27.738 | 40.29 | 23.001 | 3 | 2.4 | 0.6 | 0 | 0.2
4846 | 30/07/2025 12:01:34.691 | 97.776 | 84 | 100 | 70 | 52 | 32.605 | 9.142 | 7.187 | 132.859 | 31.16 | 28.691 | 29.278 | 603.007 | 26.726 | 27.676 | 1279.557 | 27.49 | 27.751 | 40.266 | 32.001 | 2.4 | 4.1 | 0.7 | 0 | 0.3
4847 | 30/07/2025 12:01:36.326 | 97.752 | 84 | 100 | 70 | 52 | 32.05 | 8.985 | 7.152 | 133.144 | 31.187 | 28.7 | 29.147 | 603.111 | 26.755 | 27.676 | 1284.429 | 27.488 | 27.732 | 40.114 | 32.001 | 2.4 | 3.9 | 0.7 | 0.5 | 0.3
4848 | 30/07/2025 12:01:37.968 | 97.752 | 84 | 100 | 70 | 52 | 28.542 | 9.136 | 7.136 | 133.262 | 31.175 | 28.695 | 29.282 | 603.3 | 26.737 | 27.668 | 1277.057 | 27.496 | 27.767 | 40.033 | 31.001 | 1.7 | 2.4 | 0.6 | 0.5 | 0.2
4849 | 30/07/2025 12:01:39.603 | 97.728 | 85 | 100 | 71 | 52 | 31.441 | 9.129 | 7.134 | 133.207 | 31.162 | 28.678 | 29.266 | 603.244 | 26.747 | 27.706 | 1270.535 | 27.455 | 27.752 | 40.42 | 31.001 | 1.7 | 3.4 | 0.6 | 0.6 | 0.2
4850 | 30/07/2025 12:01:41.240 | 98.28 | 87 | 100 | 70 | 52 | 32.85 | 9.137 | 7.119 | 133.265 | 31.159 | 28.677 | 29.312 | 602.487 | 26.732 | 27.687 | 1262.596 | 27.342 | 27.745 | 40.386 | 31.001 | 1.7 | 3.4 | 0.6 | 0.6 | 0.2
4851 | 30/07/2025 12:01:42.874 | 97.512 | 85 | 100 | 71 | 52 | 30.1 | 9.138 | 7.121 | 133.043 | 31.17 | 28.705 | 29.29 | 603.251 | 26.755 | 27.708 | 1269.383 | 27.371 | 27.736 | 40.34 | 26.001 | 2.1 | 4.7 | 0.7 | 0.3 | 0.2
4852 | 30/07/2025 12:01:44.509 | 98.016 | 86 | 100 | 70 | 53 | 32.63 | 9.131 | 7.121 | 133.256 | 31.156 | 28.695 | 29.294 | 602.133 | 26.735 | 27.715 | 1266.934 | 27.489 | 27.731 | 39.971 | 26.001 | 2.1 | 4.8 | 0.7 | 0 | 0.2
4853 | 30/07/2025 12:01:46.145 | 98.208 | 84 | 100 | 70 | 52 | 31.389 | 9.131 | 7.102 | 133.149 | 31.144 | 28.702 | 29.271 | 601.942 | 26.739 | 27.709 | 1279.421 | 27.482 | 27.752 | 40.057 | 29.001 | 2.3 | 3.4 | 0.3 | 0.5 | 0.2
4854 | 30/07/2025 12:01:47.780 | 97.992 | 84 | 100 | 70 | 52 | 28.53 | 9.285 | 7.07 | 133.173 | 31.161 | 28.669 | 29.277 | 601.812 | 26.751 | 27.707 | 1276.593 | 27.465 | 27.752 | 38.477 | 29.001 | 2.3 | 2.9 | 0.3 | 0.2 | 0.2
4855 | 30/07/2025 12:01:49.416 | 98.088 | 84 | 100 | 70 | 53 | 31.879 | 9.048 | 7.059 | 133 | 31.172 | 28.686 | 29.287 | 601.911 | 26.75 | 27.697 | 1277.453 | 27.508 | 27.76 | 38.601 | 25.001 | 3 | 4.7 | 0.6 | 0.5 | 0.2
4856 | 30/07/2025 12:01:51.050 | 98.352 | 84 | 100 | 70 | 52 | 32.801 | 9.137 | 7.06 | 133.12 | 31.177 | 28.69 | 29.275 | 601.968 | 26.739 | 27.719 | 1276.339 | 27.496 | 27.722 | 38.383 | 25.001 | 3 | 4.7 | 0.6 | 0.5 | 0.2
4857 | 30/07/2025 12:01:52.688 | 98.208 | 84 | 100 | 70 | 52 | 30.884 | 9.134 | 7.069 | 133.165 | 31.16 | 28.687 | 29.288 | 602.856 | 26.745 | 27.704 | 1268.523 | 27.507 | 27.743 | 39.778 | 25.001 | 3 | 4.5 | 0.6 | 0 | 0.2
4858 | 30/07/2025 12:01:54.322 | 98.376 | 84 | 100 | 70 | 52 | 32.744 | 9 | 7.07 | 133.011 | 31.189 | 28.683 | 29.248 | 603.05 | 26.74 | 27.706 | 1258.6 | 27.465 | 27.736 | 40.338 | 26.001 | 2.7 | 3.3 | 1 | 1 | 0.1
4859 | 30/07/2025 12:01:55.957 | 97.944 | 83 | 100 | 71 | 52 | 30.899 | 8.988 | 7.067 | 133.259 | 31.189 | 28.664 | 29.31 | 603.187 | 26.74 | 27.69 | 1248.526 | 27.476 | 27.758 | 40.294 | 26.001 | 2.7 | 3.8 | 1 | 0.6 | 0.1
4860 | 30/07/2025 12:01:57.593 | 97.296 | 84 | 100 | 71 | 52 | 28.887 | 9.113 | 7.117 | 132.76 | 31.174 | 28.701 | 29.277 | 603.047 | 26.737 | 27.713 | 1247.223 | 27.516 | 27.744 | 40.297 | 28.001 | 2.8 | 4.9 | 0 | 0.9 | 0.1
4861 | 30/07/2025 12:01:59.226 | 97.824 | 84 | 100 | 70 | 52 | 32.303 | 9.201 | 7.123 | 133.318 | 31.185 | 28.687 | 29.276 | 603.147 | 26.748 | 27.709 | 1248.915 | 27.484 | 27.712 | 39.963 | 28.001 | 2.8 | 4.9 | 0 | 0.9 | 0.1
4862 | 30/07/2025 12:02:00.860 | 98.328 | 83 | 100 | 70 | 53 | 32.707 | 9.129 | 7.118 | 133.188 | 31.18 | 28.692 | 29.264 | 603.18 | 26.733 | 27.686 | 1253.02 | 27.486 | 27.767 | 40.216 | 28.001 | 2.8 | 3.2 | 0 | 0.5 | 0.1
4863 | 30/07/2025 12:02:02.496 | 97.776 | 84 | 100 | 70 | 52 | 31.451 | 9.275 | 7.121 | 133.281 | 31.196 | 28.676 | 29.258 | 603.25 | 26.738 | 27.682 | 1252.43 | 27.456 | 27.747 | 40.175 | 29.001 | 2.9 | 3.6 | 0.9 | 0.6 | 0.2
4864 | 30/07/2025 12:02:04.130 | 97.992 | 85 | 100 | 70 | 52 | 32.845 | 9.214 | 7.133 | 133.155 | 31.178 | 28.678 | 29.286 | 601.988 | 26.724 | 27.682 | 1243.915 | 27.499 | 27.752 | 40.371 | 29.001 | 2.9 | 2.5 | 0.9 | 0.5 | 0.2
4865 | 30/07/2025 12:02:05.764 | 97.872 | 84 | 100 | 70 | 52 | 30.301 | 9.133 | 7.136 | 132.797 | 31.171 | 28.696 | 29.284 | 602.969 | 26.723 | 27.686 | 1237.166 | 27.498 | 27.728 | 40.257 | 23.001 | 1.9 | 4.2 | 1.5 | 0.2 | 0.2
4866 | 30/07/2025 12:02:07.402 | 98.088 | 88 | 100 | 70 | 52 | 29.18 | 8.987 | 7.133 | 133.368 | 31.182 | 28.698 | 29.296 | 602.043 | 26.733 | 27.679 | 1246.915 | 27.49 | 27.745 | 39.911 | 23.001 | 1.9 | 4.6 | 1.5 | 0 | 0.2
4867 | 30/07/2025 12:02:09.039 | 97.896 | 84 | 100 | 70 | 52 | 32.466 | 9.287 | 7.122 | 133.244 | 31.159 | 28.694 | 29.264 | 602.102 | 26.721 | 27.677 | 1261.193 | 27.487 | 27.764 | 40.291 | 23.001 | 1.9 | 4.6 | 1.5 | 0 | 0.2
4868 | 30/07/2025 12:02:10.675 | 98.328 | 85 | 100 | 71 | 52 | 28.63 | 9.436 | 7.119 | 133.248 | 31.18 | 28.678 | 29.278 | 602.172 | 26.738 | 27.672 | 1271.213 | 27.467 | 27.761 | 40.205 | 23.001 | 2.7 | 3.7 | 0.6 | 0.5 | 0.2
4869 | 30/07/2025 12:02:12.308 | 97.92 | 84 | 100 | 70 | 52 | 31.954 | 9.289 | 7.135 | 132.898 | 31.173 | 28.688 | 29.287 | 603.143 | 26.737 | 27.695 | 1276.903 | 27.497 | 27.761 | 40.296 | 23.001 | 2.7 | 3.7 | 0.6 | 0 | 0.2
4870 | 30/07/2025 12:02:13.944 | 98.016 | 84 | 100 | 70 | 52 | 32.816 | 9.268 | 7.135 | 133.16 | 31.179 | 28.7 | 29.297 | 602.15 | 26.773 | 27.697 | 1285.813 | 27.488 | 27.738 | 40.076 | 26.001 | 5.3 | 4.4 | 0.9 | 0.5 | 0.2
4871 | 30/07/2025 12:02:15.578 | 97.488 | 83 | 100 | 70 | 52 | 29.616 | 9.132 | 7.134 | 133.169 | 31.158 | 28.698 | 29.276 | 602.017 | 26.75 | 27.697 | 1291.245 | 27.509 | 27.754 | 40.07 | 26.001 | 5.3 | 4.1 | 0.9 | 0.5 | 0.2
4872 | 30/07/2025 12:02:17.211 | 96.864 | 84 | 100 | 70 | 52 | 29.703 | 9.131 | 7.134 | 133.174 | 31.136 | 28.678 | 29.26 | 602.014 | 26.744 | 27.702 | 1296.823 | 27.455 | 27.749 | 40.439 | 26.001 | 5.3 | 4.1 | 0.9 | 0.5 | 0.2
4873 | 30/07/2025 12:02:18.848 | 96.432 | 83 | 100 | 71 | 52 | 30.826 | 9.133 | 7.133 | 133.092 | 31.153 | 28.679 | 29.276 | 602.005 | 26.747 | 27.712 | 1295.443 | 27.478 | 27.748 | 40.364 | 27.001 | 2.3 | 4.9 | 0.6 | 0.2 | 0.2
4874 | 30/07/2025 12:02:20.482 | 96.408 | 82 | 100 | 70 | 52 | 28.758 | 9.135 | 7.136 | 132.926 | 31.163 | 28.696 | 29.291 | 601.857 | 26.753 | 27.721 | 1293.287 | 27.502 | 27.747 | 40.407 | 27.001 | 2.3 | 4.6 | 0.6 | 0 | 0.2
4875 | 30/07/2025 12:02:22.117 | 96.384 | 83 | 100 | 70 | 52 | 32.187 | 8.994 | 7.134 | 133.137 | 31.161 | 28.689 | 29.297 | 603.226 | 26.731 | 27.693 | 1291.793 | 27.488 | 27.728 | 40.177 | 25.001 | 2.1 | 4.3 | 1.2 | 0.5 | 0.2
4876 | 30/07/2025 12:02:23.756 | 96.48 | 83 | 100 | 70 | 52 | 32.682 | 9.218 | 7.134 | 133.306 | 31.168 | 28.691 | 29.267 | 603.195 | 26.743 | 27.713 | 1292.612 | 27.478 | 27.745 | 40.126 | 25.001 | 2.1 | 3.6 | 1.2 | 1.1 | 0.2
4877 | 30/07/2025 12:02:25.391 | 97.08 | 83 | 100 | 70 | 51 | 29.067 | 9.154 | 7.134 | 133.321 | 31.202 | 28.67 | 29.278 | 603.179 | 26.752 | 27.708 | 1287.336 | 27.467 | 27.749 | 40.283 | 25.001 | 1.9 | 4.8 | 1.2 | 0.4 | 0.2
4878 | 30/07/2025 12:02:27.027 | 97.464 | 85 | 100 | 71 | 52 | 30.308 | 9.008 | 7.134 | 132.987 | 31.17 | 28.696 | 29.293 | 603.158 | 26.748 | 27.698 | 1269.876 | 27.515 | 27.757 | 40.215 | 25.001 | 1.9 | 4.8 | 1.2 | 0.4 | 0.2
4879 | 30/07/2025 12:02:28.663 | 97.608 | 85 | 100 | 70 | 52 | 32.66 | 8.846 | 7.136 | 133.023 | 31.177 | 28.693 | 29.287 | 603.053 | 26.741 | 27.705 | 1276.793 | 27.493 | 27.727 | 40.118 | 25.001 | 1.9 | 4.6 | 1.2 | 0 | 0.2
4880 | 30/07/2025 12:02:30.298 | 97.656 | 84 | 100 | 70 | 52 | 29.223 | 8.95 | 7.165 | 132.265 | 31.187 | 28.704 | 29.281 | 603.079 | 26.75 | 27.692 | 1274.196 | 27.509 | 27.743 | 40.08 | 26.001 | 2.2 | 3.3 | 0.9 | 0.8 | 0.1
4881 | 30/07/2025 12:02:31.932 | 97.824 | 84 | 100 | 70 | 52 | 32.461 | 8.989 | 7.187 | 131.525 | 31.189 | 28.685 | 29.264 | 603.114 | 26.741 | 27.709 | 1276.978 | 27.473 | 27.74 | 40.262 | 26.001 | 2.2 | 3.3 | 0.9 | 0.1 | 0.1
4882 | 30/07/2025 12:02:33.569 | 97.944 | 84 | 100 | 70 | 52 | 32.464 | 9.122 | 7.184 | 131.669 | 31.182 | 28.667 | 29.28 | 603.192 | 26.742 | 27.689 | 1276.543 | 27.471 | 27.751 | 40.074 | 20.001 | 1.9 | 3.8 | 0.3 | 0 | 0.3
4883 | 30/07/2025 12:02:35.204 | 98.688 | 86 | 100 | 70 | 52 | 28.799 | 9.05 | 7.187 | 131.385 | 31.178 | 28.7 | 29.289 | 603.189 | 26.734 | 27.71 | 1267.328 | 27.504 | 27.745 | 40.17 | 20.001 | 1.9 | 3.8 | 0.3 | 0 | 0.3
4884 | 30/07/2025 12:02:36.838 | 98.256 | 85 | 100 | 70 | 52 | 32.807 | 8.989 | 7.186 | 131.581 | 31.175 | 28.701 | 29.293 | 603.217 | 26.717 | 27.684 | 1261.853 | 27.5 | 27.736 | 40.176 | 20.001 | 1.9 | 5.3 | 0.3 | 0.6 | 0.3
4885 | 30/07/2025 12:02:38.474 | 98.376 | 85 | 100 | 71 | 51 | 29.761 | 8.986 | 7.187 | 131.722 | 31.175 | 28.692 | 29.277 | 602.913 | 26.715 | 27.692 | 1262.804 | 27.486 | 27.752 | 39.882 | 22.001 | 2.7 | 3.2 | 2.4 | 0.3 | 0.3
4886 | 30/07/2025 12:02:40.111 | 98.184 | 88 | 100 | 70 | 51 | 29.719 | 9.13 | 7.185 | 131.611 | 31.191 | 28.685 | 29.259 | 603.224 | 26.731 | 27.676 | 1257.727 | 27.459 | 27.759 | 40.343 | 22.001 | 2.7 | 5.8 | 2.4 | 0.5 | 0.3
4887 | 30/07/2025 12:02:41.748 | 97.92 | 84 | 100 | 70 | 52 | 32.597 | 8.986 | 7.185 | 131.641 | 31.175 | 28.663 | 29.289 | 603.263 | 26.732 | 27.667 | 1270.587 | 27.502 | 27.758 | 40.264 | 22.001 | 4.6 | 3.8 | 0.6 | 0.5 | 0.3
4888 | 30/07/2025 12:02:43.384 | 97.32 | 87 | 100 | 71 | 51 | 32.122 | 8.993 | 7.188 | 131.489 | 31.164 | 28.699 | 29.282 | 603.051 | 26.735 | 27.69 | 1274.514 | 27.49 | 27.734 | 40.371 | 22.001 | 4.6 | 3.1 | 0.6 | 0.6 | 0.3
4889 | 30/07/2025 12:02:45.018 | 97.608 | 84 | 100 | 69 | 52 | 28.699 | 9.238 | 7.185 | 131.851 | 31.173 | 28.697 | 29.297 | 603.167 | 26.743 | 27.676 | 1266.987 | 27.487 | 27.741 | 39.918 | 22.001 | 4.6 | 3.1 | 0.6 | 0.6 | 0.3
4890 | 30/07/2025 12:02:46.654 | 97.704 | 85 | 100 | 70 | 53 | 32.731 | 9.133 | 7.155 | 131.684 | 31.166 | 28.692 | 29.264 | 603.074 | 26.753 | 27.691 | 1269.417 | 27.485 | 27.759 | 40.232 | 25.001 | 3.7 | 6.3 | 0.7 | 0 | 0.3
4891 | 30/07/2025 12:02:48.287 | 97.8 | 82 | 100 | 71 | 52 | 29.199 | 8.991 | 7.15 | 131.713 | 31.16 | 28.684 | 29.259 | 603.365 | 26.754 | 27.694 | 1262.441 | 27.472 | 27.771 | 40.359 | 25.001 | 3.7 | 5.3 | 0.7 | 0.6 | 0.3
4892 | 30/07/2025 12:02:49.923 | 97.8 | 84 | 98 | 70 | 53 | 30.292 | 8.984 | 7.152 | 131.494 | 31.154 | 28.687 | 29.296 | 603.259 | 26.75 | 27.711 | 1257.466 | 27.488 | 27.752 | 40.401 | 27.001 | 4.3 | 5.6 | 0 | 0.8 | 0.3
4893 | 30/07/2025 12:02:51.559 | 98.088 | 85 | 100 | 71 | 52 | 32.707 | 8.978 | 7.151 | 131.647 | 31.156 | 28.689 | 29.283 | 604.321 | 26.749 | 27.689 | 1262.784 | 27.492 | 27.726 | 40.192 | 27.001 | 4.3 | 3.8 | 0 | 0.5 | 0.3
4894 | 30/07/2025 12:02:53.193 | 98.616 | 84 | 100 | 70 | 52 | 31.479 | 9.29 | 7.152 | 131.825 | 31.157 | 28.697 | 29.292 | 605.635 | 26.738 | 27.714 | 1262.708 | 27.511 | 27.749 | 39.986 | 27.001 | 4.3 | 3.8 | 0 | 0.5 | 0.3
4895 | 30/07/2025 12:02:54.826 | 98.448 | 85 | 100 | 70 | 52 | 28.53 | 9.132 | 7.135 | 131.779 | 31.169 | 28.68 | 29.26 | 604.507 | 26.756 | 27.713 | 1274.635 | 27.473 | 27.758 | 40.481 | 29.001 | 2.4 | 4.2 | 1.2 | 0.8 | 0.3
4896 | 30/07/2025 12:02:56.461 | 99.144 | 86 | 100 | 70 | 52 | 32.462 | 9.211 | 7.132 | 131.725 | 31.15 | 28.677 | 29.276 | 604.578 | 26.747 | 27.709 | 1276.289 | 27.481 | 27.755 | 40.481 | 29.001 | 2.4 | 6.4 | 1.2 | 0 | 0.3
4897 | 30/07/2025 12:02:58.178 | 98.784 | 86 | 100 | 71 | 52 | 28.772 | 9.229 | 7.154 | 131.686 | 31.172 | 28.682 | 29.288 | 605.606 | 26.752 | 27.701 | 1279.547 | 27.501 | 27.733 | 40.428 | 26.001 | 3.6 | 5.1 | 0.6 | 0.8 | 0.3
4898 | 30/07/2025 12:02:59.818 | 99.024 | 86 | 100 | 70 | 52 | 30.806 | 8.99 | 7.134 | 131.702 | 31.18 | 28.702 | 29.301 | 606.983 | 26.735 | 27.694 | 1277.379 | 27.494 | 27.745 | 40.189 | 26.001 | 3.6 | 3.8 | 0.6 | 0.2 | 0.3
4899 | 30/07/2025 12:03:01.452 | 99.456 | 84 | 100 | 71 | 52 | 32.755 | 9.02 | 7.136 | 131.833 | 31.196 | 28.694 | 29.269 | 606.792 | 26.747 | 27.714 | 1267.625 | 27.49 | 27.755 | 38.489 | 26.001 | 4.2 | 3.8 | 0 | 0.5 | 0.3
4900 | 30/07/2025 12:03:03.086 | 99.264 | 87 | 100 | 71 | 52 | 30.802 | 9.283 | 7.134 | 132.028 | 31.195 | 28.677 | 29.281 | 606.825 | 26.756 | 27.693 | 1277.065 | 27.467 | 27.755 | 38.707 | 26.001 | 4.2 | 3.8 | 0 | 0.5 | 0.3
4901 | 30/07/2025 12:03:04.723 | 99.552 | 86 | 100 | 70 | 53 | 32.587 | 9.288 | 7.135 | 131.603 | 31.184 | 28.663 | 29.295 | 606.908 | 26.734 | 27.709 | 1277.243 | 27.482 | 27.753 | 38.701 | 26.001 | 4.2 | 3 | 0 | 0.5 | 0.3
4902 | 30/07/2025 12:03:06.358 | 99.816 | 87 | 100 | 70 | 52 | 32.018 | 9.144 | 7.134 | 131.63 | 31.19 | 28.703 | 29.309 | 606.94 | 26.738 | 27.695 | 1277.254 | 27.5 | 27.749 | 38.503 | 27.001 | 3.6 | 6.3 | 0.6 | 0.2 | 0.3
4903 | 30/07/2025 12:03:07.995 | 99.816 | 89 | 100 | 70 | 52 | 28.568 | 9.139 | 7.134 | 131.708 | 31.185 | 28.705 | 29.296 | 607.937 | 26.741 | 27.711 | 1275.367 | 27.509 | 27.752 | 40.064 | 27.001 | 3.6 | 3.7 | 0.6 | 0 | 0.3
4904 | 30/07/2025 12:03:09.630 | 99.6 | 86 | 100 | 70 | 52 | 31.372 | 9.129 | 7.151 | 131.687 | 31.178 | 28.689 | 29.267 | 607.983 | 26.732 | 27.697 | 1276.918 | 27.471 | 27.743 | 40.18 | 25.001 | 4.1 | 6.3 | 0.7 | 0 | 0.4
4905 | 30/07/2025 12:03:11.266 | 99.912 | 86 | 100 | 70 | 52 | 32.819 | 9.116 | 7.148 | 131.714 | 31.182 | 28.674 | 29.264 | 608.144 | 26.713 | 27.677 | 1279.495 | 27.465 | 27.754 | 40.312 | 25.001 | 4.1 | 6.3 | 0.7 | 0 | 0.4
4906 | 30/07/2025 12:03:12.901 | 99.48 | 86 | 100 | 71 | 52 | 30.354 | 9.292 | 7.156 | 131.702 | 31.167 | 28.692 | 29.279 | 607.962 | 26.723 | 27.685 | 1274.438 | 27.508 | 27.749 | 40.253 | 25.001 | 4.1 | 3.6 | 0.7 | 0.8 | 0.4
4907 | 30/07/2025 12:03:14.535 | 100.008 | 86 | 100 | 70 | 52 | 32.668 | 9.225 | 7.186 | 132.699 | 31.179 | 28.702 | 29.286 | 608.166 | 26.724 | 27.674 | 1268.477 | 27.504 | 27.735 | 40.24 | 29.001 | 1.8 | 3.6 | 1.8 | 0.9 | 0.3
4908 | 30/07/2025 12:03:16.170 | 100.008 | 85 | 100 | 70 | 53 | 31.613 | 9.133 | 7.148 | 133.228 | 31.175 | 28.686 | 29.279 | 607.927 | 26.736 | 27.688 | 1257.23 | 27.49 | 27.747 | 39.94 | 29.001 | 1.8 | 3.7 | 1.8 | 0 | 0.3
4909 | 30/07/2025 12:03:17.807 | 99.84 | 84 | 100 | 71 | 53 | 28.674 | 9.211 | 7.133 | 133.314 | 31.18 | 28.687 | 29.275 | 608.008 | 26.736 | 27.673 | 1255.478 | 27.461 | 27.761 | 40.155 | 24.001 | 2.1 | 4.5 | 0.6 | 1.6 | 0.3
4910 | 30/07/2025 12:03:19.446 | 99.672 | 86 | 100 | 71 | 52 | 32.019 | 9.133 | 7.134 | 132.995 | 31.163 | 28.667 | 29.285 | 608.024 | 26.745 | 27.671 | 1247.374 | 27.495 | 27.754 | 40.378 | 24.001 | 2.1 | 5.4 | 0.6 | 0.7 | 0.3
4911 | 30/07/2025 12:03:21.081 | 99.336 | 88 | 100 | 70 | 52 | 32.837 | 9.136 | 7.135 | 132.839 | 31.17 | 28.697 | 29.283 | 607.948 | 26.763 | 27.708 | 1237.034 | 27.498 | 27.75 | 40.121 | 24.001 | 2.1 | 5.4 | 0.6 | 0.7 | 0.3
4912 | 30/07/2025 12:03:22.716 | 99.072 | 86 | 100 | 70 | 52 | 29.748 | 9.291 | 7.151 | 133.262 | 31.172 | 28.7 | 29.146 | 608.158 | 26.738 | 27.701 | 1222.49 | 27.492 | 27.751 | 40.25 | 23.001 | 2.9 | 5.5 | 0.8 | 0.5 | 0.3
4913 | 30/07/2025 12:03:24.352 | 99.168 | 86 | 100 | 70 | 51 | 32.822 | 9.287 | 7.166 | 133.287 | 31.178 | 28.693 | 29.136 | 607.864 | 26.763 | 27.708 | 1219.739 | 27.493 | 27.761 | 40.002 | 23.001 | 2.9 | 2.2 | 0.8 | 0.5 | 0.3
4914 | 30/07/2025 12:03:25.987 | 98.544 | 84 | 100 | 70 | 52 | 30.924 | 9.131 | 7.202 | 133.13 | 31.164 | 28.681 | 29.273 | 608.083 | 26.743 | 27.704 | 1235.623 | 27.474 | 27.761 | 40.775 | 26.001 | 3 | 4.1 | 0.1 | 0.2 | 0.2
4915 | 30/07/2025 12:03:27.623 | 98.136 | 84 | 100 | 71 | 52 | 28.751 | 9.29 | 7.121 | 133.243 | 31.161 | 28.673 | 29.301 | 608.971 | 26.748 | 27.714 | 1244.516 | 27.486 | 27.759 | 40.309 | 26.001 | 3 | 4.8 | 0.1 | 0 | 0.2
4916 | 30/07/2025 12:03:29.257 | 97.992 | 84 | 100 | 71 | 52 | 32.201 | 9.074 | 7.094 | 133.032 | 31.177 | 28.692 | 29.292 | 609.349 | 26.748 | 27.7 | 1249.44 | 27.495 | 27.739 | 40.078 | 26.001 | 3 | 4.8 | 0.1 | 0 | 0.2
4917 | 30/07/2025 12:03:30.893 | 97.608 | 84 | 100 | 70 | 52 | 32.764 | 9.133 | 7.07 | 133.335 | 31.159 | 28.697 | 29.269 | 609.091 | 26.736 | 27.7 | 1255.376 | 27.511 | 27.74 | 40.091 | 24.001 | 3.1 | 4 | 1.2 | 0.5 | 0.2
4918 | 30/07/2025 12:03:32.527 | 97.8 | 83 | 100 | 70 | 52 | 31.334 | 9.224 | 7.069 | 133.32 | 31.179 | 28.69 | 29.286 | 609.236 | 26.737 | 27.7 | 1249.928 | 27.488 | 27.769 | 40.181 | 24.001 | 3.1 | 4.6 | 1.2 | 1.1 | 0.2
4919 | 30/07/2025 12:03:34.164 | 97.752 | 84 | 100 | 71 | 51 | 32.846 | 9.216 | 7.084 | 133.125 | 31.183 | 28.69 | 29.133 | 609.326 | 26.74 | 27.708 | 1253.141 | 27.468 | 27.754 | 38.464 | 28.001 | 3.5 | 5.4 | 2.1 | 0.7 | 0.2
4920 | 30/07/2025 12:03:35.797 | 97.56 | 83 | 100 | 70 | 52 | 30.252 | 9.135 | 7.088 | 133.155 | 31.187 | 28.683 | 29.294 | 609.242 | 26.76 | 27.699 | 1246.916 | 27.491 | 27.737 | 38.342 | 28.001 | 3.5 | 3.3 | 2.1 | 0.3 | 0.2
4921 | 30/07/2025 12:03:37.433 | 98.184 | 84 | 100 | 71 | 51 | 29.144 | 9.183 | 7.086 | 133.224 | 31.188 | 28.703 | 29.29 | 609.293 | 26.738 | 27.696 | 1254.728 | 27.497 | 27.754 | 38.25 | 24.001 | 2.3 | 3.9 | 0.9 | 0 | 0.1
4922 | 30/07/2025 12:03:39.069 | 97.944 | 82 | 100 | 70 | 52 | 32.473 | 9.209 | 7.088 | 133.277 | 31.186 | 28.695 | 29.272 | 610.129 | 26.752 | 27.709 | 1247.587 | 27.481 | 27.746 | 38.332 | 24.001 | 2.3 | 3.9 | 0.9 | 0 | 0.1
4923 | 30/07/2025 12:03:40.705 | 97.704 | 84 | 100 | 70 | 52 | 28.615 | 9.139 | 7.084 | 133.099 | 31.171 | 28.694 | 29.146 | 610.553 | 26.747 | 27.702 | 1246.652 | 27.493 | 27.774 | 38.447 | 24.001 | 2.3 | 2.5 | 0.9 | 0.5 | 0.1
4924 | 30/07/2025 12:03:42.337 | 97.44 | 84 | 100 | 70 | 52 | 31.776 | 9.135 | 7.122 | 133.181 | 31.192 | 28.665 | 29.292 | 610.53 | 26.732 | 27.705 | 1257.166 | 27.486 | 27.757 | 39.734 | 24.001 | 2.9 | 2.8 | 0.9 | 0.2 | 0.2
4925 | 30/07/2025 12:03:43.973 | 97.584 | 84 | 100 | 69 | 52 | 32.816 | 8.987 | 7.086 | 133.1 | 31.186 | 28.697 | 29.307 | 610.643 | 26.735 | 27.689 | 1257.35 | 27.493 | 27.752 | 40.206 | 24.001 | 2.9 | 4.8 | 0.9 | 1 | 0.2
4926 | 30/07/2025 12:03:45.608 | 97.08 | 84 | 100 | 69 | 53 | 29.665 | 9.196 | 7.085 | 133.066 | 31.178 | 28.694 | 29.304 | 610.434 | 26.73 | 27.697 | 1257.517 | 27.483 | 27.749 | 40.241 | 24.001 | 3.7 | 3.7 | 0 | 0.5 | 0.2
4927 | 30/07/2025 12:03:47.243 | 97.296 | 84 | 100 | 71 | 52 | 29.686 | 9.263 | 7.088 | 133.348 | 31.191 | 28.688 | 29.264 | 610.497 | 26.736 | 27.678 | 1264.416 | 27.481 | 27.738 | 40.416 | 24.001 | 3.7 | 3.7 | 0 | 0.5 | 0.2
4928 | 30/07/2025 12:03:48.877 | 97.68 | 83 | 100 | 70 | 52 | 32.611 | 9.437 | 7.127 | 133.272 | 31.173 | 28.674 | 29.287 | 610.583 | 26.724 | 27.679 | 1269.175 | 27.483 | 27.755 | 40.477 | 24.001 | 3.7 | 2.4 | 0 | 0 | 0.2
4929 | 30/07/2025 12:03:50.512 | 96.768 | 84 | 99 | 71 | 53 | 28.869 | 9.33 | 7.132 | 133.065 | 31.187 | 28.672 | 29.293 | 611.537 | 26.732 | 27.682 | 1277.179 | 27.49 | 27.752 | 40.346 | 25.001 | 2.6 | 5.5 | 0.9 | 0.5 | 0.2
4930 | 30/07/2025 12:03:52.145 | 96.648 | 83 | 100 | 70 | 51 | 32.269 | 9.122 | 7.07 | 133.101 | 31.161 | 28.704 | 29.3 | 612.849 | 26.752 | 27.67 | 1284.658 | 27.515 | 27.743 | 40.439 | 25.001 | 2.6 | 3.5 | 0.9 | 0.7 | 0.2
4931 | 30/07/2025 12:03:53.779 | 96.816 | 83 | 100 | 70 | 52 | 32.722 | 9.132 | 7.071 | 133.437 | 31.17 | 28.69 | 29.281 | 612.793 | 26.746 | 27.697 | 1273.962 | 27.489 | 27.74 | 39.953 | 25.001 | 2.3 | 4 | 1.2 | 0.7 | 0.2
4932 | 30/07/2025 12:03:55.413 | 97.632 | 84 | 100 | 70 | 52 | 29.211 | 9.089 | 7.069 | 133.105 | 31.167 | 28.688 | 29.267 | 612.965 | 26.746 | 27.678 | 1267.349 | 27.474 | 27.75 | 40.252 | 25.001 | 2.3 | 3.1 | 1.2 | 0.9 | 0.2
4933 | 30/07/2025 12:03:57.047 | 97.704 | 85 | 100 | 70 | 52 | 30.365 | 9.087 | 7.115 | 131.637 | 31.151 | 28.683 | 29.133 | 612.932 | 26.753 | 27.707 | 1276.872 | 27.486 | 27.75 | 40.28 | 25.001 | 2.3 | 3.1 | 1.2 | 0.9 | 0.2
4934 | 30/07/2025 12:03:58.679 | 97.944 | 86 | 100 | 70 | 53 | 30.33 | 8.988 | 7.12 | 131.581 | 31.159 | 28.684 | 29.293 | 612.978 | 26.743 | 27.694 | 1277.159 | 27.502 | 27.75 | 40.214 | 23.001 | 1.7 | 2.2 | 0.9 | 0.6 | 0.2
4935 | 30/07/2025 12:04:00.313 | 98.712 | 85 | 100 | 70 | 52 | 29.219 | 9.176 | 7.122 | 131.546 | 31.15 | 28.689 | 29.286 | 613.013 | 26.748 | 27.718 | 1284.594 | 27.493 | 27.739 | 40.379 | 23.001 | 1.7 | 3 | 0.9 | 0.3 | 0.2
4936 | 30/07/2025 12:04:01.948 | 98.64 | 84 | 100 | 70 | 52 | 32.426 | 9.13 | 7.11 | 131.845 | 31.164 | 28.69 | 29.277 | 612.999 | 26.762 | 27.705 | 1286.979 | 27.49 | 27.746 | 39.971 | 27.001 | 3.3 | 5.5 | 1.2 | 0 | 0.2
4937 | 30/07/2025 12:04:03.581 | 99.384 | 85 | 100 | 71 | 51 | 32.517 | 9.174 | 7.086 | 131.741 | 31.143 | 28.674 | 29.256 | 612.796 | 26.742 | 27.689 | 1278.453 | 27.478 | 27.758 | 40.294 | 27.001 | 3.3 | 4.2 | 1.2 | 0 | 0.2
4938 | 30/07/2025 12:04:05.213 | 98.928 | 88 | 100 | 70 | 53 | 28.816 | 9.129 | 7.087 | 131.605 | 31.174 | 28.685 | 29.292 | 612.918 | 26.747 | 27.711 | 1267.03 | 27.492 | 27.759 | 40.184 | 27.001 | 3.3 | 4.2 | 1.2 | 0 | 0.2
4939 | 30/07/2025 12:04:06.845 | 99.072 | 86 | 100 | 70 | 52 | 32.821 | 9.136 | 7.087 | 131.686 | 31.162 | 28.698 | 29.285 | 613.021 | 26.738 | 27.71 | 1266.85 | 27.518 | 27.749 | 40.204 | 23.001 | 2.7 | 2.5 | 0.6 | 0 | 0.2
4940 | 30/07/2025 12:04:08.477 | 99.192 | 86 | 100 | 70 | 52 | 29.729 | 8.988 | 7.143 | 131.601 | 31.193 | 28.697 | 29.283 | 612.847 | 26.751 | 27.71 | 1275.447 | 27.488 | 27.73 | 40.143 | 23.001 | 2.7 | 2 | 0.6 | 0 | 0.2
4941 | 30/07/2025 12:04:10.111 | 99.216 | 86 | 100 | 70 | 51 | 29.601 | 9.129 | 7.151 | 131.561 | 31.175 | 28.686 | 29.278 | 612.961 | 26.735 | 27.694 | 1274.812 | 27.486 | 27.769 | 39.99 | 26.001 | 2.9 | 3.3 | 0.9 | 0 | 0.2
4942 | 30/07/2025 12:04:11.743 | 99.336 | 84 | 100 | 71 | 52 | 32.582 | 9.212 | 7.15 | 131.73 | 31.192 | 28.673 | 29.276 | 612.86 | 26.737 | 27.718 | 1267.003 | 27.468 | 27.761 | 40.348 | 26.001 | 2.9 | 4.8 | 0.9 | 0.5 | 0.2
4943 | 30/07/2025 12:04:13.375 | 99.432 | 86 | 100 | 70 | 52 | 31.976 | 9.137 | 7.173 | 131.677 | 31.195 | 28.688 | 29.31 | 612.983 | 26.758 | 27.703 | 1262.534 | 27.485 | 27.745 | 40.232 | 26.001 | 2.3 | 4 | 0.2 | 0.6 | 0.1
4944 | 30/07/2025 12:04:15.007 | 99.264 | 86 | 100 | 70 | 53 | 28.602 | 9.257 | 7.186 | 132.922 | 31.187 | 28.708 | 29.302 | 612.991 | 26.74 | 27.692 | 1262.452 | 27.501 | 27.757 | 40.35 | 26.001 | 2.3 | 4 | 0.2 | 0.6 | 0.1
4945 | 30/07/2025 12:04:16.641 | 99.504 | 88 | 100 | 71 | 51 | 32.73 | 9.214 | 7.186 | 133.425 | 31.182 | 28.69 | 29.282 | 613.007 | 26.732 | 27.69 | 1266.861 | 27.494 | 27.726 | 39.91 | 26.001 | 2.3 | 2.5 | 0.2 | 0.5 | 0.1
4946 | 30/07/2025 12:04:18.278 | 99.528 | 88 | 100 | 71 | 52 | 29.114 | 9.157 | 7.173 | 133.252 | 31.171 | 28.697 | 29.261 | 614.114 | 26.724 | 27.704 | 1267.547 | 27.493 | 27.765 | 40.257 | 28.001 | 3.5 | 2.4 | 0 | 0.8 | 0.1
4947 | 30/07/2025 12:04:19.913 | 99.024 | 86 | 100 | 70 | 51 | 30.103 | 9.132 | 7.122 | 133.077 | 31.174 | 28.667 | 29.266 | 613.915 | 26.736 | 27.693 | 1262.184 | 27.467 | 27.754 | 40.37 | 28.001 | 3.5 | 3.1 | 0 | 0.4 | 0.1
4948 | 30/07/2025 12:04:21.549 | 99 | 86 | 100 | 71 | 52 | 32.677 | 8.994 | 7.129 | 133.13 | 31.177 | 28.694 | 29.304 | 614.3 | 26.713 | 27.674 | 1267.531 | 27.499 | 27.75 | 40.182 | 25.001 | 2.9 | 3.9 | 0.6 | 0 | 0.2
4949 | 30/07/2025 12:04:23.194 | 99.144 | 85 | 100 | 70 | 52 | 31.492 | 9.134 | 7.135 | 133.055 | 31.165 | 28.71 | 29.276 | 615.335 | 26.728 | 27.673 | 1269.699 | 27.485 | 27.737 | 40.209 | 25.001 | 2.9 | 3.9 | 0.6 | 0 | 0.2
4950 | 30/07/2025 12:04:24.829 | 99.048 | 86 | 100 | 70 | 52 | 28.623 | 9.129 | 7.122 | 133.427 | 31.189 | 28.694 | 29.287 | 615.441 | 26.746 | 27.69 | 1269.557 | 27.487 | 27.763 | 39.942 | 25.001 | 2.9 | 3.1 | 0.6 | 0 | 0.2
4951 | 30/07/2025 12:04:26.465 | 98.856 | 87 | 100 | 70 | 52 | 32.483 | 9.131 | 7.12 | 133.135 | 31.173 | 28.686 | 29.248 | 615.34 | 26.733 | 27.685 | 1276.164 | 27.477 | 27.752 | 40.333 | 32.001 | 4 | 5.1 | 1.6 | 0 | 0.3
4952 | 30/07/2025 12:04:28.100 | 98.76 | 84 | 100 | 70 | 52 | 28.811 | 9.165 | 7.117 | 133.245 | 31.171 | 28.671 | 29.283 | 615.464 | 26.746 | 27.675 | 1282.016 | 27.482 | 27.738 | 38.445 | 32.001 | 4 | 2.5 | 1.6 | 0.5 | 0.3
4953 | 30/07/2025 12:04:29.735 | 98.376 | 86 | 100 | 70 | 52 | 30.842 | 9.137 | 7.122 | 133.01 | 31.165 | 28.701 | 29.291 | 615.575 | 26.742 | 27.704 | 1286.161 | 27.509 | 27.758 | 38.494 | 31.001 | 3 | 5.3 | 1.8 | 0.5 | 0.3
4954 | 30/07/2025 12:04:31.366 | 97.944 | 85 | 100 | 70 | 52 | 32.694 | 9.211 | 7.123 | 134.722 | 31.153 | 28.69 | 29.276 | 615.466 | 26.759 | 27.717 | 1275.264 | 27.492 | 27.727 | 40.078 | 31.001 | 3 | 5.4 | 1.8 | 1.2 | 0.3
4955 | 30/07/2025 12:04:33.001 | 97.272 | 84 | 100 | 70 | 53 | 31.005 | 9.134 | 7.12 | 134.647 | 31.159 | 28.694 | 29.268 | 615.432 | 26.743 | 27.701 | 1277.267 | 27.476 | 27.771 | 40.349 | 31.001 | 3 | 5.4 | 1.8 | 1.2 | 0.3
4956 | 30/07/2025 12:04:34.637 | 96.864 | 82 | 100 | 71 | 51 | 32.588 | 9.131 | 7.122 | 134.736 | 31.159 | 28.681 | 29.263 | 615.35 | 26.749 | 27.701 | 1277.224 | 27.463 | 27.75 | 40.468 | 25.001 | 4.5 | 3.5 | 0.2 | 0.7 | 0.3
4957 | 30/07/2025 12:04:36.272 | 96.504 | 84 | 100 | 70 | 52 | 32.11 | 8.987 | 7.121 | 134.66 | 31.167 | 28.686 | 29.295 | 615.704 | 26.739 | 27.697 | 1277.021 | 27.508 | 27.765 | 40.142 | 25.001 | 4.5 | 3.2 | 0.2 | 0.3 | 0.3
4958 | 30/07/2025 12:04:37.906 | 96.264 | 83 | 100 | 71 | 53 | 28.654 | 8.847 | 7.125 | 134.481 | 31.161 | 28.684 | 29.277 | 615.431 | 26.74 | 27.726 | 1274.316 | 27.491 | 27.731 | 40.22 | 30.001 | 2.3 | 2.4 | 0.7 | 1.1 | 0.2
4959 | 30/07/2025 12:04:39.542 | 96.024 | 82 | 100 | 70 | 52 | 31.507 | 9.125 | 7.135 | 134.86 | 31.172 | 28.7 | 29.28 | 615.457 | 26.74 | 27.704 | 1287.301 | 27.491 | 27.741 | 40.102 | 30.001 | 2.3 | 2 | 0.7 | 0.5 | 0.2
4960 | 30/07/2025 12:04:41.173 | 95.808 | 82 | 100 | 71 | 52 | 32.858 | 8.988 | 7.132 | 134.61 | 31.184 | 28.694 | 29.274 | 614.349 | 26.745 | 27.705 | 1296.971 | 27.484 | 27.765 | 40.365 | 30.001 | 2.3 | 2 | 0.7 | 0.5 | 0.2
4961 | 30/07/2025 12:04:42.808 | 95.664 | 82 | 100 | 70 | 53 | 30.371 | 8.99 | 7.134 | 134.461 | 31.186 | 28.665 | 29.298 | 614.214 | 26.747 | 27.699 | 1282.999 | 27.49 | 27.759 | 40.317 | 27.001 | 2 | 3.6 | 1.7 | 0.2 | 0.2
4962 | 30/07/2025 12:04:44.442 | 95.76 | 84 | 100 | 71 | 52 | 32.697 | 8.988 | 7.152 | 134.743 | 31.186 | 28.693 | 29.289 | 614.292 | 26.741 | 27.702 | 1277.073 | 27.505 | 27.757 | 40.344 | 27.001 | 2 | 3.1 | 1.7 | 1.1 | 0.2
4963 | 30/07/2025 12:04:46.078 | 95.976 | 82 | 100 | 71 | 52 | 31.505 | 9.088 | 7.138 | 134.663 | 31.19 | 28.695 | 29.272 | 614.061 | 26.744 | 27.702 | 1269.349 | 27.493 | 27.723 | 40.141 | 25.001 | 2.8 | 3.7 | 0.9 | 0.6 | 0.2
4964 | 30/07/2025 12:04:47.712 | 96.048 | 82 | 100 | 70 | 52 | 28.624 | 9.132 | 7.133 | 134.659 | 31.172 | 28.687 | 29.275 | 612.992 | 26.715 | 27.697 | 1267.345 | 27.485 | 27.752 | 40.162 | 25.001 | 2.8 | 5.7 | 0.9 | 0.9 | 0.2
4965 | 30/07/2025 12:04:49.345 | 95.784 | 82 | 100 | 71 | 52 | 31.865 | 8.921 | 7.134 | 134.526 | 31.185 | 28.681 | 29.255 | 612.806 | 26.732 | 27.716 | 1267.431 | 27.462 | 27.747 | 40.497 | 24.001 | 3.1 | 3 | 0.8 | 0.8 | 0.2
4966 | 30/07/2025 12:04:51.000 | 95.712 | 82 | 100 | 70 | 52 | 32.827 | 9.127 | 7.153 | 134.862 | 31.179 | 28.688 | 29.3 | 612.937 | 26.735 | 27.683 | 1267.098 | 27.495 | 27.756 | 40.023 | 24.001 | 3.1 | 3 | 0.8 | 0.8 | 0.2
4967 | 30/07/2025 12:04:52.634 | 96.024 | 82 | 100 | 71 | 52 | 30.745 | 9.231 | 7.188 | 134.374 | 31.181 | 28.691 | 29.279 | 611.718 | 26.73 | 27.704 | 1266.911 | 27.487 | 27.745 | 40.404 | 24.001 | 3.1 | 4.8 | 0.8 | 0.2 | 0.2
4968 | 30/07/2025 12:04:54.269 | 95.856 | 84 | 100 | 70 | 52 | 32.747 | 9.131 | 7.186 | 134.824 | 31.185 | 28.697 | 29.292 | 611.731 | 26.727 | 27.678 | 1272.614 | 27.483 | 27.72 | 39.987 | 28.001 | 2.1 | 4 | 0.9 | 0.5 | 0.2
4969 | 30/07/2025 12:04:55.902 | 95.952 | 82 | 100 | 70 | 52 | 30.903 | 9.133 | 7.186 | 134.701 | 31.161 | 28.697 | 29.272 | 610.545 | 26.722 | 27.698 | 1267.391 | 27.491 | 27.766 | 40.279 | 28.001 | 2.1 | 3.8 | 0.9 | 0.2 | 0.2
4970 | 30/07/2025 12:04:57.536 | 96.312 | 84 | 100 | 70 | 52 | 28.837 | 9.212 | 7.135 | 134.516 | 31.171 | 28.662 | 29.262 | 610.325 | 26.741 | 27.692 | 1268.103 | 27.45 | 27.737 | 40.245 | 26.001 | 3.8 | 3.7 | 1.2 | 0 | 0.2
4971 | 30/07/2025 12:04:59.170 | 95.832 | 83 | 100 | 70 | 52 | 32.216 | 9.134 | 7.134 | 134.638 | 31.183 | 28.699 | 29.291 | 610.738 | 26.721 | 27.674 | 1264.979 | 27.497 | 27.754 | 40.218 | 26.001 | 3.8 | 3.7 | 1.2 | 0 | 0.2
4972 | 30/07/2025 12:05:00.804 | 96.288 | 81 | 100 | 71 | 51 | 28.61 | 9.133 | 7.135 | 134.495 | 31.183 | 28.7 | 29.291 | 610.656 | 26.751 | 27.689 | 1259.768 | 27.489 | 27.739 | 40.14 | 26.001 | 3.8 | 3.7 | 1.2 | 0.5 | 0.2
4973 | 30/07/2025 12:05:02.438 | 95.928 | 83 | 100 | 70 | 52 | 31.321 | 8.992 | 7.121 | 134.798 | 31.171 | 28.694 | 29.3 | 610.644 | 26.75 | 27.692 | 1267.092 | 27.508 | 27.757 | 39.981 | 26.001 | 3 | 4.1 | 1.6 | 0.7 | 0.2
4974 | 30/07/2025 12:05:04.073 | 96.048 | 81 | 100 | 71 | 52 | 32.845 | 9.268 | 7.121 | 134.587 | 31.173 | 28.681 | 29.264 | 610.508 | 26.75 | 27.716 | 1274.476 | 27.478 | 27.762 | 40.286 | 26.001 | 3 | 2.9 | 1.6 | 0.1 | 0.2
4975 | 30/07/2025 12:05:05.707 | 95.784 | 83 | 100 | 71 | 52 | 30.241 | 9.132 | 7.149 | 134.544 | 31.169 | 28.667 | 29.291 | 610.491 | 26.732 | 27.698 | 1277.161 | 27.482 | 27.75 | 40.174 | 27.001 | 4.6 | 3.2 | 1.3 | 0 | 0.2
4976 | 30/07/2025 12:05:07.341 | 95.328 | 81 | 100 | 71 | 51 | 29.168 | 9.138 | 7.136 | 132.998 | 31.153 | 28.7 | 29.287 | 610.658 | 26.755 | 27.718 | 1279.333 | 27.506 | 27.74 | 40.207 | 27.001 | 4.6 | 3.2 | 1.3 | 0 | 0.2
4977 | 30/07/2025 12:05:08.977 | 95.184 | 81 | 100 | 70 | 53 | 32.444 | 8.989 | 7.136 | 133.176 | 31.142 | 28.688 | 29.264 | 609.196 | 26.753 | 27.7 | 1282.007 | 27.486 | 27.718 | 38.381 | 27.001 | 4.6 | 2.7 | 1.3 | 0.5 | 0.2
4978 | 30/07/2025 12:05:10.611 | 95.832 | 83 | 100 | 70 | 52 | 28.614 | 8.87 | 7.171 | 133.106 | 31.162 | 28.706 | 29.277 | 609.195 | 26.743 | 27.733 | 1287.149 | 27.498 | 27.758 | 38.205 | 25.001 | 1.5 | 2.3 | 0.9 | 0.6 | 0.3
4979 | 30/07/2025 12:05:12.250 | 96.408 | 82 | 100 | 70 | 52 | 31.917 | 9.129 | 7.203 | 133.295 | 31.171 | 28.688 | 29.273 | 608.023 | 26.758 | 27.709 | 1285.108 | 27.451 | 27.746 | 38.576 | 25.001 | 1.5 | 4.7 | 0.9 | 0.6 | 0.3
4980 | 30/07/2025 12:05:13.885 | 96.144 | 82 | 100 | 72 | 52 | 32.828 | 9.319 | 7.133 | 133.214 | 31.175 | 28.674 | 29.303 | 608.152 | 26.737 | 27.703 | 1279.916 | 27.499 | 27.77 | 40.277 | 25.001 | 1.5 | 6.1 | 0.6 | 0 | 0.2
4981 | 30/07/2025 12:05:15.519 | 96.552 | 83 | 100 | 70 | 52 | 29.79 | 9.135 | 7.135 | 132.887 | 31.176 | 28.697 | 29.281 | 609.276 | 26.735 | 27.711 | 1274.127 | 27.492 | 27.727 | 40.153 | 25.001 | 1.5 | 5.9 | 0.6 | 0.5 | 0.2
4982 | 30/07/2025 12:05:17.154 | 96.552 | 82 | 100 | 70 | 52 | 29.713 | 9.127 | 7.134 | 133.186 | 31.184 | 28.691 | 29.286 | 609.252 | 26.751 | 27.693 | 1267.56 | 27.485 | 27.735 | 39.967 | 25.001 | 1.5 | 5.9 | 0.6 | 0.5 | 0.2
4983 | 30/07/2025 12:05:18.788 | 96.6 | 84 | 100 | 70 | 52 | 31.048 | 9.159 | 7.135 | 133.428 | 31.19 | 28.69 | 29.272 | 608.09 | 26.747 | 27.704 | 1267.506 | 27.471 | 27.743 | 40.036 | 29.001 | 2.4 | 4 | 0.7 | 0.5 | 0.3
4984 | 30/07/2025 12:05:20.422 | 96.792 | 84 | 100 | 70 | 52 | 28.805 | 9.337 | 7.148 | 133.358 | 31.185 | 28.678 | 29.276 | 608.054 | 26.731 | 27.696 | 1266.391 | 27.463 | 27.76 | 40.214 | 29.001 | 2.4 | 3.8 | 0.7 | 0.6 | 0.3
4985 | 30/07/2025 12:05:22.057 | 96.672 | 84 | 100 | 70 | 52 | 32.287 | 9.179 | 7.088 | 133.052 | 31.18 | 28.686 | 29.286 | 608.116 | 26.747 | 27.699 | 1274.22 | 27.496 | 27.749 | 40.463 | 24.001 | 2.8 | 3.3 | 1.2 | 0 | 0.3
4986 | 30/07/2025 12:05:23.693 | 96.936 | 83 | 100 | 70 | 52 | 32.762 | 9.205 | 7.072 | 133.391 | 31.188 | 28.698 | 29.279 | 607.982 | 26.751 | 27.691 | 1277.057 | 27.492 | 27.72 | 40.288 | 24.001 | 2.8 | 4.8 | 1.2 | 0 | 0.3
4987 | 30/07/2025 12:05:25.329 | 97.392 | 84 | 100 | 71 | 52 | 29.326 | 9.135 | 7.069 | 133.097 | 31.181 | 28.699 | 29.283 | 608.017 | 26.724 | 27.685 | 1274.583 | 27.495 | 27.766 | 40.066 | 24.001 | 2.8 | 4.8 | 1.2 | 0 | 0.3
4988 | 30/07/2025 12:05:26.964 | 97.32 | 85 | 100 | 70 | 53 | 30.12 | 9.136 | 7.07 | 133.153 | 31.164 | 28.678 | 29.26 | 607.925 | 26.726 | 27.694 | 1283.925 | 27.466 | 27.75 | 40.416 | 23.001 | 4.1 | 3.4 | 2.1 | 0 | 0.4
4989 | 30/07/2025 12:05:28.600 | 97.8 | 84 | 100 | 71 | 52 | 30.403 | 9.279 | 7.067 | 133.35 | 31.17 | 28.671 | 29.285 | 607.985 | 26.731 | 27.688 | 1287.497 | 27.49 | 27.75 | 40.162 | 23.001 | 4.1 | 2.5 | 2.1 | 0.6 | 0.4
4990 | 30/07/2025 12:05:30.239 | 97.44 | 83 | 100 | 70 | 52 | 29.18 | 9.279 | 7.088 | 132.943 | 31.163 | 28.689 | 29.286 | 606.925 | 26.723 | 27.679 | 1286.822 | 27.496 | 27.742 | 40.293 | 36.001 | 4.2 | 4.7 | 0.2 | 0.3 | 0.3
4991 | 30/07/2025 12:05:31.876 | 97.824 | 84 | 100 | 71 | 53 | 32.438 | 9.138 | 7.087 | 133.259 | 31.187 | 28.691 | 29.287 | 606.882 | 26.74 | 27.669 | 1269.611 | 27.495 | 27.729 | 40.122 | 36.001 | 4.2 | 5.5 | 0.2 | 0.5 | 0.3
4992 | 30/07/2025 12:05:33.514 | 97.44 | 83 | 99 | 70 | 52 | 32.512 | 9.133 | 7.121 | 133.239 | 31.171 | 28.7 | 29.269 | 606.819 | 26.738 | 27.686 | 1262.329 | 27.485 | 27.764 | 40.342 | 25.001 | 3.2 | 3 | 0.1 | 0.2 | 0.3
4993 | 30/07/2025 12:05:35.148 | 97.512 | 84 | 100 | 71 | 52 | 28.787 | 9.132 | 7.122 | 133.35 | 31.17 | 28.673 | 29.274 | 606.737 | 26.757 | 27.697 | 1266.794 | 27.471 | 27.752 | 40.214 | 25.001 | 3.2 | 3 | 0.1 | 0.2 | 0.3
4994 | 30/07/2025 12:05:36.782 | 97.368 | 83 | 99 | 71 | 51 | 32.835 | 9.241 | 7.12 | 133.095 | 31.167 | 28.671 | 29.292 | 606.787 | 26.749 | 27.683 | 1269.475 | 27.493 | 27.75 | 38.911 | 25.001 | 3.2 | 2.8 | 0.1 | 0 | 0.3
4995 | 30/07/2025 12:05:38.419 | 97.272 | 84 | 100 | 70 | 52 | 29.638 | 9.287 | 7.134 | 133.086 | 31.173 | 28.696 | 29.297 | 606.864 | 26.759 | 27.694 | 1272.284 | 27.493 | 27.745 | 39.799 | 23.001 | 2.9 | 3.3 | 0.9 | 0.5 | 0.2
4996 | 30/07/2025 12:05:40.054 | 97.68 | 84 | 100 | 71 | 52 | 29.631 | 9.291 | 7.133 | 133.2 | 31.143 | 28.694 | 29.284 | 605.61 | 26.746 | 27.699 | 1265.114 | 27.498 | 27.746 | 40.274 | 23.001 | 2.9 | 3.7 | 0.9 | 0.2 | 0.2
4997 | 30/07/2025 12:05:41.690 | 97.368 | 85 | 100 | 70 | 52 | 32.602 | 8.985 | 7.134 | 133.293 | 31.159 | 28.686 | 29.269 | 604.783 | 26.752 | 27.719 | 1264.04 | 27.472 | 27.759 | 40.354 | 26.001 | 1.2 | 5.7 | 1.9 | 0.5 | 0.3
4998 | 30/07/2025 12:05:43.325 | 97.512 | 84 | 100 | 70 | 52 | 32.196 | 9.412 | 7.132 | 133.167 | 31.153 | 28.666 | 29.28 | 604.333 | 26.739 | 27.709 | 1257.686 | 27.478 | 27.761 | 40.272 | 26.001 | 1.2 | 5.7 | 1.9 | 0.5 | 0.3
4999 | 30/07/2025 12:05:44.959 | 97.368 | 84 | 100 | 70 | 51 | 28.594 | 8.989 | 7.135 | 132.935 | 31.141 | 28.711 | 29.286 | 604.333 | 26.73 | 27.715 | 1273.325 | 27.497 | 27.742 | 40.279 | 26.001 | 1.2 | 3.7 | 1.9 | 0.5 | 0.3
5000 | 30/07/2025 12:05:46.594 | 97.08 | 83 | 100 | 70 | 52 | 32.742 | 9.081 | 7.134 | 133.017 | 31.17 | 28.694 | 29.292 | 604.419 | 26.736 | 27.689 | 1281.179 | 27.489 | 27.739 | 40.098 | 22.001 | 2.2 | 3.7 | 0 | 0.7 | 0.3
5001 | 30/07/2025 12:05:48.227 | 97.128 | 84 | 100 | 70 | 52 | 29.286 | 9.287 | 7.134 | 133.276 | 31.176 | 28.699 | 29.279 | 604.402 | 26.734 | 27.714 | 1294.242 | 27.498 | 27.754 | 40.118 | 22.001 | 2.2 | 3.7 | 0 | 0.8 | 0.3
5002 | 30/07/2025 12:05:49.862 | 97.056 | 84 | 100 | 70 | 52 | 30.332 | 9.211 | 7.135 | 133.354 | 31.187 | 28.683 | 29.256 | 604.346 | 26.755 | 27.705 | 1304.794 | 27.461 | 27.753 | 40.451 | 27.001 | 2 | 3.8 | 0.6 | 0 | 0.2
5003 | 30/07/2025 12:05:51.495 | 97.44 | 86 | 100 | 70 | 52 | 32.688 | 9.192 | 7.132 | 133.232 | 31.186 | 28.679 | 29.279 | 604.499 | 26.742 | 27.698 | 1320.117 | 27.501 | 27.758 | 40.419 | 27.001 | 2 | 2.7 | 0.6 | 0.5 | 0.2
5004 | 30/07/2025 12:05:53.129 | 97.536 | 84 | 100 | 70 | 52 | 31.553 | 9.294 | 7.137 | 132.95 | 31.181 | 28.698 | 29.299 | 604.271 | 26.747 | 27.707 | 1309.783 | 27.484 | 27.733 | 40.182 | 27.001 | 2 | 2.7 | 0.6 | 0.5 | 0.2
5005 | 30/07/2025 12:05:54.764 | 97.392 | 85 | 100 | 70 | 52 | 32.493 | 9.289 | 7.134 | 133.1 | 31.186 | 28.692 | 29.292 | 604.439 | 26.744 | 27.699 | 1306.759 | 27.504 | 27.746 | 40.149 | 25.001 | 2.5 | 2.8 | 1.3 | 0.2 | 0.2
5006 | 30/07/2025 12:05:56.399 | 97.608 | 86 | 100 | 70 | 53 | 32.555 | 9.283 | 7.136 | 133.182 | 31.189 | 28.684 | 29.266 | 604.381 | 26.752 | 27.71 | 1297.165 | 27.487 | 27.76 | 40.084 | 25.001 | 2.5 | 2.8 | 1.3 | 0.5 | 0.2
5007 | 30/07/2025 12:05:58.034 | 98.16 | 85 | 100 | 70 | 52 | 28.9 | 9.182 | 7.133 | 133.281 | 31.187 | 28.679 | 29.278 | 604.376 | 26.734 | 27.686 | 1287.257 | 27.456 | 27.759 | 40.295 | 25.001 | 2.9 | 3.7 | 1.5 | 0.5 | 0.2
5008 | 30/07/2025 12:05:59.669 | 97.632 | 84 | 100 | 70 | 53 | 30.843 | 9.116 | 7.134 | 133.089 | 31.183 | 28.682 | 29.29 | 604.414 | 26.718 | 27.7 | 1287.154 | 27.503 | 27.751 | 40.338 | 25.001 | 2.9 | 5.3 | 1.5 | 0.6 | 0.2
5009 | 30/07/2025 12:06:01.305 | 98.136 | 85 | 100 | 71 | 51 | 32.792 | 9.164 | 7.135 | 133.061 | 31.19 | 28.693 | 29.28 | 604.47 | 26.732 | 27.695 | 1291.292 | 27.488 | 27.728 | 40.2 | 25.001 | 2.9 | 5.3 | 1.5 | 0.6 | 0.2
5010 | 30/07/2025 12:06:02.940 | 97.56 | 84 | 100 | 70 | 53 | 31.041 | 9.094 | 7.134 | 133.353 | 31.173 | 28.695 | 29.283 | 604.393 | 26.733 | 27.67 | 1284.922 | 27.507 | 27.767 | 40.031 | 18 | 2.6 | 3.2 | 1 | 0.1 | 0.2
5011 | 30/07/2025 12:06:04.573 | 97.512 | 84 | 100 | 70 | 52 | 32.604 | 9.091 | 7.134 | 133.233 | 31.186 | 28.686 | 29.272 | 604.339 | 26.714 | 27.682 | 1284.642 | 27.474 | 27.748 | 40.126 | 18 | 2.6 | 5.2 | 1 | 0.5 | 0.2
5012 | 30/07/2025 12:06:06.208 | 97.776 | 87 | 100 | 70 | 52 | 32.177 | 9.214 | 7.133 | 133.061 | 31.18 | 28.66 | 29.273 | 604.272 | 26.729 | 27.679 | 1281.294 | 27.481 | 27.758 | 38.655 | 23.001 | 2.2 | 3.8 | 0.7 | 0.6 | 0.2
5013 | 30/07/2025 12:06:07.843 | 97.368 | 83 | 100 | 70 | 52 | 28.663 | 9.141 | 7.136 | 132.958 | 31.177 | 28.693 | 29.278 | 604.304 | 26.744 | 27.682 | 1281.964 | 27.498 | 27.745 | 40.448 | 23.001 | 2.2 | 2.9 | 0.7 | 0.5 | 0.2
5014 | 30/07/2025 12:06:09.485 | 97.368 | 82 | 100 | 71 | 54 | 31.332 | 9.217 | 7.135 | 133.329 | 31.174 | 28.691 | 29.296 | 604.536 | 26.733 | 27.689 | 1271.841 | 27.497 | 27.742 | 40.007 | 23.001 | 4.6 | 5.4 | 0.4 | 0.2 | 0.1
5015 | 30/07/2025 12:06:11.119 | 98.064 | 84 | 100 | 71 | 52 | 32.849 | 9.285 | 7.135 | 133.172 | 31.163 | 28.689 | 29.284 | 604.366 | 26.742 | 27.711 | 1272.153 | 27.487 | 27.758 | 40.168 | 23.001 | 4.6 | 5.4 | 0.4 | 0.2 | 0.1
5016 | 30/07/2025 12:06:12.754 | 98.064 | 85 | 100 | 71 | 52 | 30.127 | 9.224 | 7.132 | 133.241 | 31.162 | 28.69 | 29.273 | 604.388 | 26.743 | 27.684 | 1275.325 | 27.467 | 27.767 | 40.279 | 23.001 | 4.6 | 5.2 | 0.4 | 0.5 | 0.1
5017 | 30/07/2025 12:06:14.388 | 98.04 | 85 | 100 | 69 | 52 | 32.716 | 9.13 | 7.151 | 132.959 | 31.158 | 28.674 | 29.285 | 602.897 | 26.748 | 27.716 | 1277.194 | 27.484 | 27.752 | 40.27 | 29.001 | 3.3 | 1.6 | 0.6 | 0 | 0.2
5018 | 30/07/2025 12:06:16.028 | 97.92 | 84 | 100 | 69 | 53 | 31.562 | 9.134 | 7.152 | 132.969 | 31.161 | 28.703 | 29.3 | 603.224 | 26.751 | 27.7 | 1274.283 | 27.492 | 27.742 | 40.166 | 29.001 | 3.3 | 4.4 | 0.6 | 0 | 0.2
5019 | 30/07/2025 12:06:17.676 | 98.064 | 84 | 100 | 70 | 52 | 28.595 | 8.991 | 7.149 | 133.302 | 31.154 | 28.707 | 29.277 | 603.373 | 26.74 | 27.713 | 1277.62 | 27.516 | 27.741 | 40.004 | 29.001 | 1.5 | 3.9 | 0.6 | 1 | 0.1
5020 | 30/07/2025 12:06:19.312 | 97.056 | 82 | 100 | 70 | 51 | 31.826 | 9.131 | 7.136 | 133.262 | 31.168 | 28.682 | 29.264 | 603.092 | 26.737 | 27.708 | 1284.719 | 27.472 | 27.755 | 40.231 | 29.001 | 1.5 | 3.9 | 0.6 | 1 | 0.1
5021 | 30/07/2025 12:06:20.950 | 96.912 | 84 | 100 | 70 | 53 | 28.859 | 9.211 | 7.132 | 133.054 | 31.163 | 28.681 | 29.267 | 603.219 | 26.738 | 27.703 | 1279.634 | 27.472 | 27.76 | 40.256 | 29.001 | 1.5 | 4.1 | 0.6 | 0.5 | 0.1
5022 | 30/07/2025 12:06:22.585 | 97.176 | 84 | 100 | 70 | 52 | 30.862 | 9.217 | 7.136 | 133.198 | 31.187 | 28.675 | 29.286 | 602.898 | 26.755 | 27.698 | 1272.236 | 27.486 | 27.74 | 40.244 | 29.001 | 2.9 | 3.8 | 0.9 | 0.9 | 0.1
5023 | 30/07/2025 12:06:24.220 | 97.392 | 84 | 100 | 71 | 52 | 32.755 | 9.292 | 7.133 | 132.904 | 31.192 | 28.698 | 29.29 | 604.594 | 26.746 | 27.692 | 1257.226 | 27.497 | 27.744 | 40.164 | 29.001 | 2.9 | 3.9 | 0.9 | 1.1 | 0.1
5024 | 30/07/2025 12:06:25.856 | 97.752 | 86 | 100 | 71 | 52 | 30.939 | 9.205 | 7.135 | 133.334 | 31.182 | 28.689 | 29.286 | 604.433 | 26.743 | 27.715 | 1247.479 | 27.482 | 27.748 | 39.786 | 27.001 | 3 | 3.9 | 1.2 | 0.6 | 0.2
5025 | 30/07/2025 12:06:27.489 | 97.848 | 84 | 100 | 70 | 52 | 28.821 | 9.435 | 7.151 | 133.244 | 31.192 | 28.68 | 29.268 | 603.208 | 26.744 | 27.697 | 1232.797 | 27.469 | 27.75 | 40.208 | 27.001 | 3 | 3.2 | 1.2 | 0.7 | 0.2
5026 | 30/07/2025 12:06:29.125 | 97.152 | 84 | 100 | 71 | 52 | 32.268 | 9.29 | 7.133 | 133.165 | 31.186 | 28.669 | 29.29 | 603.151 | 26.733 | 27.696 | 1238.025 | 27.503 | 27.751 | 40.282 | 27.001 | 3 | 3.2 | 1.2 | 0.7 | 0.2
5027 | 30/07/2025 12:06:30.760 | 96.936 | 83 | 100 | 70 | 52 | 28.641 | 9.291 | 7.135 | 133.11 | 31.19 | 28.695 | 29.308 | 603.023 | 26.732 | 27.688 | 1239.922 | 27.496 | 27.748 | 40.247 | 27.001 | 4 | 4.5 | 0.6 | 0.5 | 0.2
5028 | 30/07/2025 12:06:32.396 | 96.576 | 83 | 100 | 70 | 52 | 31.348 | 9.29 | 7.134 | 132.975 | 31.189 | 28.708 | 29.295 | 603.18 | 26.734 | 27.705 | 1246.379 | 27.506 | 27.744 | 40.135 | 27.001 | 4 | 2.8 | 0.6 | 0.2 | 0.2
5029 | 30/07/2025 12:06:34.033 | 96.696 | 83 | 100 | 70 | 51 | 32.865 | 9.213 | 7.136 | 133.239 | 31.192 | 28.684 | 29.273 | 603.099 | 26.74 | 27.688 | 1249.472 | 27.48 | 27.743 | 40.017 | 28.001 | 2.1 | 3.1 | 0 | 0.8 | 0.2
5030 | 30/07/2025 12:06:35.668 | 96.36 | 82 | 100 | 71 | 52 | 30.446 | 9.145 | 7.185 | 134.707 | 31.175 | 28.675 | 29.271 | 603.301 | 26.728 | 27.673 | 1258.208 | 27.469 | 27.756 | 40.297 | 28.001 | 2.1 | 4.7 | 0 | 0.5 | 0.2
5031 | 30/07/2025 12:06:37.304 | 96.168 | 82 | 100 | 70 | 53 | 29.228 | 8.989 | 7.187 | 134.237 | 31.173 | 28.676 | 29.279 | 603.134 | 26.731 | 27.693 | 1279.24 | 27.503 | 27.748 | 40.29 | 28.001 | 2.1 | 4.7 | 0 | 0.5 | 0.2
5032 | 30/07/2025 12:06:38.939 | 96.384 | 84 | 100 | 70 | 52 | 31.693 | 8.984 | 7.186 | 134.566 | 31.171 | 28.7 | 29.293 | 603.129 | 26.713 | 27.672 | 1282.447 | 27.516 | 27.751 | 40.264 | 30.001 | 3.1 | 5.4 | 1.2 | 0.5 | 0.2
5033 | 30/07/2025 12:06:40.576 | 96.336 | 82 | 100 | 70 | 52 | 28.623 | 9.287 | 7.092 | 133.087 | 31.172 | 28.69 | 29.284 | 603.085 | 26.728 | 27.688 | 1274.112 | 27.474 | 27.728 | 40.086 | 30.001 | 3.1 | 3.5 | 1.2 | 0.1 | 0.2
5034 | 30/07/2025 12:06:42.210 | 96.816 | 83 | 100 | 71 | 52 | 31.894 | 8.984 | 7.069 | 133.272 | 31.179 | 28.687 | 29.283 | 603.237 | 26.742 | 27.669 | 1272.144 | 27.478 | 27.75 | 40.18 | 21.001 | 3.2 | 4 | 1.2 | 0 | 0.2
5035 | 30/07/2025 12:06:43.845 | 96.432 | 82 | 100 | 70 | 51 | 32.842 | 9.277 | 7.07 | 133.126 | 31.175 | 28.682 | 29.273 | 603.185 | 26.743 | 27.7 | 1263.93 | 27.481 | 27.754 | 40.214 | 21.001 | 3.2 | 5.1 | 1.2 | 0.5 | 0.2
5036 | 30/07/2025 12:06:45.479 | 96.768 | 84 | 99 | 71 | 52 | 29.854 | 9.135 | 7.072 | 133.019 | 31.161 | 28.693 | 29.278 | 603.096 | 26.756 | 27.701 | 1251.166 | 27.507 | 27.727 | 40.287 | 28.001 | 3.3 | 2.9 | 0.6 | 0 | 0.3
5037 | 30/07/2025 12:06:47.114 | 96.456 | 83 | 100 | 71 | 51 | 29.593 | 9.136 | 7.067 | 133.211 | 31.169 | 28.692 | 29.284 | 603.468 | 26.743 | 27.7 | 1239.5 | 27.499 | 27.734 | 40.095 | 28.001 | 3.3 | 2.9 | 0.6 | 0 | 0.3
5038 | 30/07/2025 12:06:48.749 | 96.648 | 83 | 100 | 71 | 52 | 31 | 9.208 | 7.071 | 133.36 | 31.166 | 28.691 | 29.292 | 603.186 | 26.766 | 27.705 | 1237.259 | 27.487 | 27.742 | 39.971 | 28.001 | 3.3 | 2.8 | 0.6 | 0.5 | 0.3
5039 | 30/07/2025 12:06:50.381 | 96.24 | 82 | 100 | 70 | 51 | 28.773 | 9.133 | 7.068 | 133.19 | 31.145 | 28.69 | 29.263 | 603.279 | 26.737 | 27.704 | 1245.081 | 27.474 | 27.769 | 40.305 | 21.001 | 1.5 | 2.2 | 0.4 | 0.6 | 0.3
5040 | 30/07/2025 12:06:52.016 | 96.144 | 83 | 100 | 70 | 52 | 32.187 | 8.988 | 7.119 | 133.11 | 31.151 | 28.662 | 29.276 | 603.117 | 26.751 | 27.711 | 1255.146 | 27.463 | 27.753 | 40.323 | 21.001 | 1.5 | 2.3 | 0.4 | 0.7 | 0.3
5041 | 30/07/2025 12:06:53.650 | 95.424 | 82 | 100 | 70 | 52 | 32.754 | 9.132 | 7.121 | 133.04 | 31.176 | 28.7 | 29.294 | 603.145 | 26.743 | 27.692 | 1246.712 | 27.489 | 27.744 | 40.134 | 26.001 | 2.3 | 2.6 | 0.9 | 0 | 0.2
5042 | 30/07/2025 12:06:55.283 | 94.872 | 82 | 100 | 70 | 51 | 29.218 | 9.18 | 7.134 | 133.085 | 31.186 | 28.705 | 29.286 | 602.345 | 26.731 | 27.704 | 1246.101 | 27.506 | 27.728 | 40.049 | 26.001 | 2.3 | 2.6 | 0.9 | 0 | 0.2
5043 | 30/07/2025 12:06:56.918 | 94.656 | 82 | 100 | 70 | 54 | 30.202 | 8.988 | 7.136 | 134.749 | 31.19 | 28.689 | 29.267 | 601.931 | 26.753 | 27.698 | 1239.984 | 27.479 | 27.74 | 40.39 | 26.001 | 2.3 | 3.5 | 0.9 | 0.5 | 0.2
5044 | 30/07/2025 12:06:58.552 | 94.272 | 82 | 100 | 70 | 51 | 30.313 | 8.985 | 7.134 | 134.468 | 31.187 | 28.678 | 29.254 | 602.082 | 26.743 | 27.719 | 1242.431 | 27.469 | 27.753 | 40.4 | 26.001 | 3.2 | 2 | 0.1 | 0 | 0.2
5045 | 30/07/2025 12:07:00.189 | 94.44 | 82 | 100 | 70 | 52 | 29.117 | 8.952 | 7.135 | 133.286 | 31.186 | 28.671 | 29.287 | 601.77 | 26.759 | 27.706 | 1243.658 | 27.482 | 27.744 | 40.214 | 26.001 | 3.2 | 4.3 | 0.1 | 0.5 | 0.2
5046 | 30/07/2025 12:07:01.826 | 94.368 | 83 | 100 | 71 | 51 | 32.468 | 8.945 | 7.099 | 133.098 | 31.189 | 28.698 | 29.303 | 603.278 | 26.741 | 27.698 | 1266.447 | 27.502 | 27.754 | 40.149 | 25.001 | 3.7 | 5.5 | 0 | 0.8 | 0.2
5047 | 30/07/2025 12:07:03.461 | 94.8 | 82 | 100 | 70 | 52 | 32.548 | 9.132 | 7.09 | 133.256 | 31.18 | 28.693 | 29.279 | 603.206 | 26.732 | 27.706 | 1262.538 | 27.491 | 27.742 | 39.942 | 25.001 | 3.7 | 3.1 | 0 | 1 | 0.2
5048 | 30/07/2025 12:07:05.098 | 95.328 | 82 | 100 | 70 | 52 | 28.788 | 8.965 | 7.086 | 133.306 | 31.192 | 28.688 | 29.268 | 603.234 | 26.73 | 27.692 | 1265.963 | 27.472 | 27.763 | 38.338 | 25.001 | 3.7 | 3.1 | 0 | 1 | 0.2
5049 | 30/07/2025 12:07:06.735 | 95.352 | 82 | 100 | 71 | 52 | 32.827 | 8.917 | 7.085 | 133.202 | 31.174 | 28.669 | 29.257 | 603.022 | 26.736 | 27.702 | 1275.393 | 27.452 | 27.742 | 38.522 | 33.001 | 1.6 | 1.7 | 1.2 | 0.1 | 0.2
5050 | 30/07/2025 12:07:08.370 | 95.688 | 82 | 100 | 71 | 52 | 29.809 | 9.137 | 7.085 | 133.165 | 31.19 | 28.687 | 29.308 | 603.211 | 26.731 | 27.681 | 1262.691 | 27.505 | 27.754 | 38.387 | 33.001 | 1.6 | 3.2 | 1.2 | 1 | 0.2
5051 | 30/07/2025 12:07:10.006 | 95.592 | 83 | 100 | 70 | 51 | 29.723 | 9.14 | 7.087 | 132.819 | 31.182 | 28.709 | 29.278 | 603.252 | 26.721 | 27.692 | 1267.128 | 27.496 | 27.739 | 38.406 | 22.001 | 2.3 | 3.7 | 0.7 | 1.7 | 0.1
5052 | 30/07/2025 12:07:11.640 | 95.376 | 81 | 100 | 70 | 52 | 32.65 | 9.13 | 7.088 | 133.391 | 31.179 | 28.688 | 29.288 | 603.161 | 26.742 | 27.688 | 1260.52 | 27.484 | 27.743 | 38.285 | 22.001 | 2.3 | 2.3 | 0.7 | 0.2 | 0.1
5053 | 30/07/2025 12:07:13.276 | 96.264 | 83 | 100 | 72 | 51 | 32.228 | 9.202 | 7.123 | 131.74 | 31.171 | 28.679 | 29.28 | 603.261 | 26.717 | 27.675 | 1258.753 | 27.476 | 27.774 | 38.607 | 22.001 | 2.3 | 2.3 | 0.7 | 0.2 | 0.1
5054 | 30/07/2025 12:07:14.910 | 96.312 | 83 | 100 | 71 | 51 | 32.281 | 9.211 | 7.12 | 131.768 | 31.187 | 28.676 | 29.293 | 603.19 | 26.75 | 27.683 | 1261.651 | 27.472 | 27.762 | 38.225 | 28.001 | 2.7 | 5.1 | 0 | 0 | 0.2
5055 | 30/07/2025 12:07:16.543 | 96.624 | 83 | 100 | 70 | 52 | 32.744 | 8.847 | 7.134 | 131.619 | 31.167 | 28.698 | 29.273 | 603.254 | 26.722 | 27.677 | 1274.439 | 27.515 | 27.747 | 38.498 | 28.001 | 2.7 | 4 | 0 | 0.5 | 0.2
5056 | 30/07/2025 12:07:18.175 | 97.032 | 84 | 100 | 70 | 52 | 29.288 | 8.966 | 7.135 | 131.351 | 31.165 | 28.693 | 29.295 | 603.201 | 26.75 | 27.703 | 1271.951 | 27.486 | 27.729 | 38.238 | 24.001 | 2 | 4.7 | 0 | 0.6 | 0.1
5057 | 30/07/2025 12:07:19.810 | 96.816 | 83 | 100 | 69 | 52 | 30.142 | 9.027 | 7.133 | 131.795 | 31.174 | 28.691 | 29.289 | 603.228 | 26.742 | 27.686 | 1263.297 | 27.485 | 27.747 | 39.811 | 24.001 | 2 | 3.3 | 0 | 0.8 | 0.1
5058 | 30/07/2025 12:07:21.444 | 96.936 | 84 | 100 | 71 | 52 | 32.73 | 8.913 | 7.132 | 131.572 | 31.164 | 28.67 | 29.277 | 602.969 | 26.736 | 27.71 | 1257.464 | 27.466 | 27.75 | 38.483 | 26.001 | 3.3 | 2.6 | 1.2 | 0.1 | 0.1
5059 | 30/07/2025 12:07:23.078 | 96.84 | 85 | 100 | 71 | 53 | 31.692 | 8.988 | 7.137 | 131.701 | 31.159 | 28.697 | 29.295 | 602.9 | 26.769 | 27.721 | 1259.478 | 27.492 | 27.753 | 38.203 | 26.001 | 3.3 | 2.6 | 1.2 | 0.1 | 0.1
5060 | 30/07/2025 12:07:24.714 | 97.296 | 84 | 100 | 70 | 52 | 32.487 | 8.991 | 7.134 | 131.351 | 31.152 | 28.699 | 29.283 | 601.996 | 26.751 | 27.73 | 1264.873 | 27.491 | 27.741 | 38.474 | 26.001 | 3.3 | 2.5 | 1.2 | 0 | 0.1
5061 | 30/07/2025 12:07:26.349 | 97.464 | 84 | 100 | 72 | 52 | 32.585 | 9.158 | 7.135 | 131.848 | 31.159 | 28.693 | 29.287 | 603.18 | 26.745 | 27.699 | 1262.227 | 27.484 | 27.739 | 39.581 | 22.001 | 5 | 3.2 | 1.1 | 0 | 0.1
5062 | 30/07/2025 12:07:27.985 | 97.44 | 84 | 100 | 71 | 52 | 28.917 | 9.143 | 7.134 | 131.571 | 31.162 | 28.696 | 29.287 | 603.24 | 26.753 | 27.698 | 1261.037 | 27.489 | 27.766 | 38.462 | 22.001 | 5 | 6 | 1.1 | 0.5 | 0.1
5063 | 30/07/2025 12:07:29.620 | 97.584 | 84 | 100 | 70 | 52 | 30.792 | 9.131 | 7.134 | 131.615 | 31.187 | 28.671 | 29.282 | 603.055 | 26.745 | 27.709 | 1255.874 | 27.473 | 27.751 | 38.465 | 30.001 | 1.8 | 3.9 | 0.6 | 1.1 | 0.2
5064 | 30/07/2025 12:07:31.255 | 97.992 | 86 | 100 | 71 | 52 | 32.75 | 9.133 | 7.123 | 131.56 | 31.178 | 28.692 | 29.298 | 603.171 | 26.74 | 27.685 | 1251.532 | 27.505 | 27.744 | 38.361 | 30.001 | 1.8 | 3.9 | 0.6 | 1.1 | 0.2
5065 | 30/07/2025 12:07:32.890 | 97.944 | 84 | 100 | 70 | 52 | 29.627 | 9.136 | 7.122 | 131.535 | 31.182 | 28.688 | 29.281 | 603.187 | 26.748 | 27.699 | 1246.909 | 27.488 | 27.724 | 39.956 | 30.001 | 1.8 | 3.5 | 0.6 | 0.6 | 0.2
5066 | 30/07/2025 12:07:34.525 | 97.296 | 83 | 100 | 72 | 51 | 32.58 | 9.164 | 7.121 | 131.86 | 31.17 | 28.694 | 29.303 | 603.317 | 26.738 | 27.701 | 1257.219 | 27.489 | 27.76 | 38.144 | 27.001 | 3.6 | 2.1 | 1.5 | 0.5 | 0.1
5067 | 30/07/2025 12:07:36.161 | 97.2 | 84 | 100 | 70 | 52 | 32.106 | 8.859 | 7.12 | 131.591 | 31.186 | 28.682 | 29.253 | 603.197 | 26.736 | 27.713 | 1247.543 | 27.47 | 27.754 | 38.587 | 27.001 | 3.6 | 4.2 | 1.5 | 0.6 | 0.1
5068 | 30/07/2025 12:07:37.797 | 97.512 | 84 | 100 | 71 | 52 | 28.612 | 9.128 | 7.086 | 131.645 | 31.189 | 28.675 | 29.291 | 602.999 | 26.747 | 27.699 | 1256.986 | 27.483 | 27.746 | 38.346 | 23.001 | 2.7 | 5.4 | 0 | 0.5 | 0.1
5069 | 30/07/2025 12:07:39.432 | 97.56 | 84 | 100 | 71 | 52 | 31.262 | 9.278 | 7.086 | 131.566 | 31.176 | 28.694 | 29.297 | 603.223 | 26.729 | 27.688 | 1264.619 | 27.512 | 27.747 | 38.438 | 23.001 | 2.7 | 4.5 | 0 | 0.6 | 0.1
5070 | 30/07/2025 12:07:41.066 | 98.112 | 85 | 100 | 70 | 53 | 29.229 | 9.133 | 7.087 | 131.72 | 31.186 | 28.689 | 29.285 | 603.392 | 26.731 | 27.68 | 1267.003 | 27.486 | 27.719 | 38.069 | 23.001 | 2.7 | 4.5 | 0 | 0.6 | 0.1
5071 | 30/07/2025 12:07:42.701 | 98.616 | 86 | 100 | 70 | 52 | 30.204 | 9.159 | 7.086 | 131.526 | 31.184 | 28.704 | 29.289 | 603.181 | 26.726 | 27.692 | 1266.922 | 27.501 | 27.771 | 40.25 | 26.001 | 3.1 | 3.6 | 0.7 | 0.5 | 0.1
5072 | 30/07/2025 12:07:44.337 | 99.024 | 85 | 100 | 70 | 51 | 32.682 | 9.068 | 7.087 | 131.835 | 31.169 | 28.671 | 29.255 | 603.223 | 26.737 | 27.697 | 1262.294 | 27.46 | 27.745 | 40.445 | 26.001 | 3.1 | 4.2 | 0.7 | 0 | 0.1
5073 | 30/07/2025 12:07:45.972 | 98.808 | 86 | 100 | 71 | 52 | 31.724 | 8.988 | 7.133 | 131.78 | 31.186 | 28.686 | 29.311 | 603.075 | 26.737 | 27.672 | 1262.178 | 27.498 | 27.761 | 40.187 | 26.001 | 3.3 | 2 | 0.2 | 0 | 0.1
5074 | 30/07/2025 12:07:47.607 | 98.304 | 85 | 100 | 70 | 52 | 28.668 | 8.99 | 7.133 | 131.503 | 31.178 | 28.703 | 29.294 | 603.235 | 26.734 | 27.691 | 1259.066 | 27.505 | 27.736 | 40.165 | 26.001 | 3.3 | 1.8 | 0.2 | 0.5 | 0.1
5075 | 30/07/2025 12:07:49.243 | 98.472 | 84 | 100 | 70 | 52 | 31.891 | 9.202 | 7.135 | 131.754 | 31.179 | 28.692 | 29.274 | 603.26 | 26.751 | 27.682 | 1258.224 | 27.492 | 27.743 | 39.96 | 26.001 | 3.3 | 1.8 | 0.2 | 0.5 | 0.1
5076 | 30/07/2025 12:07:50.877 | 98.712 | 87 | 100 | 71 | 52 | 28.936 | 9.133 | 7.135 | 131.679 | 31.17 | 28.689 | 29.262 | 603.245 | 26.735 | 27.694 | 1259.918 | 27.476 | 27.746 | 40.13 | 24.001 | 3 | 1.7 | 0 | 0.6 | 0.1
5077 | 30/07/2025 12:07:52.511 | 99.024 | 85 | 100 | 71 | 52 | 30.801 | 9.207 | 7.133 | 131.775 | 31.174 | 28.672 | 29.271 | 603.046 | 26.751 | 27.684 | 1260.395 | 27.467 | 27.752 | 40.308 | 24.001 | 3 | 4.8 | 0 | 0.5 | 0.1
5078 | 30/07/2025 12:07:54.147 | 98.952 | 86 | 100 | 71 | 52 | 32.842 | 9.138 | 7.135 | 131.586 | 31.17 | 28.707 | 29.3 | 603.177 | 26.744 | 27.718 | 1262.555 | 27.513 | 27.76 | 40.318 | 31.001 | 2.4 | 3.2 | 0.1 | 0 | 0.2
5079 | 30/07/2025 12:07:55.781 | 98.256 | 86 | 100 | 70 | 52 | 31.144 | 9.158 | 7.136 | 131.531 | 31.15 | 28.702 | 29.289 | 603.125 | 26.748 | 27.704 | 1267.048 | 27.485 | 27.739 | 40.208 | 31.001 | 2.4 | 3.3 | 0.1 | 0 | 0.2
5080 | 30/07/2025 12:07:57.421 | 98.064 | 85 | 100 | 71 | 52 | 28.794 | 9.237 | 7.186 | 133.44 | 31.153 | 28.69 | 29.276 | 603.342 | 26.733 | 27.686 | 1262.01 | 27.483 | 27.745 | 40.349 | 24.001 | 1.4 | 2 | 0 | 0.6 | 0.2
5081 | 30/07/2025 12:07:59.058 | 97.968 | 84 | 100 | 71 | 52 | 32.291 | 9.133 | 7.176 | 133.135 | 31.167 | 28.686 | 29.259 | 603.175 | 26.761 | 27.71 | 1257.148 | 27.47 | 27.766 | 40.319 | 24.001 | 1.4 | 2 | 0 | 0.6 | 0.2
5082 | 30/07/2025 12:08:00.695 | 98.112 | 84 | 100 | 70 | 53 | 28.742 | 9.138 | 7.133 | 133.173 | 31.154 | 28.674 | 29.292 | 603.219 | 26.736 | 27.701 | 1257.967 | 27.485 | 27.763 | 40.48 | 24.001 | 1.4 | 1 | 0 | 0.1 | 0.2
5083 | 30/07/2025 12:08:02.329 | 98.088 | 85 | 100 | 69 | 53 | 31.486 | 9 | 7.088 | 133.009 | 31.169 | 28.695 | 29.276 | 603.202 | 26.746 | 27.708 | 1266.159 | 27.49 | 27.744 | 40.28 | 28.001 | 2.5 | 3.1 | 0.8 | 0 | 0.2
5084 | 30/07/2025 12:08:03.965 | 98.496 | 87 | 100 | 70 | 53 | 32.843 | 8.953 | 7.086 | 133.207 | 31.193 | 28.697 | 29.298 | 603.154 | 26.744 | 27.689 | 1267.297 | 27.496 | 27.74 | 39.967 | 28.001 | 2.5 | 4.3 | 0.8 | 0.6 | 0.2
5085 | 30/07/2025 12:08:05.598 | 98.328 | 85 | 100 | 70 | 52 | 30.443 | 9.131 | 7.12 | 133.136 | 31.186 | 28.687 | 29.271 | 603.229 | 26.743 | 27.697 | 1264.654 | 27.492 | 27.745 | 40.162 | 27.001 | 2.3 | 3.4 | 0.6 | 1.2 | 0.2
5086 | 30/07/2025 12:08:07.233 | 98.712 | 86 | 100 | 70 | 52 | 29.088 | 8.838 | 7.133 | 133.09 | 31.179 | 28.664 | 29.27 | 602.998 | 26.741 | 27.702 | 1271.103 | 27.472 | 27.737 | 40.214 | 27.001 | 2.3 | 3.4 | 0.6 | 1.2 | 0.2
5087 | 30/07/2025 12:08:08.867 | 98.688 | 86 | 100 | 71 | 53 | 31.549 | 9.053 | 7.134 | 133.077 | 31.171 | 28.678 | 29.289 | 601.961 | 26.732 | 27.704 | 1267.602 | 27.505 | 27.751 | 40.245 | 27.001 | 2.3 | 2.1 | 0.6 | 0.5 | 0.2
5088 | 30/07/2025 12:08:10.504 | 98.328 | 86 | 100 | 71 | 52 | 28.615 | 9.22 | 7.124 | 133.08 | 31.189 | 28.697 | 29.284 | 601.907 | 26.754 | 27.695 | 1276.9 | 27.496 | 27.727 | 40.183 | 26.001 | 1.8 | 3.3 | 0.6 | 1.1 | 0.3
5089 | 30/07/2025 12:08:12.139 | 97.68 | 84 | 100 | 70 | 52 | 31.732 | 9.435 | 7.114 | 133.316 | 31.182 | 28.704 | 29.293 | 602.108 | 26.734 | 27.692 | 1284.954 | 27.502 | 27.754 | 40.021 | 26.001 | 1.8 | 2.7 | 0.6 | 0.3 | 0.3
5090 | 30/07/2025 12:08:13.774 | 97.992 | 84 | 100 | 70 | 52 | 32.834 | 9.288 | 7.084 | 133.103 | 31.171 | 28.683 | 29.258 | 601.967 | 26.738 | 27.722 | 1287.079 | 27.467 | 27.759 | 40.409 | 32.001 | 2.6 | 4.6 | 0.6 | 0.5 | 0.3
5091 | 30/07/2025 12:08:15.409 | 98.376 | 86 | 100 | 71 | 52 | 29.716 | 9.284 | 7.109 | 133.191 | 31.188 | 28.677 | 29.296 | 601.976 | 26.736 | 27.694 | 1291.805 | 27.486 | 27.75 | 40.215 | 32.001 | 2.6 | 4.2 | 0.6 | 0.2 | 0.3
5092 | 30/07/2025 12:08:17.046 | 97.872 | 84 | 100 | 68 | 52 | 32.73 | 9.291 | 7.122 | 133.08 | 31.178 | 28.687 | 29.292 | 601.836 | 26.725 | 27.694 | 1292.131 | 27.495 | 27.746 | 40.242 | 32.001 | 2.6 | 4.2 | 0.6 | 0.2 | 0.3
5093 | 30/07/2025 12:08:18.680 | 97.872 | 85 | 100 | 70 | 52 | 31.002 | 9.134 | 7.122 | 133.227 | 31.171 | 28.698 | 29.292 | 602.185 | 26.738 | 27.68 | 1289.656 | 27.489 | 27.717 | 40.092 | 27.001 | 2.3 | 4.2 | 1 | 0 | 0.2
5094 | 30/07/2025 12:08:20.314 | 98.136 | 86 | 100 | 69 | 52 | 28.787 | 8.987 | 7.122 | 133.06 | 31.167 | 28.698 | 29.279 | 601.998 | 26.728 | 27.685 | 1289.832 | 27.5 | 27.761 | 40.013 | 27.001 | 2.3 | 3.7 | 1 | 0 | 0.2
5095 | 30/07/2025 12:08:21.950 | 98.136 | 84 | 100 | 71 | 53 | 32.2 | 9.132 | 7.12 | 133.222 | 31.182 | 28.676 | 29.267 | 601.923 | 26.742 | 27.688 | 1287.388 | 27.452 | 27.747 | 40.254 | 27.001 | 2.4 | 3.6 | 1.2 | 0 | 0.2
5096 | 30/07/2025 12:08:23.581 | 98.568 | 87 | 100 | 70 | 51 | 32.73 | 9.128 | 7.12 | 133.208 | 31.176 | 28.687 | 29.296 | 602.031 | 26.731 | 27.687 | 1287.648 | 27.487 | 27.764 | 40.176 | 27.001 | 2.4 | 4.9 | 1.2 | 0.5 | 0.2
5097 | 30/07/2025 12:08:25.217 | 99.168 | 85 | 100 | 70 | 52 | 29.254 | 8.985 | 7.122 | 133.052 | 31.168 | 28.698 | 29.291 | 601.921 | 26.74 | 27.697 | 1289.664 | 27.49 | 27.733 | 38.609 | 27.001 | 2.4 | 4.9 | 1.2 | 0.5 | 0.2
5098 | 30/07/2025 12:08:26.852 | 98.832 | 86 | 100 | 70 | 52 | 32.867 | 9.127 | 7.123 | 133.321 | 31.174 | 28.7 | 29.293 | 602.077 | 26.73 | 27.677 | 1292.086 | 27.506 | 27.74 | 38.421 | 25.001 | 2.8 | 3.6 | 1 | 0 | 0.2
5099 | 30/07/2025 12:08:28.487 | 98.952 | 87 | 100 | 70 | 52 | 30.454 | 8.986 | 7.124 | 133.177 | 31.16 | 28.689 | 29.268 | 601.837 | 26.729 | 27.706 | 1287.348 | 27.477 | 27.753 | 40.13 | 25.001 | 2.8 | 3.4 | 1 | 0 | 0.2
5100 | 30/07/2025 12:08:30.121 | 98.688 | 84 | 100 | 71 | 52 | 29.113 | 9.171 | 7.119 | 133.134 | 31.159 | 28.676 | 29.28 | 601.965 | 26.742 | 27.705 | 1287.329 | 27.462 | 27.756 | 38.464 | 27.001 | 5 | 3 | 0.8 | 0 | 0.3
5101 | 30/07/2025 12:08:31.757 | 98.712 | 85 | 100 | 70 | 52 | 32.491 | 9.102 | 7.133 | 133.03 | 31.161 | 28.701 | 29.284 | 601.865 | 26.744 | 27.708 | 1287.166 | 27.498 | 27.751 | 38.337 | 27.001 | 5 | 3.9 | 0.8 | 0.5 | 0.3
5102 | 30/07/2025 12:08:33.393 | 98.424 | 86 | 100 | 71 | 51 | 32.618 | 9.21 | 7.136 | 133.223 | 31.162 | 28.693 | 29.285 | 601.83 | 26.753 | 27.712 | 1285.955 | 27.484 | 27.739 | 38.36 | 27.001 | 2.3 | 4.6 | 0.7 | 0.5 | 0.3
5103 | 30/07/2025 12:08:35.028 | 98.28 | 87 | 100 | 70 | 53 | 32.015 | 8.991 | 7.135 | 133.083 | 31.152 | 28.699 | 29.291 | 601.982 | 26.743 | 27.723 | 1289.695 | 27.504 | 27.737 | 38.362 | 27.001 | 2.3 | 4.6 | 0.7 | 0.5 | 0.3
5104 | 30/07/2025 12:08:36.663 | 98.376 | 88 | 100 | 71 | 51 | 32.822 | 8.986 | 7.134 | 133.302 | 31.19 | 28.686 | 29.272 | 601.987 | 26.754 | 27.708 | 1292.282 | 27.467 | 27.762 | 38.437 | 27.001 | 2.3 | 2.4 | 0.7 | 0.6 | 0.3
5105 | 30/07/2025 12:08:38.296 | 99.168 | 86 | 100 | 68 | 52 | 29.901 | 9.099 | 7.133 | 133.319 | 31.168 | 28.678 | 29.263 | 602.06 | 26.74 | 27.707 | 1277.494 | 27.496 | 27.758 | 38.441 | 21.001 | 1 | 2 | 0.7 | 0 | 0.2
5106 | 30/07/2025 12:08:39.933 | 98.808 | 84 | 100 | 70 | 52 | 29.644 | 9.135 | 7.137 | 132.898 | 31.176 | 28.698 | 29.286 | 601.868 | 26.741 | 27.709 | 1280.897 | 27.492 | 27.741 | 40.337 | 21.001 | 1 | 2.8 | 0.7 | 0 | 0.2
5107 | 30/07/2025 12:08:41.568 | 99.096 | 85 | 100 | 71 | 52 | 32.607 | 9.21 | 7.134 | 133.253 | 31.197 | 28.696 | 29.288 | 602.109 | 26.745 | 27.684 | 1270.022 | 27.484 | 27.721 | 39.321 | 26.001 | 3.6 | 4.5 | 0.4 | 0 | 0.2
5108 | 30/07/2025 12:08:43.204 | 98.976 | 86 | 100 | 71 | 53 | 32.195 | 9.129 | 7.122 | 133.312 | 31.186 | 28.699 | 29.286 | 602.003 | 26.742 | 27.688 | 1268.522 | 27.497 | 27.765 | 40.322 | 26.001 | 3.6 | 4.5 | 0.4 | 0 | 0.2
5109 | 30/07/2025 12:08:44.839 | 98.856 | 87 | 100 | 71 | 53 | 32.129 | 8.989 | 7.121 | 133.261 | 31.195 | 28.686 | 29.285 | 602.114 | 26.732 | 27.685 | 1258.061 | 27.459 | 27.766 | 40.414 | 26.001 | 3.6 | 4.8 | 0.4 | 0 | 0.2
5110 | 30/07/2025 12:08:46.474 | 98.736 | 84 | 100 | 70 | 52 | 32.775 | 9.134 | 7.07 | 133.025 | 31.182 | 28.677 | 29.285 | 601.896 | 26.741 | 27.719 | 1262.162 | 27.492 | 27.765 | 40.366 | 27.001 | 3.5 | 4.8 | 0.8 | 0 | 0.1
5111 | 30/07/2025 12:08:48.111 | 98.928 | 87 | 100 | 70 | 52 | 29.256 | 9.138 | 7.07 | 132.92 | 31.191 | 28.7 | 29.29 | 601.844 | 26.743 | 27.697 | 1260.756 | 27.491 | 27.728 | 40.327 | 27.001 | 3.5 | 3.9 | 0.8 | 0.5 | 0.1
5112 | 30/07/2025 12:08:49.794 | 99.168 | 86 | 100 | 70 | 52 | 30.154 | 9.141 | 7.071 | 133.291 | 31.18 | 28.702 | 29.293 | 602.114 | 26.729 | 27.694 | 1257.844 | 27.498 | 27.757 | 40.047 | 27.001 | 2.5 | 4.8 | 0 | 0 | 0.2
5113 | 30/07/2025 12:08:51.429 | 98.592 | 86 | 100 | 69 | 52 | 32.723 | 9.132 | 7.07 | 133.053 | 31.172 | 28.683 | 29.268 | 601.8 | 26.727 | 27.69 | 1261.961 | 27.474 | 27.753 | 40.256 | 27.001 | 2.5 | 5.2 | 0 | 0.8 | 0.2
5114 | 30/07/2025 12:08:53.063 | 98.592 | 88 | 100 | 70 | 53 | 29.221 | 9.034 | 7.067 | 133.353 | 31.162 | 28.675 | 29.265 | 601.929 | 26.728 | 27.682 | 1265.086 | 27.481 | 27.763 | 40.36 | 27.001 | 2.5 | 5.2 | 0 | 0.8 | 0.2
5115 | 30/07/2025 12:08:54.698 | 98.376 | 84 | 100 | 70 | 52 | 32.446 | 8.983 | 7.072 | 133.044 | 31.172 | 28.689 | 29.292 | 601.822 | 26.734 | 27.691 | 1272.071 | 27.506 | 27.752 | 40.321 | 26.001 | 2.1 | 3.8 | 0.6 | 0.5 | 0.1
5116 | 30/07/2025 12:08:56.342 | 98.52 | 87 | 100 | 71 | 52 | 32.507 | 9.287 | 7.092 | 133.138 | 31.178 | 28.698 | 29.305 | 602.167 | 26.728 | 27.667 | 1267.156 | 27.497 | 27.731 | 40.311 | 26.001 | 2.1 | 3.7 | 0.6 | 0.8 | 0.1
5117 | 30/07/2025 12:08:57.978 | 98.328 | 85 | 100 | 69 | 52 | 28.826 | 8.995 | 7.135 | 133.057 | 31.164 | 28.697 | 29.274 | 602.121 | 26.733 | 27.69 | 1260.589 | 27.493 | 27.746 | 40.155 | 23.001 | 2.7 | 3.3 | 0.7 | 1.2 | 0.1
5118 | 30/07/2025 12:08:59.613 | 97.848 | 84 | 100 | 70 | 52 | 30.711 | 8.915 | 7.12 | 133.161 | 31.178 | 28.681 | 29.249 | 601.878 | 26.755 | 27.707 | 1257.246 | 27.452 | 27.757 | 40.172 | 23.001 | 2.7 | 3.4 | 0.7 | 0.3 | 0.1
5119 | 30/07/2025 12:09:01.245 | 97.8 | 84 | 100 | 71 | 53 | 32.792 | 9.132 | 7.119 | 132.879 | 31.151 | 28.685 | 29.304 | 601.896 | 26.752 | 27.697 | 1259.805 | 27.503 | 27.769 | 40.292 | 23.001 | 2.7 | 3.4 | 0.7 | 0.3 | 0.1
5120 | 30/07/2025 12:09:02.883 | 98.304 | 86 | 99 | 70 | 52 | 29.664 | 9.126 | 7.123 | 133.128 | 31.165 | 28.693 | 29.29 | 601.887 | 26.756 | 27.69 | 1267.083 | 27.495 | 27.747 | 40.164 | 29.001 | 1.7 | 1.8 | 0 | 0.5 | 0.2
5121 | 30/07/2025 12:09:04.517 | 98.136 | 85 | 100 | 70 | 52 | 32.624 | 8.988 | 7.097 | 133.155 | 31.145 | 28.703 | 29.29 | 601.998 | 26.735 | 27.712 | 1255.154 | 27.509 | 27.732 | 40.2 | 29.001 | 1.7 | 4 | 0 | 1 | 0.2
5122 | 30/07/2025 12:09:06.150 | 98.016 | 85 | 100 | 70 | 53 | 32.308 | 8.911 | 7.088 | 133.211 | 31.165 | 28.687 | 29.277 | 601.933 | 26.752 | 27.722 | 1253.046 | 27.489 | 27.761 | 40.119 | 29.001 | 2.4 | 5.6 | 0.7 | 0.2 | 0.2
5123 | 30/07/2025 12:09:07.782 | 98.064 | 84 | 100 | 70 | 52 | 28.691 | 8.876 | 7.085 | 133.402 | 31.164 | 28.673 | 29.277 | 601.999 | 26.746 | 27.699 | 1254.441 | 27.467 | 27.757 | 40.412 | 29.001 | 2.4 | 3 | 0.7 | 0 | 0.2
5124 | 30/07/2025 12:09:09.415 | 98.376 | 86 | 100 | 70 | 50 | 31.468 | 9.204 | 7.095 | 132.865 | 31.177 | 28.704 | 29.299 | 601.949 | 26.741 | 27.715 | 1255.603 | 27.509 | 27.757 | 40.484 | 29.001 | 2 | 4 | 0.3 | 0 | 0.2
5125 | 30/07/2025 12:09:11.050 | 98.232 | 84 | 100 | 70 | 52 | 29.427 | 9.135 | 7.12 | 133.148 | 31.176 | 28.698 | 29.283 | 602.018 | 26.744 | 27.698 | 1250.519 | 27.497 | 27.743 | 40.598 | 29.001 | 2 | 4 | 0.3 | 0 | 0.2
5126 | 30/07/2025 12:09:12.683 | 98.856 | 86 | 100 | 71 | 52 | 30.329 | 9.136 | 7.12 | 133.152 | 31.185 | 28.689 | 29.29 | 603.012 | 26.748 | 27.719 | 1255.926 | 27.499 | 27.752 | 40.056 | 29.001 | 2 | 4.1 | 0.3 | 0 | 0.2
5127 | 30/07/2025 12:09:14.321 | 97.992 | 86 | 100 | 70 | 52 | 32.727 | 9.129 | 7.121 | 133.253 | 31.188 | 28.694 | 29.28 | 603.253 | 26.756 | 27.705 | 1267.38 | 27.474 | 27.769 | 40.275 | 33.001 | 3.6 | 4.3 | 1.2 | 1 | 0.2
5128 | 30/07/2025 12:09:15.955 | 98.376 | 86 | 100 | 70 | 52 | 31.738 | 9.135 | 7.085 | 133.173 | 31.182 | 28.672 | 29.287 | 603.311 | 26.746 | 27.704 | 1267.425 | 27.488 | 27.759 | 40.454 | 33.001 | 3.6 | 4.5 | 1.2 | 0.9 | 0.2
5129 | 30/07/2025 12:09:17.589 | 98.592 | 85 | 100 | 70 | 52 | 28.641 | 9.152 | 7.09 | 132.992 | 31.186 | 28.694 | 29.293 | 602.932 | 26.746 | 27.701 | 1271.829 | 27.494 | 27.75 | 40.301 | 24.001 | 2.3 | 1.9 | 0.6 | 0.1 | 0.2
5130 | 30/07/2025 12:09:19.220 | 98.256 | 84 | 100 | 71 | 52 | 31.763 | 9.133 | 7.087 | 133.187 | 31.189 | 28.696 | 29.294 | 603.239 | 26.731 | 27.684 | 1274.944 | 27.491 | 27.731 | 40.13 | 24.001 | 2.3 | 1.9 | 0.6 | 0.1 | 0.2
5131 | 30/07/2025 12:09:20.852 | 98.496 | 86 | 100 | 70 | 53 | 28.912 | 9.131 | 7.074 | 133.331 | 31.179 | 28.689 | 29.285 | 603.156 | 26.739 | 27.706 | 1269.289 | 27.492 | 27.74 | 39.96 | 24.001 | 2.3 | 3.3 | 0.6 | 0 | 0.2
5132 | 30/07/2025 12:09:22.484 | 98.424 | 86 | 100 | 70 | 52 | 30.671 | 9.131 | 7.069 | 133.169 | 31.173 | 28.686 | 29.273 | 602.287 | 26.735 | 27.674 | 1260.188 | 27.467 | 27.744 | 40.559 | 24.001 | 3 | 2.5 | 0.2 | 0.5 | 0.2
5133 | 30/07/2025 12:09:24.115 | 98.928 | 86 | 100 | 71 | 53 | 32.811 | 9.136 | 7.069 | 133.185 | 31.172 | 28.673 | 29.275 | 602.914 | 26.737 | 27.697 | 1257.965 | 27.486 | 27.75 | 40.366 | 24.001 | 3 | 4.1 | 0.2 | 0.6 | 0.2
5134 | 30/07/2025 12:09:25.751 | 99 | 84 | 100 | 71 | 53 | 31.085 | 9.132 | 7.062 | 133.21 | 31.194 | 28.699 | 29.297 | 603.067 | 26.74 | 27.682 | 1245.759 | 27.491 | 27.731 | 40.176 | 23.001 | 2.6 | 4.8 | 0 | 0 | 0.2
5135 | 30/07/2025 12:09:27.385 | 99 | 86 | 100 | 70 | 52 | 28.821 | 9.084 | 7.059 | 133.279 | 31.18 | 28.697 | 29.291 | 603.215 | 26.736 | 27.687 | 1236.747 | 27.5 | 27.749 | 39.997 | 23.001 | 2.6 | 2.6 | 0 | 0.5 | 0.2
5136 | 30/07/2025 12:09:29.021 | 99.168 | 86 | 100 | 70 | 52 | 32.15 | 9.132 | 7.059 | 133.188 | 31.159 | 28.692 | 29.247 | 603.022 | 26.74 | 27.682 | 1244.319 | 27.476 | 27.751 | 40.285 | 23.001 | 2.6 | 2.6 | 0 | 0.5 | 0.2
5137 | 30/07/2025 12:09:30.656 | 98.808 | 85 | 100 | 70 | 53 | 28.639 | 9.136 | 7.056 | 133.121 | 31.168 | 28.669 | 29.263 | 603.17 | 26.735 | 27.681 | 1248.762 | 27.463 | 27.751 | 40.24 | 28.001 | 1.8 | 4.7 | 1 | 0.5 | 0.3
5138 | 30/07/2025 12:09:32.290 | 98.28 | 85 | 100 | 70 | 52 | 31.152 | 8.988 | 7.061 | 132.957 | 31.174 | 28.679 | 29.276 | 603.072 | 26.733 | 27.686 | 1254.777 | 27.502 | 27.744 | 40.251 | 28.001 | 1.8 | 4.2 | 1 | 0.1 | 0.3
5139 | 30/07/2025 12:09:33.946 | 97.896 | 84 | 100 | 71 | 53 | 32.85 | 9.004 | 7.058 | 133.102 | 31.158 | 28.692 | 29.295 | 603.236 | 26.749 | 27.683 | 1247.819 | 27.499 | 27.739 | 40.273 | 25.001 | 3.9 | 2 | 0.6 | 0.8 | 0.2
5140 | 30/07/2025 12:09:35.581 | 97.464 | 85 | 100 | 71 | 53 | 30.435 | 9.133 | 7.069 | 133.102 | 31.164 | 28.702 | 29.265 | 603.126 | 26.751 | 27.717 | 1249.538 | 27.494 | 27.753 | 40.023 | 25.001 | 3.9 | 1.7 | 0.6 | 0.4 | 0.2
5141 | 30/07/2025 12:09:37.215 | 97.68 | 86 | 100 | 70 | 53 | 29.104 | 9.13 | 7.068 | 133.295 | 31.165 | 28.686 | 29.271 | 603.068 | 26.749 | 27.702 | 1249.121 | 27.451 | 27.758 | 40.257 | 25.001 | 3.9 | 1.7 | 0.6 | 0.4 | 0.2
5142 | 30/07/2025 12:09:38.850 | 97.584 | 84 | 100 | 70 | 52 | 31.647 | 9.134 | 7.069 | 133 | 31.154 | 28.671 | 29.258 | 603.091 | 26.75 | 27.716 | 1254.365 | 27.461 | 27.737 | 39.96 | 30.001 | 2.9 | 3.8 | 0.3 | 0 | 0.2
5143 | 30/07/2025 12:09:40.484 | 97.032 | 84 | 100 | 72 | 52 | 28.611 | 9.131 | 7.069 | 133.057 | 31.155 | 28.693 | 29.315 | 603.125 | 26.75 | 27.706 | 1242.895 | 27.497 | 27.753 | 38.364 | 30.001 | 2.9 | 3.5 | 0.3 | 1 | 0.2
5144 | 30/07/2025 12:09:42.118 | 97.008 | 84 | 100 | 71 | 52 | 35.209 | 9.153 | 7.071 | 133.158 | 31.16 | 28.694 | 29.283 | 603.167 | 26.743 | 27.704 | 1239.362 | 27.498 | 27.732 | 38.397 | 25.001 | 4.7 | 2.9 | 1 | 0.1 | 0.2
5145 | 30/07/2025 12:09:43.752 | 97.008 | 83 | 100 | 70 | 52 | 32.842 | 9.13 | 7.072 | 133.304 | 31.184 | 28.685 | 29.276 | 603.164 | 26.761 | 27.71 | 1230.694 | 27.48 | 27.753 | 39.972 | 25.001 | 4.7 | 1.7 | 1 | 0 | 0.2
5146 | 30/07/2025 12:09:45.385 | 96.864 | 82 | 100 | 70 | 52 | 29.92 | 8.991 | 7.069 | 133.12 | 31.175 | 28.673 | 29.284 | 602.141 | 26.741 | 27.696 | 1232.22 | 27.47 | 27.75 | 40.351 | 26.001 | 1.9 | 3 | 0 | 0 | 0.2
5147 | 30/07/2025 12:09:47.020 | 97.056 | 84 | 100 | 71 | 53 | 32.755 | 8.911 | 7.069 | 133.267 | 31.188 | 28.669 | 29.28 | 601.843 | 26.761 | 27.701 | 1240.293 | 27.479 | 27.75 | 40.234 | 26.001 | 1.9 | 3 | 0 | 0 | 0.2
5148 | 30/07/2025 12:09:48.655 | 96.72 | 83 | 100 | 70 | 52 | 31.103 | 8.988 | 7.07 | 132.953 | 31.19 | 28.698 | 29.288 | 601.923 | 26.741 | 27.693 | 1242.988 | 27.502 | 27.752 | 40.212 | 26.001 | 1.9 | 4.5 | 0 | 0.6 | 0.2
5149 | 30/07/2025 12:09:50.289 | 96.84 | 84 | 100 | 70 | 52 | 28.779 | 9.286 | 7.07 | 133.183 | 31.185 | 28.692 | 29.273 | 601.913 | 26.741 | 27.719 | 1250.696 | 27.49 | 27.732 | 38.151 | 26.001 | 2.2 | 7.6 | 1.2 | 0.3 | 0.2
5150 | 30/07/2025 12:09:51.924 | 97.008 | 83 | 100 | 71 | 52 | 32.235 | 8.988 | 7.07 | 133.161 | 31.183 | 28.691 | 29.267 | 601.977 | 26.748 | 27.694 | 1241.462 | 27.471 | 27.758 | 39.846 | 26.001 | 2.2 | 4.9 | 1.2 | 0.5 | 0.2
5151 | 30/07/2025 12:09:53.561 | 96.624 | 84 | 100 | 70 | 52 | 32.845 | 9.268 | 7.084 | 133.219 | 31.187 | 28.677 | 29.284 | 602.07 | 26.735 | 27.7 | 1247.328 | 27.471 | 27.751 | 38.58 | 33.001 | 2.3 | 3.1 | 1.3 | 1.1 | 0.2
5152 | 30/07/2025 12:09:55.194 | 96.384 | 82 | 100 | 70 | 51 | 29.471 | 9.136 | 7.09 | 132.975 | 31.178 | 28.697 | 29.306 | 601.69 | 26.745 | 27.702 | 1249.214 | 27.498 | 27.746 | 40.029 | 33.001 | 2.3 | 3.1 | 1.3 | 1.1 | 0.2
5153 | 30/07/2025 12:09:56.828 | 96.384 | 83 | 100 | 70 | 52 | 32.924 | 9.157 | 7.129 | 132.887 | 31.18 | 28.704 | 29.29 | 601.824 | 26.73 | 27.69 | 1254.616 | 27.514 | 27.749 | 38.627 | 33.001 | 2.3 | 2.8 | 1.3 | 0.2 | 0.2
5154 | 30/07/2025 12:09:58.462 | 96.336 | 82 | 100 | 71 | 52 | 30.568 | 9.127 | 7.135 | 133.104 | 31.18 | 28.69 | 29.285 | 602.095 | 26.745 | 27.693 | 1266.679 | 27.486 | 27.725 | 40.27 | 25.001 | 3 | 2.3 | 1.7 | 0 | 0.1
5155 | 30/07/2025 12:10:00.100 | 96.216 | 82 | 100 | 70 | 52 | 29.236 | 9.427 | 7.132 | 133.258 | 31.176 | 28.687 | 29.264 | 601.963 | 26.715 | 27.678 | 1276.854 | 27.471 | 27.762 | 40.401 | 25.001 | 3 | 5.3 | 1.7 | 0 | 0.1
5156 | 30/07/2025 12:10:01.734 | 97.056 | 84 | 100 | 70 | 52 | 32.551 | 9.39 | 7.133 | 132.949 | 31.174 | 28.674 | 29.288 | 600.444 | 26.731 | 27.685 | 1276.939 | 27.483 | 27.752 | 40.306 | 29.001 | 2 | 4.4 | 0.6 | 0 | 0.2
5157 | 30/07/2025 12:10:03.372 | 96.984 | 84 | 100 | 69 | 52 | 32.596 | 9.185 | 7.134 | 133.098 | 31.177 | 28.693 | 29.294 | 601.839 | 26.74 | 27.681 | 1287.991 | 27.496 | 27.744 | 40.195 | 29.001 | 2 | 3.9 | 0.6 | 0 | 0.2
5158 | 30/07/2025 12:10:05.006 | 97.128 | 85 | 100 | 70 | 52 | 31.815 | 9.138 | 7.136 | 132.726 | 31.171 | 28.696 | 29.29 | 601.724 | 26.739 | 27.676 | 1291.607 | 27.481 | 27.731 | 40.154 | 29.001 | 2 | 3.9 | 0.6 | 0 | 0.2
5159 | 30/07/2025 12:10:06.642 | 97.2 | 84 | 100 | 72 | 52 | 32.943 | 9.131 | 7.134 | 133.243 | 31.181 | 28.685 | 29.298 | 602.093 | 26.749 | 27.681 | 1277.568 | 27.491 | 27.746 | 40.126 | 27.001 | 2.6 | 3.4 | 0.7 | 0 | 0.2
5160 | 30/07/2025 12:10:08.275 | 97.128 | 84 | 100 | 70 | 52 | 29.926 | 8.989 | 7.133 | 133.204 | 31.157 | 28.69 | 29.269 | 601.906 | 26.75 | 27.705 | 1272.925 | 27.48 | 27.76 | 40.348 | 27.001 | 2.6 | 3.2 | 0.7 | 0.5 | 0.2
5161 | 30/07/2025 12:10:09.910 | 97.104 | 84 | 100 | 70 | 52 | 29.501 | 9.13 | 7.136 | 133.057 | 31.158 | 28.676 | 29.289 | 600.455 | 26.753 | 27.7 | 1271.937 | 27.495 | 27.741 | 40.267 | 27.001 | 1.5 | 3.6 | 1.2 | 0.8 | 0.2
5162 | 30/07/2025 12:10:11.544 | 97.2 | 84 | 100 | 70 | 52 | 32.613 | 9.35 | 7.135 | 132.946 | 31.164 | 28.692 | 29.278 | 600.491 | 26.746 | 27.712 | 1268.294 | 27.503 | 27.745 | 40.253 | 27.001 | 1.5 | 3.3 | 1.2 | 0.6 | 0.2
5163 | 30/07/2025 12:10:13.178 | 96.984 | 83 | 100 | 71 | 52 | 32.243 | 9.285 | 7.134 | 133.383 | 31.152 | 28.692 | 29.283 | 601.926 | 26.744 | 27.723 | 1265.128 | 27.481 | 27.748 | 40.017 | 27.001 | 1.5 | 3.3 | 1.2 | 0.6 | 0.2
5164 | 30/07/2025 12:10:14.810 | 97.008 | 82 | 100 | 70 | 53 | 32.247 | 9.29 | 7.133 | 133.205 | 31.15 | 28.69 | 29.278 | 601.855 | 26.738 | 27.692 | 1267.396 | 27.507 | 27.757 | 40.084 | 30.001 | 1.6 | 2.9 | 1.2 | 0 | 0.2
5165 | 30/07/2025 12:10:16.444 | 97.224 | 82 | 100 | 70 | 52 | 32.793 | 9.142 | 7.134 | 133.167 | 31.161 | 28.675 | 29.272 | 601.881 | 26.751 | 27.709 | 1257.9 | 27.469 | 27.751 | 40.348 | 30.001 | 1.6 | 3 | 1.2 | 0 | 0.2
5166 | 30/07/2025 12:10:18.080 | 97.008 | 83 | 100 | 71 | 54 | 29.228 | 9.288 | 7.087 | 133.071 | 31.171 | 28.692 | 29.303 | 601.97 | 26.758 | 27.693 | 1257.16 | 27.499 | 27.756 | 38.295 | 27.001 | 2.5 | 4.6 | 0.9 | 0.5 | 0.2
5167 | 30/07/2025 12:10:19.717 | 96.888 | 83 | 100 | 71 | 52 | 30.244 | 8.992 | 7.085 | 133.053 | 31.185 | 28.7 | 29.284 | 601.946 | 26.742 | 27.704 | 1257.1 | 27.502 | 27.727 | 38.299 | 27.001 | 2.5 | 3.8 | 0.9 | 0.6 | 0.2
5168 | 30/07/2025 12:10:21.350 | 97.44 | 84 | 100 | 70 | 52 | 32.669 | 9.103 | 7.073 | 133.321 | 31.176 | 28.689 | 29.266 | 601.924 | 26.76 | 27.707 | 1257.433 | 27.484 | 27.749 | 39.946 | 27.001 | 2.5 | 3.8 | 0.9 | 0.6 | 0.2
5169 | 30/07/2025 12:10:22.985 | 97.32 | 83 | 100 | 70 | 52 | 29.152 | 9.133 | 7.069 | 133.07 | 31.176 | 28.694 | 29.269 | 601.884 | 26.74 | 27.706 | 1255.34 | 27.473 | 27.748 | 40.217 | 24.001 | 1.8 | 4.9 | 0.6 | 0.6 | 0.2
5170 | 30/07/2025 12:10:24.621 | 96.936 | 82 | 100 | 71 | 52 | 32.46 | 9.291 | 7.068 | 133.234 | 31.194 | 28.664 | 29.287 | 601.949 | 26.749 | 27.707 | 1257.21 | 27.474 | 27.75 | 40.234 | 24.001 | 1.8 | 4.3 | 0.6 | 0 | 0.2
5171 | 30/07/2025 12:10:26.273 | 97.248 | 83 | 100 | 70 | 52 | 32.646 | 9.288 | 7.076 | 133.022 | 31.176 | 28.695 | 29.281 | 601.977 | 26.74 | 27.695 | 1250.266 | 27.502 | 27.761 | 40.233 | 26.001 | 2.6 | 4.3 | 0.2 | 0 | 0.2
5172 | 30/07/2025 12:10:27.907 | 96.864 | 83 | 100 | 70 | 52 | 28.922 | 9.435 | 7.087 | 133.241 | 31.177 | 28.697 | 29.29 | 601.98 | 26.74 | 27.7 | 1237.731 | 27.482 | 27.713 | 38.367 | 26.001 | 2.6 | 4.3 | 0.2 | 1.3 | 0.2
5173 | 30/07/2025 12:10:29.542 | 96.84 | 84 | 100 | 70 | 52 | 30.789 | 9.286 | 7.121 | 133.428 | 31.182 | 28.692 | 29.278 | 603.205 | 26.738 | 27.682 | 1237.365 | 27.479 | 27.749 | 38.169 | 24.001 | 3.5 | 3.1 | 0.6 | 0.6 | 0.2
5174 | 30/07/2025 12:10:31.177 | 96.432 | 82 | 100 | 70 | 52 | 32.804 | 9.285 | 7.121 | 133.128 | 31.175 | 28.675 | 29.264 | 603.187 | 26.73 | 27.684 | 1237.513 | 27.476 | 27.752 | 40.267 | 24.001 | 3.5 | 3.1 | 0.6 | 0.6 | 0.2
5175 | 30/07/2025 12:10:32.811 | 96.048 | 82 | 100 | 70 | 52 | 29.674 | 9.433 | 7.121 | 132.995 | 31.18 | 28.675 | 29.305 | 603.281 | 26.719 | 27.681 | 1237.092 | 27.487 | 27.745 | 40.258 | 24.001 | 3.5 | 4.5 | 0.6 | 0.5 | 0.2
5176 | 30/07/2025 12:10:34.446 | 95.592 | 82 | 100 | 70 | 52 | 32.643 | 9.204 | 7.126 | 132.849 | 31.186 | 28.71 | 29.291 | 601.852 | 26.721 | 27.691 | 1227.963 | 27.5 | 27.745 | 40.454 | 23.001 | 1.8 | 4.1 | 0.1 | 0.1 | 0.3
5177 | 30/07/2025 12:10:36.080 | 95.616 | 83 | 100 | 70 | 51 | 32.201 | 9.128 | 7.134 | 133.503 | 31.184 | 28.689 | 29.288 | 601.97 | 26.737 | 27.679 | 1223.493 | 27.481 | 27.731 | 40.005 | 23.001 | 1.8 | 2.6 | 0.1 | 0 | 0.3
5178 | 30/07/2025 12:10:37.714 | 95.496 | 82 | 100 | 71 | 53 | 28.723 | 8.984 | 7.133 | 133.287 | 31.166 | 28.694 | 29.268 | 602.02 | 26.737 | 27.673 | 1225.94 | 27.492 | 27.775 | 40.294 | 28.001 | 1.9 | 3 | 0.1 | 0 | 0.2
5179 | 30/07/2025 12:10:39.349 | 95.448 | 82 | 100 | 70 | 52 | 31.226 | 9.287 | 7.135 | 133.253 | 31.173 | 28.68 | 29.283 | 601.751 | 26.739 | 27.682 | 1237.163 | 27.468 | 27.743 | 40.284 | 28.001 | 1.9 | 3 | 0.1 | 0 | 0.2
5180 | 30/07/2025 12:10:40.984 | 95.304 | 82 | 100 | 70 | 52 | 29.412 | 9.255 | 7.151 | 133.086 | 31.159 | 28.688 | 29.294 | 601.933 | 26.742 | 27.691 | 1237.751 | 27.516 | 27.749 | 40.245 | 28.001 | 1.9 | 2.7 | 0.1 | 0 | 0.2
5181 | 30/07/2025 12:10:42.618 | 95.28 | 82 | 100 | 70 | 51 | 30.077 | 9.175 | 7.153 | 132.824 | 31.176 | 28.692 | 29.282 | 603.038 | 26.756 | 27.689 | 1237.25 | 27.495 | 27.735 | 40.368 | 26.001 | 2.3 | 4.2 | 1.6 | 1.2 | 0.2
5182 | 30/07/2025 12:10:44.251 | 95.448 | 84 | 100 | 70 | 52 | 32.749 | 9.154 | 7.151 | 133.471 | 31.157 | 28.694 | 29.3 | 603.429 | 26.738 | 27.696 | 1247.339 | 27.49 | 27.755 | 38.201 | 26.001 | 2.3 | 3.3 | 1.6 | 0.6 | 0.2
5183 | 30/07/2025 12:10:45.885 | 95.28 | 82 | 99 | 70 | 52 | 31.765 | 9.286 | 7.15 | 133.031 | 31.139 | 28.684 | 29.271 | 603.165 | 26.753 | 27.719 | 1253.093 | 27.479 | 27.759 | 40.525 | 26.001 | 3 | 6.3 | 0.7 | 0.6 | 0.2
5184 | 30/07/2025 12:10:47.521 | 95.256 | 82 | 100 | 71 | 52 | 28.61 | 9.137 | 7.126 | 131.79 | 31.166 | 28.677 | 29.283 | 603.194 | 26.754 | 27.715 | 1254.633 | 27.493 | 27.743 | 40.301 | 26.001 | 3 | 5.6 | 0.7 | 0 | 0.2
5185 | 30/07/2025 12:10:49.155 | 95.28 | 83 | 100 | 70 | 52 | 31.795 | 8.995 | 7.122 | 131.68 | 31.155 | 28.705 | 29.291 | 602.006 | 26.743 | 27.704 | 1256.97 | 27.51 | 27.748 | 40.047 | 26.001 | 3 | 5.6 | 0.7 | 0 | 0.2
5186 | 30/07/2025 12:10:50.790 | 95.952 | 83 | 100 | 71 | 53 | 28.947 | 9.106 | 7.081 | 131.748 | 31.162 | 28.698 | 29.28 | 601.993 | 26.74 | 27.69 | 1253.902 | 27.49 | 27.731 | 39.984 | 28.001 | 1.9 | 1.9 | 0.6 | 0.5 | 0.2
5187 | 30/07/2025 12:10:52.426 | 96.6 | 83 | 100 | 72 | 52 | 30.747 | 9.215 | 7.068 | 131.801 | 31.158 | 28.694 | 29.281 | 601.959 | 26.75 | 27.703 | 1247.51 | 27.496 | 27.764 | 38.222 | 28.001 | 1.9 | 3.3 | 0.6 | 0.1 | 0.2
5188 | 30/07/2025 12:10:54.061 | 96.888 | 84 | 100 | 70 | 52 | 32.755 | 9.127 | 7.069 | 131.693 | 31.18 | 28.677 | 29.269 | 601.864 | 26.748 | 27.706 | 1251.626 | 27.46 | 27.753 | 38.445 | 25.001 | 2.8 | 5 | 0.2 | 0.5 | 0.2
5189 | 30/07/2025 12:10:55.698 | 97.032 | 84 | 100 | 72 | 52 | 31.125 | 9.134 | 7.07 | 131.587 | 31.188 | 28.697 | 29.31 | 601.944 | 26.731 | 27.687 | 1257.701 | 27.494 | 27.75 | 38.558 | 25.001 | 2.8 | 2.5 | 0.2 | 0.5 | 0.2
5190 | 30/07/2025 12:10:57.338 | 97.32 | 86 | 100 | 71 | 52 | 28.779 | 9.144 | 7.072 | 129.998 | 31.195 | 28.698 | 29.277 | 602.107 | 26.741 | 27.705 | 1267.409 | 27.494 | 27.726 | 40.406 | 25.001 | 2.8 | 2.5 | 0.2 | 0.5 | 0.2
5191 | 30/07/2025 12:10:58.972 | 98.04 | 86 | 100 | 70 | 52 | 32.303 | 9.277 | 7.09 | 130.487 | 31.191 | 28.696 | 29.296 | 603.154 | 26.743 | 27.689 | 1272.197 | 27.493 | 27.735 | 40.026 | 23.001 | 4.1 | 2.3 | 0 | 0.5 | 0.2
5192 | 30/07/2025 12:11:00.608 | 98.208 | 87 | 100 | 70 | 52 | 28.629 | 9.133 | 7.121 | 130.237 | 31.184 | 28.69 | 29.275 | 601.915 | 26.734 | 27.718 | 1273.335 | 27.481 | 27.755 | 40.175 | 23.001 | 4.1 | 2.1 | 0 | 0.2 | 0.2
5193 | 30/07/2025 12:11:02.240 | 98.112 | 84 | 100 | 70 | 52 | 31.324 | 9.027 | 7.132 | 130.286 | 31.191 | 28.674 | 29.286 | 603.138 | 26.739 | 27.692 | 1264.592 | 27.474 | 27.753 | 38.469 | 28.001 | 3.6 | 4.2 | 0 | 0 | 0.2
5194 | 30/07/2025 12:11:03.874 | 98.28 | 87 | 100 | 71 | 54 | 32.862 | 9.288 | 7.134 | 130.283 | 31.18 | 28.691 | 29.282 | 602.004 | 26.723 | 27.693 | 1276.903 | 27.509 | 27.751 | 38.473 | 28.001 | 3.6 | 4.4 | 0 | 0 | 0.2
5195 | 30/07/2025 12:11:05.508 | 98.304 | 86 | 100 | 71 | 51 | 30.618 | 8.996 | 7.135 | 130.293 | 31.179 | 28.691 | 29.283 | 603.154 | 26.726 | 27.702 | 1274.581 | 27.488 | 27.731 | 38.169 | 27.001 | 2.2 | 6 | 0.9 | 0.6 | 0.1
5196 | 30/07/2025 12:11:07.141 | 99.072 | 87 | 99 | 70 | 52 | 32.731 | 9.022 | 7.135 | 130.282 | 31.177 | 28.696 | 29.271 | 602.081 | 26.721 | 27.693 | 1277.164 | 27.502 | 27.75 | 38.159 | 27.001 | 2.2 | 6 | 0.9 | 0.6 | 0.1
5197 | 30/07/2025 12:11:08.777 | 99.288 | 86 | 100 | 70 | 53 | 31.761 | 8.986 | 7.152 | 130.23 | 31.179 | 28.68 | 29.26 | 601.947 | 26.742 | 27.68 | 1280.687 | 27.464 | 27.757 | 38.299 | 27.001 | 2.2 | 3.3 | 0.9 | 0.3 | 0.1
5198 | 30/07/2025 12:11:10.413 | 99.312 | 88 | 100 | 70 | 54 | 28.746 | 9.133 | 7.151 | 130.21 | 31.174 | 28.675 | 29.307 | 602.031 | 26.725 | 27.664 | 1277.391 | 27.487 | 27.755 | 38.555 | 32.001 | 3.9 | 3.6 | 1 | 1.6 | 0.1
5199 | 30/07/2025 12:11:12.047 | 99.552 | 87 | 100 | 70 | 52 | 31.866 | 9.137 | 7.152 | 129.97 | 31.178 | 28.709 | 29.285 | 601.878 | 26.727 | 27.686 | 1279.403 | 27.505 | 27.758 | 39.297 | 32.001 | 3.9 | 3.1 | 1 | 0.7 | 0.1
5200 | 30/07/2025 12:11:13.681 | 99.72 | 86 | 100 | 70 | 52 | 32.872 | 9.228 | 7.151 | 130.502 | 31.188 | 28.693 | 29.288 | 602.069 | 26.745 | 27.669 | 1272.629 | 27.492 | 27.73 | 38.213 | 28.001 | 1.9 | 4.7 | 0.6 | 0.5 | 0.2
5201 | 30/07/2025 12:11:15.323 | 100.008 | 87 | 100 | 71 | 53 | 30.035 | 9.135 | 7.151 | 130.211 | 31.16 | 28.69 | 29.285 | 602.095 | 26.741 | 27.698 | 1267.47 | 27.493 | 27.758 | 40.198 | 28.001 | 1.9 | 4.7 | 0.6 | 0.5 | 0.2
5202 | 30/07/2025 12:11:16.960 | 99.72 | 89 | 100 | 70 | 51 | 32.836 | 9.133 | 7.15 | 130.404 | 31.182 | 28.681 | 29.272 | 602.077 | 26.743 | 27.698 | 1269.186 | 27.464 | 27.75 | 38.984 | 28.001 | 1.9 | 4.6 | 0.6 | 0 | 0.2
5203 | 30/07/2025 12:11:18.595 | 99.216 | 87 | 100 | 71 | 53 | 31.217 | 9.141 | 7.153 | 131.629 | 31.145 | 28.679 | 29.298 | 601.815 | 26.754 | 27.698 | 1269.426 | 27.514 | 27.756 | 38.545 | 29.001 | 2.3 | 3.1 | 0.4 | 0 | 0.1
5204 | 30/07/2025 12:11:20.231 | 98.664 | 86 | 100 | 71 | 52 | 28.824 | 9.131 | 7.155 | 131.643 | 31.148 | 28.69 | 29.281 | 601.714 | 26.751 | 27.697 | 1274.493 | 27.495 | 27.725 | 38.349 | 29.001 | 2.3 | 3.5 | 0.4 | 0.5 | 0.1
5205 | 30/07/2025 12:11:21.865 | 98.232 | 86 | 100 | 70 | 51 | 32.23 | 9.131 | 7.186 | 131.969 | 31.152 | 28.693 | 29.283 | 602.17 | 26.733 | 27.696 | 1282.344 | 27.488 | 27.75 | 38.111 | 27.001 | 2.7 | 3.3 | 0.1 | 0.5 | 0.1
5206 | 30/07/2025 12:11:23.499 | 97.8 | 86 | 100 | 70 | 52 | 32.827 | 9.286 | 7.185 | 131.398 | 31.166 | 28.682 | 29.261 | 603.093 | 26.742 | 27.711 | 1283.905 | 27.465 | 27.749 | 38.438 | 27.001 | 2.7 | 3.5 | 0.1 | 0 | 0.1
5207 | 30/07/2025 12:11:25.135 | 97.848 | 85 | 100 | 70 | 52 | 31.273 | 9.28 | 7.184 | 131.661 | 31.16 | 28.676 | 29.266 | 603.28 | 26.744 | 27.7 | 1280.766 | 27.48 | 27.764 | 38.524 | 27.001 | 2.7 | 3.5 | 0.1 | 0 | 0.1
5208 | 30/07/2025 12:11:26.772 | 97.584 | 85 | 100 | 71 | 51 | 32.853 | 8.988 | 7.189 | 131.677 | 31.186 | 28.69 | 29.288 | 603.041 | 26.743 | 27.718 | 1267.097 | 27.496 | 27.743 | 38.492 | 32.001 | 2.5 | 4 | 0.9 | 0.5 | 0.1
5209 | 30/07/2025 12:11:28.408 | 97.536 | 86 | 100 | 70 | 52 | 30.477 | 9.117 | 7.168 | 133.062 | 31.178 | 28.695 | 29.291 | 603.184 | 26.744 | 27.695 | 1267.215 | 27.482 | 27.735 | 38.388 | 32.001 | 2.5 | 2 | 0.9 | 0.9 | 0.1
5210 | 30/07/2025 12:11:30.042 | 97.944 | 84 | 100 | 71 | 52 | 29.047 | 9.133 | 7.151 | 132.874 | 31.188 | 28.695 | 29.271 | 603.323 | 26.74 | 27.706 | 1261.832 | 27.502 | 27.754 | 38.367 | 30.001 | 3.8 | 5.6 | 1.5 | 1 | 0.2
5211 | 30/07/2025 12:11:31.678 | 97.608 | 85 | 100 | 71 | 52 | 32.416 | 8.989 | 7.151 | 133.194 | 31.174 | 28.678 | 29.264 | 603.06 | 26.746 | 27.701 | 1257.555 | 27.464 | 27.745 | 39.804 | 30.001 | 3.8 | 3.3 | 1.5 | 0.5 | 0.2
5212 | 30/07/2025 12:11:33.312 | 97.008 | 83 | 100 | 70 | 54 | 32.605 | 9.189 | 7.152 | 133.087 | 31.19 | 28.683 | 29.282 | 603.253 | 26.734 | 27.695 | 1257.588 | 27.495 | 27.751 | 40.239 | 30.001 | 3.8 | 3.3 | 1.5 | 0.5 | 0.2
5213 | 30/07/2025 12:11:34.948 | 97.464 | 84 | 100 | 70 | 52 | 31.754 | 9.291 | 7.187 | 133.14 | 31.187 | 28.691 | 29.29 | 603.001 | 26.765 | 27.708 | 1257.165 | 27.495 | 27.749 | 40.116 | 27.001 | 2.5 | 4.7 | 0.1 | 0.8 | 0.1
5214 | 30/07/2025 12:11:36.584 | 97.488 | 84 | 100 | 70 | 53 | 32.867 | 9.132 | 7.17 | 133.068 | 31.185 | 28.696 | 29.299 | 603.352 | 26.731 | 27.688 | 1255.296 | 27.49 | 27.756 | 39.992 | 27.001 | 2.5 | 3.9 | 0.1 | 0.6 | 0.1
5215 | 30/07/2025 12:11:38.219 | 97.272 | 84 | 100 | 70 | 52 | 29.837 | 9.267 | 7.152 | 133.158 | 31.184 | 28.691 | 29.267 | 603.185 | 26.727 | 27.694 | 1248.359 | 27.474 | 27.743 | 40.277 | 29.001 | 2.7 | 3.4 | 0.3 | 0.6 | 0.1
5216 | 30/07/2025 12:11:39.857 | 97.512 | 84 | 100 | 70 | 51 | 29.724 | 9.128 | 7.132 | 133.228 | 31.188 | 28.668 | 29.276 | 603.168 | 26.734 | 27.673 | 1252.545 | 27.462 | 27.743 | 40.297 | 29.001 | 2.7 | 3 | 0.3 | 0 | 0.1
5217 | 30/07/2025 12:11:41.492 | 97.752 | 85 | 100 | 69 | 53 | 32.667 | 9.134 | 7.134 | 133.019 | 31.167 | 28.7 | 29.286 | 603.32 | 26.742 | 27.691 | 1248.427 | 27.509 | 27.75 | 40.324 | 29.001 | 1.9 | 4.8 | 0.6 | 0 | 0.2
5218 | 30/07/2025 12:11:43.127 | 98.136 | 84 | 100 | 70 | 53 | 28.894 | 9.13 | 7.133 | 133.017 | 31.178 | 28.696 | 29.286 | 603.152 | 26.737 | 27.678 | 1247.485 | 27.496 | 27.735 | 40.299 | 29.001 | 1.9 | 4.8 | 0.6 | 0 | 0.2
5219 | 30/07/2025 12:11:44.763 | 97.92 | 84 | 100 | 70 | 52 | 32.262 | 9.014 | 7.126 | 133.226 | 31.177 | 28.705 | 29.284 | 603.448 | 26.722 | 27.677 | 1247.297 | 27.502 | 27.742 | 40.083 | 29.001 | 1.9 | 2.2 | 0.6 | 0 | 0.2
5220 | 30/07/2025 12:11:46.399 | 97.824 | 85 | 100 | 70 | 53 | 32.827 | 9.287 | 7.121 | 133.215 | 31.176 | 28.685 | 29.254 | 603.122 | 26.748 | 27.678 | 1244.419 | 27.466 | 27.746 | 40.185 | 28.001 | 3 | 3.3 | 0.1 | 0 | 0.1
5221 | 30/07/2025 12:11:48.036 | 97.92 | 85 | 100 | 70 | 52 | 29.52 | 9.211 | 7.132 | 133.129 | 31.17 | 28.681 | 29.293 | 603.32 | 26.739 | 27.678 | 1248.372 | 27.492 | 27.766 | 40.262 | 28.001 | 3 | 4 | 0.1 | 0 | 0.1
5222 | 30/07/2025 12:11:49.671 | 97.656 | 85 | 100 | 70 | 52 | 30.094 | 9.267 | 7.136 | 132.771 | 31.158 | 28.694 | 29.289 | 603.107 | 26.748 | 27.706 | 1255.28 | 27.499 | 27.756 | 40.346 | 24.001 | 3.7 | 4.4 | 1.2 | 0.5 | 0.2
5223 | 30/07/2025 12:11:51.305 | 96.984 | 83 | 100 | 70 | 52 | 32.718 | 9.254 | 7.135 | 133.312 | 31.175 | 28.694 | 29.285 | 603.141 | 26.744 | 27.697 | 1257.276 | 27.488 | 27.74 | 39.93 | 24.001 | 3.7 | 4.4 | 1.2 | 0.5 | 0.2
5224 | 30/07/2025 12:11:52.943 | 96.84 | 85 | 100 | 70 | 52 | 29.127 | 9.432 | 7.136 | 133.04 | 31.161 | 28.69 | 29.282 | 603.178 | 26.756 | 27.715 | 1254.728 | 27.484 | 27.749 | 40.066 | 24.001 | 3.7 | 3.5 | 1.2 | 0 | 0.2
5225 | 30/07/2025 12:11:54.579 | 96.504 | 84 | 100 | 71 | 53 | 32.511 | 9.189 | 7.133 | 133.236 | 31.151 | 28.684 | 29.282 | 603.225 | 26.738 | 27.691 | 1249.952 | 27.463 | 27.756 | 40.455 | 35.001 | 3.7 | 2.7 | 0.6 | 0.5 | 0.3
5226 | 30/07/2025 12:11:56.213 | 96.84 | 84 | 100 | 71 | 52 | 32.686 | 9.179 | 7.149 | 133.077 | 31.15 | 28.69 | 29.305 | 603.159 | 26.735 | 27.713 | 1266.538 | 27.501 | 27.761 | 38.418 | 35.001 | 3.7 | 2.8 | 0.6 | 0.5 | 0.3
5227 | 30/07/2025 12:11:57.850 | 96.552 | 85 | 100 | 70 | 52 | 29.023 | 9.139 | 7.146 | 132.998 | 31.165 | 28.694 | 29.292 | 602.997 | 26.756 | 27.707 | 1264.449 | 27.489 | 27.723 | 38.337 | 28.001 | 3.1 | 4.5 | 0.9 | 0.2 | 0.2
5228 | 30/07/2025 12:11:59.484 | 96.72 | 85 | 100 | 70 | 52 | 30.752 | 9.094 | 7.135 | 133.373 | 31.161 | 28.694 | 29.277 | 603.304 | 26.743 | 27.699 | 1258.008 | 27.493 | 27.759 | 38.164 | 28.001 | 3.1 | 3.7 | 0.9 | 0.5 | 0.2
5229 | 30/07/2025 12:12:01.119 | 96.84 | 84 | 100 | 69 | 52 | 29.882 | 9.021 | 7.135 | 133.436 | 31.182 | 28.688 | 29.261 | 603.07 | 26.753 | 27.705 | 1247.83 | 27.482 | 27.763 | 38.324 | 28.001 | 3.1 | 3.7 | 0.9 | 0.5 | 0.2
5230 | 30/07/2025 12:12:02.754 | 96.648 | 83 | 100 | 70 | 52 | 29.547 | 9.202 | 7.131 | 133.183 | 31.177 | 28.679 | 29.268 | 603.374 | 26.745 | 27.705 | 1247.318 | 27.489 | 27.761 | 40.492 | 28.001 | 1.7 | 5.4 | 0.2 | 0.8 | 0.1
5231 | 30/07/2025 12:12:04.388 | 96.648 | 84 | 100 | 71 | 53 | 32.63 | 8.989 | 7.136 | 133.037 | 31.184 | 28.684 | 29.294 | 602.998 | 26.74 | 27.705 | 1259.958 | 27.497 | 27.735 | 40.237 | 28.001 | 1.7 | 3.2 | 0.2 | 0.6 | 0.1
5232 | 30/07/2025 12:12:06.022 | 96.24 | 84 | 100 | 71 | 52 | 32.222 | 9.202 | 7.124 | 133.08 | 31.184 | 28.694 | 29.287 | 603.178 | 26.74 | 27.689 | 1260.519 | 27.488 | 27.741 | 40.084 | 23.001 | 2.3 | 2.8 | 1 | 0 | 0.2
5233 | 30/07/2025 12:12:07.656 | 96.312 | 84 | 100 | 71 | 52 | 28.725 | 9.433 | 7.086 | 133.189 | 31.169 | 28.697 | 29.272 | 603.256 | 26.736 | 27.698 | 1262.643 | 27.496 | 27.759 | 40.158 | 23.001 | 2.3 | 3.6 | 1 | 0.8 | 0.2
5234 | 30/07/2025 12:12:09.292 | 96.672 | 84 | 100 | 70 | 52 | 31.242 | 9.431 | 7.087 | 133.204 | 31.187 | 28.681 | 29.271 | 603.172 | 26.752 | 27.694 | 1257.345 | 27.455 | 27.745 | 40.335 | 23.001 | 2.3 | 3.6 | 1 | 0.8 | 0.2
5235 | 30/07/2025 12:12:10.927 | 96.144 | 82 | 100 | 70 | 52 | 29.353 | 9.285 | 7.086 | 133.142 | 31.182 | 28.666 | 29.284 | 603.114 | 26.722 | 27.706 | 1257.491 | 27.469 | 27.763 | 40.353 | 24.001 | 3 | 3.2 | 0.6 | 1.7 | 0.2
5236 | 30/07/2025 12:12:12.561 | 96.072 | 84 | 100 | 71 | 52 | 30.164 | 9.155 | 7.089 | 133.077 | 31.191 | 28.692 | 29.292 | 601.811 | 26.743 | 27.682 | 1257.37 | 27.488 | 27.742 | 40.262 | 24.001 | 3 | 3.8 | 0.6 | 0.8 | 0.2
5237 | 30/07/2025 12:12:14.196 | 96.912 | 84 | 100 | 70 | 52 | 32.729 | 9.202 | 7.087 | 133.223 | 31.169 | 28.7 | 29.3 | 602.104 | 26.733 | 27.667 | 1256.526 | 27.502 | 27.739 | 40.185 | 21.001 | 1.5 | 3.4 | 0.6 | 0 | 0.2
5238 | 30/07/2025 12:12:15.830 | 96.432 | 84 | 100 | 70 | 53 | 31.769 | 9.238 | 7.089 | 133.216 | 31.173 | 28.686 | 29.275 | 601.918 | 26.734 | 27.701 | 1257.15 | 27.478 | 27.754 | 40.266 | 21.001 | 1.5 | 5.3 | 0.6 | 0 | 0.2
5239 | 30/07/2025 12:12:17.465 | 96.648 | 84 | 100 | 70 | 52 | 28.638 | 9.201 | 7.11 | 133.295 | 31.187 | 28.671 | 29.284 | 601.895 | 26.722 | 27.682 | 1256.997 | 27.468 | 27.757 | 40.302 | 22.001 | 2.9 | 5.2 | 1.2 | 0.8 | 0.2
5240 | 30/07/2025 12:12:19.105 | 97.512 | 85 | 100 | 70 | 52 | 32.634 | 9.139 | 7.121 | 133.196 | 31.179 | 28.674 | 29.3 | 601.88 | 26.742 | 27.683 | 1256.936 | 27.484 | 27.748 | 40.236 | 22.001 | 2.9 | 5.2 | 1.2 | 0.8 | 0.2
5241 | 30/07/2025 12:12:20.739 | 97.104 | 83 | 100 | 70 | 52 | 28.899 | 9.135 | 7.128 | 133.03 | 31.176 | 28.7 | 29.312 | 601.847 | 26.72 | 27.659 | 1257.277 | 27.5 | 27.754 | 38.371 | 22.001 | 2.9 | 3.9 | 1.2 | 0.1 | 0.2
5242 | 30/07/2025 12:12:22.374 | 97.584 | 84 | 100 | 70 | 52 | 30.716 | 9.156 | 7.134 | 133.238 | 31.171 | 28.708 | 29.275 | 602.012 | 26.747 | 27.703 | 1262.443 | 27.503 | 27.742 | 38.245 | 27.001 | 2.2 | 5.4 | 1.2 | 0 | 0.1
5243 | 30/07/2025 12:12:24.009 | 97.8 | 84 | 100 | 70 | 52 | 32.817 | 9.282 | 7.134 | 133.234 | 31.173 | 28.684 | 29.261 | 601.925 | 26.759 | 27.704 | 1257.146 | 27.478 | 27.76 | 38.389 | 27.001 | 2.2 | 3.5 | 1.2 | 0 | 0.1
5244 | 30/07/2025 12:12:25.645 | 97.464 | 86 | 99 | 71 | 52 | 31.292 | 9.135 | 7.133 | 133.109 | 31.148 | 28.677 | 29.294 | 601.986 | 26.749 | 27.709 | 1262.215 | 27.484 | 27.768 | 38.429 | 30.001 | 3.6 | 4.2 | 1.8 | 0.6 | 0.1
5245 | 30/07/2025 12:12:27.280 | 97.608 | 87 | 100 | 70 | 52 | 28.856 | 9.172 | 7.136 | 132.739 | 31.157 | 28.702 | 29.286 | 601.786 | 26.756 | 27.714 | 1271.698 | 27.496 | 27.744 | 38.496 | 30.001 | 3.6 | 4.2 | 1.8 | 0.6 | 0.1
5246 | 30/07/2025 12:12:28.914 | 97.2 | 84 | 100 | 69 | 52 | 32.338 | 9.295 | 7.133 | 132.987 | 31.154 | 28.703 | 29.293 | 601.824 | 26.747 | 27.744 | 1276.915 | 27.513 | 27.735 | 38.566 | 30.001 | 3.6 | 4.4 | 1.8 | 0.8 | 0.1
5247 | 30/07/2025 12:12:30.549 | 97.44 | 84 | 100 | 71 | 52 | 28.783 | 9.152 | 7.136 | 133.231 | 31.154 | 28.7 | 29.268 | 601.929 | 26.75 | 27.712 | 1269.682 | 27.483 | 27.757 | 38.249 | 30.001 | 2.6 | 3.9 | 0 | 0.6 | 0.1
5248 | 30/07/2025 12:12:32.183 | 96.816 | 85 | 100 | 70 | 52 | 31.355 | 9.294 | 7.134 | 133.165 | 31.17 | 28.688 | 29.268 | 602.02 | 26.746 | 27.694 | 1276.996 | 27.465 | 27.767 | 38.508 | 30.001 | 2.6 | 4.3 | 0 | 0.3 | 0.1
5249 | 30/07/2025 12:12:33.818 | 96.888 | 84 | 100 | 71 | 54 | 32.886 | 9.135 | 7.134 | 133.089 | 31.17 | 28.686 | 29.29 | 601.992 | 26.739 | 27.85 | 1282.496 | 27.495 | 27.757 | 38.479 | 26.001 | 2.6 | 3.5 | 0.6 | 0.5 | 0.1
5250 | 30/07/2025 12:12:35.451 | 96.216 | 84 | 100 | 70 | 52 | 30.619 | 8.989 | 7.134 | 133.139 | 31.181 | 28.699 | 29.294 | 601.873 | 26.757 | 27.707 | 1283.049 | 27.49 | 27.739 | 40.266 | 26.001 | 2.6 | 2.9 | 0.6 | 0 | 0.1
5251 | 30/07/2025 12:12:37.086 | 96.528 | 83 | 100 | 70 | 53 | 32.736 | 8.915 | 7.135 | 132.953 | 31.197 | 28.696 | 29.285 | 601.806 | 26.739 | 27.776 | 1276.552 | 27.486 | 27.737 | 40.119 | 26.001 | 2.6 | 2.9 | 0.6 | 0 | 0.1
5252 | 30/07/2025 12:12:38.721 | 96.384 | 84 | 100 | 71 | 52 | 31.82 | 9.209 | 7.134 | 133.208 | 31.183 | 28.686 | 29.28 | 603.249 | 26.75 | 27.692 | 1271.962 | 27.477 | 27.75 | 40.035 | 26.001 | 1.9 | 3.8 | 0.6 | 0 | 0.1
5253 | 30/07/2025 12:12:40.357 | 96 | 85 | 100 | 70 | 51 | 28.581 | 8.988 | 7.132 | 133.165 | 31.18 | 28.68 | 29.279 | 603.158 | 26.743 | 27.851 | 1277.043 | 27.48 | 27.768 | 40.286 | 26.001 | 1.9 | 2.5 | 0.6 | 0.8 | 0.1
5254 | 30/07/2025 12:12:41.992 | 96.168 | 82 | 100 | 71 | 52 | 31.711 | 8.988 | 7.137 | 133.076 | 31.17 | 28.689 | 29.292 | 601.857 | 26.744 | 27.84 | 1279.314 | 27.503 | 27.752 | 40.409 | 26.001 | 2.8 | 4.6 | 0.6 | 0.4 | 0.1
5255 | 30/07/2025 12:12:43.626 | 95.928 | 82 | 100 | 70 | 51 | 32.889 | 9.136 | 7.133 | 132.933 | 31.18 | 28.693 | 29.288 | 601.993 | 26.729 | 27.834 | 1282.268 | 27.488 | 27.743 | 40.217 | 26.001 | 2.8 | 4.6 | 0.6 | 0.5 | 0.1
5256 | 30/07/2025 12:12:45.262 | 96.216 | 84 | 100 | 69 | 52 | 30.03 | 9.268 | 7.134 | 133.037 | 31.173 | 28.702 | 29.275 | 602.075 | 26.732 | 27.693 | 1286.045 | 27.495 | 27.751 | 40.192 | 26.001 | 2.8 | 4.6 | 0.6 | 0.5 | 0.1
5257 | 30/07/2025 12:12:46.896 | 96.408 | 84 | 100 | 71 | 52 | 32.852 | 9.13 | 7.132 | 133.229 | 31.171 | 28.695 | 29.285 | 601.851 | 26.731 | 27.829 | 1281.919 | 27.487 | 27.763 | 40.235 | 23.001 | 2.2 | 4.8 | 0 | 0 | 0.1
5258 | 30/07/2025 12:12:48.530 | 96.816 | 84 | 100 | 71 | 53 | 31.134 | 8.999 | 7.121 | 132.962 | 31.171 | 28.663 | 29.266 | 601.895 | 26.731 | 27.726 | 1278.003 | 27.471 | 27.758 | 40.397 | 23.001 | 2.2 | 3.8 | 0 | 0.5 | 0.1
5259 | 30/07/2025 12:12:50.164 | 97.176 | 84 | 100 | 70 | 52 | 28.85 | 9.138 | 7.149 | 133.187 | 31.185 | 28.698 | 29.295 | 601.879 | 26.731 | 27.828 | 1264.836 | 27.491 | 27.746 | 40.363 | 29.001 | 2.1 | 4.8 | 0 | 0.8 | 0.1
5260 | 30/07/2025 12:12:51.798 | 96.672 | 85 | 100 | 71 | 50 | 32.202 | 9.135 | 7.185 | 133.173 | 31.176 | 28.706 | 29.274 | 603.157 | 26.734 | 27.67 | 1257.598 | 27.507 | 27.74 | 40.231 | 29.001 | 2.1 | 3.1 | 0 | 0.9 | 0.1
5261 | 30/07/2025 12:12:53.433 | 96.912 | 84 | 100 | 70 | 52 | 32.768 | 8.983 | 7.135 | 133.112 | 31.169 | 28.686 | 29.271 | 601.926 | 26.733 | 27.833 | 1259.719 | 27.492 | 27.766 | 40.171 | 23.001 | 1.7 | 2.8 | 0.6 | 1 | 0.2
5262 | 30/07/2025 12:12:55.067 | 96.6 | 83 | 100 | 70 | 52 | 31.171 | 9.129 | 7.133 | 133.068 | 31.169 | 28.688 | 29.263 | 602.426 | 26.746 | 27.825 | 1265.628 | 27.473 | 27.761 | 40.35 | 23.001 | 1.7 | 2.8 | 0.6 | 1 | 0.2
5263 | 30/07/2025 12:12:56.702 | 96.312 | 84 | 100 | 70 | 52 | 32.874 | 9.135 | 7.135 | 133.116 | 31.164 | 28.673 | 29.282 | 602.014 | 26.747 | 27.835 | 1264.822 | 27.479 | 27.75 | 40.231 | 23.001 | 1.7 | 3.9 | 0.6 | 0.1 | 0.2
5264 | 30/07/2025 12:12:58.336 | 96.576 | 84 | 100 | 70 | 52 | 30.598 | 8.988 | 7.135 | 132.975 | 31.174 | 28.7 | 29.297 | 601.919 | 26.743 | 27.827 | 1266.682 | 27.505 | 27.748 | 40.1 | 25.001 | 3 | 3.1 | 0.1 | 0.8 | 0.2
5265 | 30/07/2025 12:13:00.053 | 96.072 | 83 | 100 | 71 | 53 | 29.154 | 8.989 | 7.135 | 133.151 | 31.162 | 28.691 | 29.275 | 601.97 | 26.742 | 27.867 | 1267.127 | 27.49 | 27.737 | 38.293 | 25.001 | 3 | 2.8 | 0.1 | 0.8 | 0.2
5266 | 30/07/2025 12:13:01.688 | 96.36 | 84 | 100 | 70 | 52 | 35.033 | 9.178 | 7.134 | 133.242 | 31.167 | 28.693 | 29.268 | 601.891 | 26.747 | 27.841 | 1260.615 | 27.472 | 27.752 | 38.363 | 28.001 | 3.5 | 2.6 | 0.6 | 0.7 | 0.2
5267 | 30/07/2025 12:13:03.324 | 95.736 | 83 | 100 | 71 | 52 | 32.771 | 9.133 | 7.132 | 133.167 | 31.156 | 28.675 | 29.283 | 602.013 | 26.746 | 27.849 | 1263.632 | 27.487 | 27.76 | 40.309 | 28.001 | 3.5 | 2.6 | 0.6 | 0.7 | 0.2
5268 | 30/07/2025 12:13:04.958 | 95.616 | 84 | 100 | 70 | 50 | 31.866 | 9.131 | 7.134 | 133.191 | 31.167 | 28.686 | 29.302 | 601.802 | 26.754 | 27.851 | 1262.172 | 27.496 | 27.76 | 38.613 | 28.001 | 3.5 | 4.5 | 0.6 | 0 | 0.2
5269 | 30/07/2025 12:13:06.593 | 96.024 | 83 | 100 | 71 | 52 | 32.902 | 9.135 | 7.127 | 133.009 | 31.169 | 28.697 | 29.29 | 603.033 | 26.744 | 27.854 | 1267.695 | 27.508 | 27.739 | 38.602 | 28.001 | 2.8 | 4.6 | 1.5 | 0.5 | 0.2
5270 | 30/07/2025 12:13:08.227 | 95.352 | 82 | 100 | 70 | 52 | 30.077 | 9.132 | 7.125 | 133.171 | 31.183 | 28.694 | 29.284 | 603.106 | 26.75 | 27.848 | 1275.049 | 27.486 | 27.732 | 40.04 | 28.001 | 2.8 | 4.2 | 1.5 | 0.5 | 0.2
5271 | 30/07/2025 12:13:09.863 | 95.64 | 83 | 100 | 71 | 52 | 29.541 | 9.13 | 7.118 | 133.067 | 31.196 | 28.688 | 29.264 | 603.289 | 26.748 | 27.845 | 1278.752 | 27.478 | 27.766 | 40.295 | 27.001 | 3.4 | 2.8 | 0.6 | 0.5 | 0.1
5272 | 30/07/2025 12:13:11.500 | 94.992 | 84 | 100 | 70 | 52 | 32.606 | 9.252 | 7.125 | 133.017 | 31.191 | 28.681 | 29.282 | 603.173 | 26.741 | 27.858 | 1284.685 | 27.486 | 27.76 | 40.177 | 27.001 | 3.4 | 2.1 | 0.6 | 0.2 | 0.1
5273 | 30/07/2025 12:13:13.135 | 94.992 | 82 | 100 | 71 | 52 | 32.361 | 8.914 | 7.134 | 133.154 | 31.192 | 28.695 | 29.29 | 603.022 | 26.738 | 27.844 | 1295.681 | 27.493 | 27.74 | 39.98 | 27.001 | 3.4 | 2.1 | 0.6 | 0.2 | 0.1
5274 | 30/07/2025 12:13:14.769 | 94.632 | 83 | 100 | 70 | 51 | 32.222 | 9.127 | 7.15 | 133.03 | 31.183 | 28.696 | 29.283 | 602.998 | 26.729 | 27.856 | 1296.699 | 27.477 | 27.726 | 40.158 | 27.001 | 1.6 | 4 | 0.6 | 0 | 0.2
5275 | 30/07/2025 12:13:16.404 | 95.544 | 83 | 100 | 70 | 53 | 32.841 | 8.985 | 7.187 | 133.443 | 31.189 | 28.694 | 29.276 | 603.307 | 26.735 | 27.828 | 1297.236 | 27.483 | 27.747 | 39.935 | 27.001 | 1.6 | 5 | 0.6 | 0 | 0.2
5276 | 30/07/2025 12:13:18.038 | 95.4 | 83 | 100 | 71 | 52 | 29.46 | 9.133 | 7.186 | 133.156 | 31.167 | 28.672 | 29.26 | 603.259 | 26.722 | 27.834 | 1289.564 | 27.479 | 27.75 | 40.289 | 23.001 | 3.6 | 3.7 | 0.7 | 0.5 | 0.2
5277 | 30/07/2025 12:13:19.672 | 95.496 | 84 | 100 | 70 | 51 | 30.156 | 8.986 | 7.162 | 133.096 | 31.175 | 28.687 | 29.31 | 603.102 | 26.74 | 27.836 | 1278.518 | 27.495 | 27.744 | 40.214 | 23.001 | 3.6 | 6.9 | 0.7 | 0 | 0.2
5278 | 30/07/2025 12:13:21.308 | 95.592 | 83 | 100 | 70 | 52 | 32.711 | 9.136 | 7.134 | 132.787 | 31.173 | 28.693 | 29.287 | 603.191 | 26.712 | 27.829 | 1270.03 | 27.496 | 27.743 | 40.055 | 23.001 | 3.6 | 6.9 | 0.7 | 0 | 0.2
5279 | 30/07/2025 12:13:22.944 | 95.232 | 82 | 100 | 70 | 54 | 29.131 | 9.234 | 7.137 | 133.329 | 31.176 | 28.691 | 29.268 | 603.181 | 26.741 | 27.824 | 1270.256 | 27.486 | 27.713 | 39.915 | 27.001 | 2.7 | 3.8 | 1.9 | 0 | 0.2
5280 | 30/07/2025 12:13:24.578 | 96.288 | 85 | 100 | 70 | 53 | 32.454 | 8.993 | 7.151 | 133.145 | 31.161 | 28.693 | 29.264 | 603.106 | 26.724 | 27.817 | 1274.605 | 27.48 | 27.763 | 40.135 | 27.001 | 2.7 | 4.1 | 1.9 | 0.5 | 0.2
5281 | 30/07/2025 12:13:26.212 | 96.504 | 83 | 100 | 71 | 51 | 32.624 | 8.989 | 7.151 | 133.128 | 31.165 | 28.664 | 29.264 | 603.078 | 26.735 | 27.825 | 1279.115 | 27.465 | 27.762 | 40.29 | 28.001 | 3.3 | 3.8 | 0.4 | 0.2 | 0.2
5282 | 30/07/2025 12:13:27.846 | 96.672 | 84 | 100 | 71 | 52 | 28.943 | 8.965 | 7.135 | 131.555 | 31.173 | 28.698 | 29.301 | 602.988 | 26.737 | 27.822 | 1284.648 | 27.491 | 27.752 | 40.181 | 28.001 | 3.3 | 3.4 | 0.4 | 0.8 | 0.2
5283 | 30/07/2025 12:13:29.481 | 96.504 | 83 | 100 | 71 | 52 | 30.586 | 9.134 | 7.122 | 131.69 | 31.176 | 28.696 | 29.285 | 603.144 | 26.735 | 27.83 | 1286.229 | 27.511 | 27.74 | 40.236 | 30.001 | 3.7 | 3.4 | 1.4 | 0.5 | 0.2
5284 | 30/07/2025 12:13:31.116 | 96.144 | 83 | 100 | 71 | 51 | 32.81 | 9.148 | 7.136 | 131.843 | 31.161 | 28.694 | 29.272 | 603.207 | 26.747 | 27.84 | 1278.156 | 27.492 | 27.757 | 40.086 | 30.001 | 3.7 | 3.4 | 1.4 | 0.5 | 0.2
5285 | 30/07/2025 12:13:32.752 | 96.648 | 84 | 100 | 70 | 52 | 29.538 | 8.987 | 7.132 | 131.629 | 31.158 | 28.693 | 29.265 | 603.162 | 26.739 | 27.852 | 1267.614 | 27.472 | 27.762 | 40.122 | 30.001 | 3.7 | 4 | 1.4 | 0.6 | 0.2
5286 | 30/07/2025 12:13:34.387 | 97.008 | 85 | 100 | 70 | 53 | 32.606 | 9.003 | 7.134 | 131.761 | 31.168 | 28.668 | 29.283 | 603.065 | 26.768 | 27.862 | 1248.896 | 27.46 | 27.74 | 40.213 | 24.001 | 1.5 | 4.8 | 1 | 0.1 | 0.2
5287 | 30/07/2025 12:13:36.022 | 97.392 | 84 | 100 | 71 | 52 | 32.399 | 8.991 | 7.114 | 131.746 | 31.145 | 28.699 | 29.294 | 603.051 | 26.748 | 27.85 | 1250.247 | 27.518 | 27.751 | 40.256 | 24.001 | 1.5 | 5.9 | 1 | 0.5 | 0.2
5288 | 30/07/2025 12:13:37.655 | 97.776 | 85 | 100 | 70 | 52 | 28.71 | 8.842 | 7.088 | 131.745 | 31.157 | 28.691 | 29.279 | 603.093 | 26.748 | 27.854 | 1257.47 | 27.486 | 27.73 | 40.08 | 23.001 | 2.5 | 5.7 | 0.7 | 0.2 | 0.2
5289 | 30/07/2025 12:13:39.295 | 97.584 | 84 | 100 | 71 | 52 | 31.385 | 8.959 | 7.085 | 131.925 | 31.163 | 28.685 | 29.278 | 603.234 | 26.74 | 27.849 | 1264.875 | 27.476 | 27.765 | 40.117 | 23.001 | 2.5 | 5.7 | 0.7 | 0.2 | 0.2
5290 | 30/07/2025 12:13:40.930 | 98.232 | 86 | 100 | 71 | 52 | 29.394 | 9.125 | 7.086 | 131.78 | 31.172 | 28.68 | 29.26 | 603.076 | 26.743 | 27.859 | 1267.099 | 27.449 | 27.76 | 39.296 | 23.001 | 2.5 | 3.9 | 0.7 | 0.5 | 0.2
5291 | 30/07/2025 12:13:42.567 | 98.16 | 85 | 100 | 71 | 52 | 30.179 | 9.174 | 7.132 | 131.702 | 31.181 | 28.685 | 29.307 | 603.148 | 26.734 | 27.848 | 1265.19 | 27.496 | 27.755 | 38.488 | 30.001 | 5.7 | 1.7 | 0.9 | 0.6 | 0.1
5292 | 30/07/2025 12:13:44.202 | 98.232 | 84 | 100 | 70 | 52 | 32.737 | 8.927 | 7.125 | 131.631 | 31.181 | 28.697 | 29.294 | 603.047 | 26.731 | 27.854 | 1268.928 | 27.496 | 27.741 | 38.533 | 30.001 | 5.7 | 3.5 | 0.9 | 0.5 | 0.1
5293 | 30/07/2025 12:13:45.838 | 97.992 | 84 | 100 | 69 | 54 | 31.841 | 9.256 | 7.122 | 131.995 | 31.195 | 28.693 | 29.262 | 602.663 | 26.749 | 27.853 | 1275.521 | 27.49 | 27.727 | 37.979 | 27.001 | 3.5 | 4 | 0.9 | 0.8 | 0.1
5294 | 30/07/2025 12:13:47.473 | 98.256 | 84 | 100 | 70 | 51 | 28.708 | 9.133 | 7.12 | 131.622 | 31.185 | 28.683 | 29.259 | 602.042 | 26.738 | 27.839 | 1267.034 | 27.467 | 27.774 | 38.372 | 27.001 | 3.5 | 5.4 | 0.9 | 0.4 | 0.1
5295 | 30/07/2025 12:13:49.106 | 98.304 | 87 | 100 | 70 | 52 | 31.86 | 8.989 | 7.122 | 131.484 | 31.192 | 28.668 | 29.289 | 601.831 | 26.739 | 27.867 | 1267.277 | 27.465 | 27.759 | 38.465 | 27.001 | 3.5 | 5.4 | 0.9 | 0.4 | 0.1
5296 | 30/07/2025 12:13:50.744 | 98.688 | 87 | 100 | 70 | 52 | 29.051 | 9.129 | 7.121 | 131.74 | 31.174 | 28.693 | 29.287 | 602.096 | 26.74 | 27.852 | 1265.348 | 27.514 | 27.764 | 38.47 | 28.001 | 5.2 | 3.2 | 0.6 | 0.6 | 0.3
5297 | 30/07/2025 12:13:52.379 | 98.376 | 87 | 100 | 71 | 53 | 30.736 | 8.987 | 7.124 | 131.447 | 31.185 | 28.695 | 29.289 | 601.704 | 26.726 | 27.86 | 1257.244 | 27.49 | 27.721 | 39.784 | 28.001 | 5.2 | 4.1 | 0.6 | 0.1 | 0.3
5298 | 30/07/2025 12:13:54.015 | 97.968 | 85 | 100 | 70 | 52 | 32.87 | 9.129 | 7.133 | 131.784 | 31.188 | 28.692 | 29.288 | 602.04 | 26.728 | 27.83 | 1257.771 | 27.491 | 27.757 | 40.052 | 28.001 | 2.3 | 3.8 | 0.2 | 0 | 0.2
5299 | 30/07/2025 12:13:55.651 | 98.376 | 86 | 100 | 70 | 52 | 31.296 | 9.134 | 7.133 | 131.629 | 31.178 | 28.682 | 29.259 | 601.891 | 26.721 | 27.832 | 1257.334 | 27.467 | 27.757 | 38.612 | 28.001 | 2.3 | 4.5 | 0.2 | 0.5 | 0.2
5300 | 30/07/2025 12:13:57.285 | 98.448 | 86 | 100 | 70 | 52 | 28.876 | 9.139 | 7.136 | 131.576 | 31.181 | 28.671 | 29.298 | 602.023 | 26.735 | 27.831 | 1264.304 | 27.489 | 27.746 | 38.39 | 28.001 | 2.3 | 4.5 | 0.2 | 0.5 | 0.2
5301 | 30/07/2025 12:13:58.919 | 98.136 | 85 | 100 | 70 | 53 | 32.309 | 9.288 | 7.134 | 131.222 | 31.176 | 28.705 | 29.294 | 601.911 | 26.725 | 27.843 | 1263.865 | 27.506 | 27.749 | 38.535 | 29.001 | 3.8 | 4.1 | 1.5 | 0 | 0.3
5302 | 30/07/2025 12:14:00.554 | 97.848 | 84 | 100 | 71 | 52 | 28.73 | 9.289 | 7.134 | 133.368 | 31.188 | 28.693 | 29.282 | 601.909 | 26.734 | 27.823 | 1247.282 | 27.486 | 27.708 | 38.345 | 29.001 | 3.8 | 4.6 | 1.5 | 1.1 | 0.3
5303 | 30/07/2025 12:14:02.187 | 98.328 | 88 | 100 | 70 | 54 | 31.161 | 9.435 | 7.134 | 133.052 | 31.174 | 28.695 | 29.27 | 602.06 | 26.734 | 27.827 | 1258.21 | 27.498 | 27.761 | 38.533 | 27.001 | 2.7 | 5.9 | 1 | 1.1 | 0.3
5304 | 30/07/2025 12:14:03.822 | 98.184 | 85 | 100 | 71 | 52 | 32.916 | 9.134 | 7.134 | 133.285 | 31.167 | 28.659 | 29.265 | 601.754 | 26.734 | 27.842 | 1268.065 | 27.469 | 27.753 | 38.567 | 27.001 | 2.7 | 3.5 | 1 | 0.8 | 0.3
5305 | 30/07/2025 12:14:05.454 | 98.28 | 86 | 100 | 70 | 52 | 30.595 | 9.246 | 7.134 | 133.227 | 31.161 | 28.693 | 29.308 | 601.858 | 26.754 | 27.845 | 1278.063 | 27.506 | 27.758 | 38.305 | 22.001 | 1.8 | 3.4 | 0.4 | 0.5 | 0.3
5306 | 30/07/2025 12:14:07.088 | 98.376 | 85 | 100 | 70 | 52 | 32.725 | 9.245 | 7.137 | 132.986 | 31.152 | 28.695 | 29.295 | 601.718 | 26.737 | 27.845 | 1274.771 | 27.489 | 27.743 | 38.395 | 22.001 | 1.8 | 3.4 | 0.4 | 0.5 | 0.3
5307 | 30/07/2025 12:14:08.720 | 98.544 | 87 | 100 | 70 | 52 | 31.834 | 9.26 | 7.133 | 133.354 | 31.156 | 28.689 | 29.287 | 602.116 | 26.739 | 27.838 | 1276.044 | 27.488 | 27.735 | 38.278 | 22.001 | 1.8 | 2.9 | 0.4 | 0.6 | 0.3
5308 | 30/07/2025 12:14:10.353 | 97.944 | 85 | 100 | 71 | 51 | 28.706 | 9.208 | 7.151 | 133.064 | 31.16 | 28.69 | 29.282 | 602.019 | 26.747 | 27.88 | 1277.171 | 27.477 | 27.769 | 39.602 | 30.001 | 1.8 | 4 | 0 | 0.1 | 0.3
5309 | 30/07/2025 12:14:11.986 | 97.464 | 84 | 100 | 71 | 52 | 31.771 | 9.129 | 7.151 | 133.419 | 31.163 | 28.68 | 29.276 | 601.912 | 26.755 | 27.844 | 1274.463 | 27.459 | 27.745 | 38.43 | 30.001 | 1.8 | 3.9 | 0 | 0.8 | 0.3
5310 | 30/07/2025 12:14:13.618 | 97.32 | 85 | 100 | 70 | 52 | 32.876 | 9.05 | 7.153 | 133.006 | 31.161 | 28.706 | 29.29 | 601.925 | 26.737 | 27.841 | 1267.089 | 27.515 | 27.753 | 38.234 | 25.001 | 3.1 | 4.2 | 0.6 | 0.5 | 0.3
5311 | 30/07/2025 12:14:15.253 | 96.864 | 84 | 100 | 70 | 52 | 29.979 | 8.985 | 7.152 | 133.096 | 31.166 | 28.693 | 29.276 | 602.001 | 26.737 | 27.864 | 1262.27 | 27.489 | 27.722 | 38.219 | 25.001 | 3.1 | 4.2 | 0.6 | 0.5 | 0.3
5312 | 30/07/2025 12:14:16.888 | 96.384 | 84 | 100 | 70 | 52 | 32.799 | 8.991 | 7.152 | 133.259 | 31.175 | 28.694 | 29.282 | 601.908 | 26.743 | 27.858 | 1262.564 | 27.506 | 27.749 | 38.271 | 25.001 | 3.1 | 4.6 | 0.6 | 0.1 | 0.3
5313 | 30/07/2025 12:14:18.521 | 96.768 | 84 | 100 | 71 | 52 | 31.318 | 9.139 | 7.153 | 133.147 | 31.24 | 28.682 | 29.262 | 601.945 | 26.742 | 27.865 | 1267.41 | 27.472 | 27.76 | 39.585 | 28.001 | 3.4 | 3.9 | 1.9 | 0 | 0.3
5314 | 30/07/2025 12:14:20.155 | 97.296 | 84 | 100 | 70 | 52 | 28.786 | 9.131 | 7.168 | 133.241 | 31.179 | 28.674 | 29.313 | 602.09 | 26.738 | 27.842 | 1267.502 | 27.488 | 27.755 | 40.384 | 28.001 | 3.4 | 6.3 | 1.9 | 0 | 0.3
5315 | 30/07/2025 12:14:21.790 | 97.056 | 84 | 100 | 70 | 51 | 32.235 | 9.216 | 7.182 | 133.009 | 31.177 | 28.706 | 29.281 | 601.844 | 26.738 | 27.85 | 1276.918 | 27.494 | 27.745 | 40.38 | 25.001 | 2.2 | 3.7 | 0.8 | 0.8 | 0.3
5316 | 30/07/2025 12:14:23.427 | 97.056 | 84 | 100 | 70 | 52 | 32.855 | 9.134 | 7.152 | 133.325 | 31.188 | 28.692 | 29.291 | 601.815 | 26.762 | 27.852 | 1287.033 | 27.49 | 27.741 | 39.86 | 25.001 | 2.2 | 4.3 | 0.8 | 0.3 | 0.3
5317 | 30/07/2025 12:14:25.062 | 96.96 | 85 | 100 | 72 | 52 | 31.391 | 9.21 | 7.152 | 133.08 | 31.18 | 28.692 | 29.269 | 601.858 | 26.737 | 27.86 | 1287.245 | 27.484 | 27.755 | 40.078 | 25.001 | 2.2 | 4.3 | 0.8 | 0.3 | 0.3
5318 | 30/07/2025 12:14:26.696 | 96.6 | 84 | 100 | 70 | 52 | 32.898 | 9.202 | 7.133 | 133.208 | 31.354 | 28.674 | 29.272 | 602.013 | 26.733 | 27.844 | 1284.55 | 27.462 | 27.75 | 40.356 | 28.001 | 3 | 3.8 | 1.2 | 0.5 | 0.3
5319 | 30/07/2025 12:14:28.331 | 96.648 | 84 | 100 | 71 | 52 | 30.709 | 9.234 | 7.134 | 133.013 | 31.343 | 28.692 | 29.293 | 602.012 | 26.733 | 27.84 | 1270.591 | 27.512 | 27.754 | 40.268 | 28.001 | 3 | 3.8 | 1.2 | 1.2 | 0.3
5320 | 30/07/2025 12:14:29.967 | 97.2 | 85 | 100 | 71 | 52 | 29.208 | 9.195 | 7.136 | 132.81 | 31.233 | 28.692 | 29.27 | 601.823 | 26.739 | 27.834 | 1259.956 | 27.488 | 27.716 | 40.379 | 27.001 | 3.1 | 4.8 | 0 | 0.8 | 0.3
5321 | 30/07/2025 12:14:31.602 | 97.344 | 84 | 100 | 72 | 52 | 32.478 | 9.129 | 7.134 | 133.243 | 31.179 | 28.689 | 29.284 | 600.693 | 26.725 | 27.803 | 1260.157 | 27.481 | 27.729 | 39.966 | 27.001 | 3.1 | 5.3 | 0 | 0.5 | 0.3
5322 | 30/07/2025 12:14:33.236 | 97.008 | 85 | 100 | 70 | 53 | 32.742 | 9.134 | 7.132 | 132.995 | 31.177 | 28.684 | 29.258 | 600.429 | 26.724 | 27.822 | 1257.607 | 27.477 | 27.756 | 40.343 | 27.001 | 3.1 | 5.3 | 0 | 0.5 | 0.3
5323 | 30/07/2025 12:14:34.872 | 97.224 | 84 | 100 | 71 | 52 | 31.745 | 9.213 | 7.133 | 133.181 | 31.181 | 28.673 | 29.274 | 600.611 | 26.719 | 27.823 | 1257.909 | 27.476 | 27.759 | 39.822 | 29.001 | 3.1 | 4.7 | 0.3 | 0.8 | 0.2
5324 | 30/07/2025 12:14:36.506 | 97.344 | 85 | 100 | 70 | 52 | 32.947 | 8.987 | 7.136 | 132.944 | 31.343 | 28.698 | 29.288 | 600.473 | 26.735 | 27.838 | 1263.093 | 27.503 | 27.76 | 38.46 | 29.001 | 3.1 | 4.2 | 0.3 | 0.7 | 0.2
5325 | 30/07/2025 12:14:38.139 | 97.584 | 84 | 100 | 71 | 50 | 30.108 | 9.311 | 7.134 | 133.165 | 31.366 | 28.695 | 29.274 | 600.413 | 26.75 | 27.842 | 1247.437 | 27.49 | 27.731 | 38.271 | 25.001 | 2.7 | 3.5 | 0.3 | 0.7 | 0.3
5326 | 30/07/2025 12:14:39.775 | 97.56 | 84 | 100 | 71 | 53 | 29.491 | 9.159 | 7.133 | 131.848 | 31.157 | 28.689 | 29.267 | 600.634 | 26.757 | 27.855 | 1239.242 | 27.509 | 27.756 | 38.195 | 25.001 | 2.7 | 3.7 | 0.3 | 0.9 | 0.3
5327 | 30/07/2025 12:14:41.409 | 97.752 | 84 | 100 | 70 | 52 | 32.623 | 8.989 | 7.134 | 131.791 | 31.33 | 28.672 | 29.271 | 601.856 | 26.748 | 27.852 | 1246.674 | 27.467 | 27.751 | 38.46 | 23.001 | 3.1 | 4.3 | 1.2 | 0.5 | 0.3
5328 | 30/07/2025 12:14:43.043 | 97.2 | 86 | 100 | 70 | 53 | 28.824 | 9.205 | 7.133 | 131.652 | 31.333 | 28.668 | 29.29 | 602.003 | 26.746 | 27.856 | 1251.958 | 27.494 | 27.752 | 38.513 | 23.001 | 3.1 | 4.3 | 1.2 | 0.5 | 0.3
5329 | 30/07/2025 12:14:44.678 | 97.056 | 85 | 100 | 71 | 51 | 32.139 | 9.146 | 7.136 | 131.653 | 31.334 | 28.701 | 29.288 | 601.75 | 26.764 | 27.862 | 1257.175 | 27.491 | 27.729 | 38.511 | 23.001 | 3.1 | 5.8 | 1.2 | 0.5 | 0.3
5330 | 30/07/2025 12:14:46.313 | 97.272 | 85 | 100 | 70 | 52 | 32.812 | 9.14 | 7.134 | 131.883 | 31.339 | 28.694 | 29.299 | 602.076 | 26.739 | 27.85 | 1257.389 | 27.488 | 27.747 | 38.375 | 29.001 | 2.3 | 3.7 | 0.3 | 0.2 | 0.3
5331 | 30/07/2025 12:14:47.950 | 96.96 | 86 | 100 | 70 | 51 | 29.403 | 8.984 | 7.133 | 131.779 | 31.337 | 28.676 | 29.277 | 601.863 | 26.737 | 27.863 | 1252.928 | 27.478 | 27.759 | 38.389 | 29.001 | 2.3 | 4 | 0.3 | 1.1 | 0.3
5332 | 30/07/2025 12:14:49.584 | 97.848 | 86 | 100 | 71 | 53 | 30.011 | 9.128 | 7.133 | 131.836 | 31.366 | 28.677 | 29.282 | 601.792 | 26.757 | 27.846 | 1257.394 | 27.471 | 27.749 | 38.458 | 24.001 | 2.9 | 3.5 | 0.7 | 0.5 | 0.3
5333 | 30/07/2025 12:14:51.219 | 97.824 | 88 | 100 | 70 | 51 | 32.72 | 9.134 | 7.134 | 131.514 | 31.355 | 28.707 | 29.301 | 601.935 | 26.751 | 27.853 | 1257.204 | 27.525 | 27.752 | 38.516 | 24.001 | 2.9 | 3.5 | 0.7 | 0.5 | 0.3
5334 | 30/07/2025 12:14:52.853 | 98.472 | 86 | 100 | 70 | 52 | 29.069 | 9.28 | 7.134 | 131.435 | 31.359 | 28.698 | 29.293 | 601.77 | 26.741 | 27.84 | 1260.534 | 27.492 | 27.738 | 38.31 | 24.001 | 2.9 | 4 | 0.7 | 0.5 | 0.3
5335 | 30/07/2025 12:14:54.488 | 98.664 | 86 | 100 | 70 | 52 | 32.461 | 9.285 | 7.151 | 131.786 | 31.358 | 28.695 | 29.276 | 601.949 | 26.737 | 27.848 | 1267.35 | 27.504 | 27.735 | 38.139 | 25.001 | 2.6 | 2.8 | 1.5 | 1.7 | 0.2
5336 | 30/07/2025 12:14:56.122 | 98.856 | 88 | 100 | 70 | 52 | 32.647 | 9.134 | 7.152 | 131.721 | 31.359 | 28.684 | 29.262 | 601.816 | 26.753 | 27.851 | 1267.062 | 27.469 | 27.752 | 38.416 | 25.001 | 2.6 | 3.3 | 1.5 | 0.6 | 0.2
5337 | 30/07/2025 12:14:57.756 | 98.832 | 87 | 100 | 71 | 52 | 29.036 | 9.288 | 7.133 | 131.592 | 31.375 | 28.684 | 29.296 | 601.936 | 26.734 | 27.834 | 1277.203 | 27.477 | 27.751 | 38.342 | 26.001 | 3.2 | 2.9 | 0.6 | 0.8 | 0.3
5338 | 30/07/2025 12:14:59.391 | 98.592 | 86 | 100 | 70 | 52 | 30.817 | 9.137 | 7.135 | 131.331 | 31.351 | 28.704 | 29.28 | 601.841 | 26.734 | 27.845 | 1269.908 | 27.5 | 27.744 | 38.545 | 26.001 | 3.2 | 5.5 | 0.6 | 0.8 | 0.3
5339 | 30/07/2025 12:15:01.025 | 98.544 | 85 | 100 | 71 | 53 | 30.14 | 9.138 | 7.133 | 131.657 | 31.361 | 28.696 | 29.29 | 602.109 | 26.733 | 27.833 | 1264.829 | 27.506 | 27.752 | 38.505 | 26.001 | 3.2 | 5.5 | 0.6 | 0.8 | 0.3
5340 | 30/07/2025 12:15:02.661 | 98.736 | 86 | 100 | 70 | 52 | 29.654 | 9.126 | 7.135 | 131.825 | 31.348 | 28.697 | 29.282 | 600.484 | 26.719 | 27.84 | 1267.109 | 27.481 | 27.752 | 38.306 | 31.001 | 1.4 | 4 | 0.7 | 0.5 | 0.3
5341 | 30/07/2025 12:15:04.301 | 98.904 | 85 | 100 | 71 | 52 | 32.605 | 9.285 | 7.119 | 131.847 | 31.362 | 28.676 | 29.269 | 600.557 | 26.725 | 27.833 | 1261.698 | 27.461 | 27.749 | 38.368 | 31.001 | 1.4 | 6 | 0.7 | 0.3 | 0.3
5342 | 30/07/2025 12:15:05.935 | 98.592 | 86 | 100 | 69 | 52 | 32.459 | 9.433 | 7.091 | 131.461 | 31.343 | 28.685 | 29.277 | 600.451 | 26.72 | 27.829 | 1267.239 | 27.506 | 27.747 | 38.409 | 21.001 | 1.7 | 4.4 | 0.3 | 0.5 | 0.4
5343 | 30/07/2025 12:15:07.570 | 98.448 | 86 | 100 | 70 | 52 | 28.776 | 9.137 | 7.089 | 131.531 | 31.354 | 28.703 | 29.288 | 600.36 | 26.736 | 27.824 | 1271.522 | 27.496 | 27.728 | 38.359 | 21.001 | 1.7 | 4.2 | 0.3 | 0 | 0.4
5344 | 30/07/2025 12:15:09.204 | 98.472 | 88 | 100 | 71 | 52 | 32.911 | 9.258 | 7.095 | 131.472 | 31.351 | 28.708 | 29.278 | 600.455 | 26.738 | 27.835 | 1274.396 | 27.49 | 27.742 | 38.303 | 21.001 | 1.7 | 4.2 | 0.3 | 0 | 0.4
5345 | 30/07/2025 12:15:10.848 | 98.184 | 86 | 100 | 71 | 52 | 29.557 | 8.987 | 7.124 | 131.776 | 31.359 | 28.686 | 29.279 | 600.497 | 26.746 | 27.833 | 1276.772 | 27.482 | 27.752 | 38.173 | 29.001 | 2.1 | 1.9 | 0 | 0.5 | 0.3
5346 | 30/07/2025 12:15:12.482 | 98.616 | 86 | 100 | 70 | 51 | 30.027 | 9.134 | 7.119 | 133.167 | 31.344 | 28.675 | 29.281 | 600.523 | 26.747 | 27.826 | 1277.142 | 27.481 | 27.757 | 38.526 | 29.001 | 2.1 | 3.2 | 0 | 1.1 | 0.3
5347 | 30/07/2025 12:15:14.118 | 98.472 | 86 | 100 | 70 | 52 | 32.785 | 9.2 | 7.097 | 132.872 | 31.324 | 28.693 | 29.274 | 600.388 | 26.74 | 27.846 | 1276.447 | 27.492 | 27.739 | 38.445 | 23.001 | 2.8 | 4.7 | 1.2 | 0.7 | 0.3
5348 | 30/07/2025 12:15:16.653 | 98.304 | 86 | 100 | 70 | 51 | 32.489 | 9.287 | 7.095 | 133.316 | 31.332 | 28.693 | 29.284 | 600.555 | 26.757 | 27.862 | 1276.912 | 27.486 | 27.73 | 38.267 | 23.001 | 2.8 | 2.7 | 1.2 | 0.3 | 0.3
5349 | 30/07/2025 12:15:18.288 | 98.184 | 85 | 100 | 70 | 52 | 32.73 | 9.131 | 7.119 | 133.027 | 31.348 | 28.686 | 29.278 | 600.578 | 26.744 | 27.839 | 1277.296 | 27.479 | 27.769 | 38.332 | 21.001 | 2.8 | 2 | 0 | 0 | 0.3
5350 | 30/07/2025 12:15:19.922 | 98.376 | 85 | 100 | 70 | 52 | 31.782 | 9.208 | 7.122 | 133.121 | 31.333 | 28.672 | 29.267 | 600.412 | 26.756 | 27.849 | 1282.913 | 27.455 | 27.749 | 38.386 | 21.001 | 2.8 | 6.2 | 0 | 0 | 0.3
5351 | 30/07/2025 12:15:21.555 | 97.896 | 84 | 100 | 70 | 52 | 32.917 | 9.212 | 7.119 | 133.186 | 31.349 | 28.689 | 29.294 | 600.623 | 26.748 | 27.852 | 1277.107 | 27.497 | 27.761 | 38.471 | 27.001 | 2.2 | 4.1 | 0 | 1 | 0.3
5352 | 30/07/2025 12:15:23.190 | 97.704 | 85 | 100 | 71 | 51 | 30.079 | 9.271 | 7.087 | 132.999 | 31.344 | 28.695 | 29.279 | 599.108 | 26.733 | 27.867 | 1267.028 | 27.501 | 27.747 | 38.506 | 27.001 | 2.2 | 4.1 | 0 | 1 | 0.3
5353 | 30/07/2025 12:15:24.826 | 98.376 | 84 | 100 | 71 | 52 | 29.485 | 9.171 | 7.073 | 133.39 | 31.372 | 28.688 | 29.267 | 600.048 | 26.755 | 27.848 | 1267.187 | 27.487 | 27.749 | 38.083 | 27.001 | 2.2 | 4.6 | 0 | 0.6 | 0.3
5354 | 30/07/2025 12:15:26.461 | 98.136 | 86 | 100 | 72 | 52 | 32.629 | 9.133 | 7.068 | 133.106 | 31.359 | 28.686 | 29.256 | 600.516 | 26.737 | 27.844 | 1267.143 | 27.477 | 27.76 | 38.451 | 23.001 | 2.9 | 2.6 | 0.3 | 0.6 | 0.3
5355 | 30/07/2025 12:15:28.103 | 97.92 | 84 | 100 | 70 | 52 | 28.794 | 9.127 | 7.066 | 133.203 | 31.368 | 28.674 | 29.271 | 600.532 | 26.756 | 27.849 | 1258.861 | 27.466 | 27.752 | 38.426 | 23.001 | 2.9 | 2.8 | 0.3 | 0 | 0.3
5356 | 30/07/2025 12:15:29.742 | 97.944 | 86 | 100 | 70 | 52 | 32.189 | 9.137 | 7.069 | 133.023 | 31.339 | 28.701 | 29.284 | 600.524 | 26.74 | 27.851 | 1257.451 | 27.518 | 27.751 | 38.441 | 25.001 | 2.7 | 3.2 | 0.6 | 0 | 0.3
5357 | 30/07/2025 12:15:31.376 | 97.632 | 85 | 100 | 70 | 52 | 32.902 | 9.133 | 7.088 | 133.036 | 31.355 | 28.695 | 29.274 | 600.392 | 26.75 | 27.846 | 1259.946 | 27.487 | 27.724 | 38.249 | 25.001 | 2.7 | 4.4 | 0.6 | 0.5 | 0.3
5358 | 30/07/2025 12:15:33.011 | 97.872 | 85 | 100 | 71 | 51 | 29.453 | 9.131 | 7.087 | 133.185 | 31.357 | 28.689 | 29.281 | 600.781 | 26.722 | 27.837 | 1261.391 | 27.487 | 27.759 | 38.197 | 25.001 | 2.7 | 4.4 | 0.6 | 0.5 | 0.3
5359 | 30/07/2025 12:15:34.644 | 97.536 | 85 | 100 | 70 | 52 | 30.157 | 9.278 | 7.083 | 133.113 | 31.346 | 28.676 | 29.256 | 599.25 | 26.738 | 27.85 | 1267.064 | 27.461 | 27.747 | 38.404 | 24.001 | 3 | 5.2 | 0 | 0.8 | 0.3
5360 | 30/07/2025 12:15:36.280 | 97.8 | 84 | 100 | 71 | 52 | 32.792 | 9.208 | 7.121 | 133.124 | 31.368 | 28.69 | 29.301 | 597.963 | 26.734 | 27.832 | 1265.272 | 27.489 | 27.742 | 38.173 | 24.001 | 3 | 3.8 | 0 | 0.4 | 0.3
5361 | 30/07/2025 12:15:37.915 | 97.512 | 83 | 100 | 70 | 51 | 29.186 | 9.197 | 7.123 | 132.98 | 31.335 | 28.697 | 29.28 | 597.898 | 26.714 | 27.836 | 1257.625 | 27.495 | 27.744 | 38.382 | 27.001 | 3.5 | 2.6 | 0.3 | 0.6 | 0.4
5362 | 30/07/2025 12:15:39.551 | 97.464 | 84 | 100 | 70 | 52 | 32.484 | 9.13 | 7.135 | 133.334 | 31.367 | 28.694 | 29.29 | 598.102 | 26.734 | 27.835 | 1252.942 | 27.497 | 27.727 | 38.137 | 27.001 | 3.5 | 5.4 | 0.3 | 1.5 | 0.4
5363 | 30/07/2025 12:15:41.186 | 97.272 | 84 | 100 | 70 | 52 | 32.756 | 9.282 | 7.133 | 133.145 | 31.342 | 28.691 | 29.259 | 598.026 | 26.726 | 27.824 | 1257.025 | 27.501 | 27.769 | 38.464 | 27.001 | 3.5 | 5.4 | 0.3 | 1.5 | 0.4
5364 | 30/07/2025 12:15:42.820 | 96.6 | 83 | 100 | 69 | 52 | 29.086 | 8.994 | 7.151 | 133.057 | 31.344 | 28.656 | 29.279 | 598.017 | 26.744 | 27.829 | 1258.636 | 27.459 | 27.758 | 38.308 | 28.001 | 2.2 | 4.6 | 1 | 1.1 | 0.3
5365 | 30/07/2025 12:15:44.455 | 96.624 | 83 | 100 | 70 | 52 | 30.657 | 9.133 | 7.152 | 133.055 | 31.355 | 28.695 | 29.292 | 598.064 | 26.739 | 27.828 | 1249.293 | 27.493 | 27.752 | 38.385 | 28.001 | 2.2 | 3.9 | 1 | 0.8 | 0.3
5366 | 30/07/2025 12:15:46.090 | 96.312 | 84 | 100 | 70 | 51 | 30.144 | 9.209 | 7.152 | 132.949 | 31.353 | 28.703 | 29.284 | 597.923 | 26.75 | 27.859 | 1248.838 | 27.484 | 27.732 | 38.248 | 22.001 | 2.9 | 5.1 | 0.6 | 1.4 | 0.3
5367 | 30/07/2025 12:15:47.725 | 96.528 | 84 | 100 | 70 | 52 | 29.616 | 9.289 | 7.151 | 133.291 | 31.345 | 28.701 | 29.283 | 597.948 | 26.75 | 27.846 | 1247.459 | 27.502 | 27.743 | 38.996 | 22.001 | 2.9 | 3.8 | 0.6 | 0 | 0.3
5368 | 30/07/2025 12:15:49.359 | 95.928 | 82 | 100 | 70 | 52 | 32.699 | 9.134 | 7.151 | 133.168 | 31.325 | 28.688 | 29.253 | 597.921 | 26.742 | 27.86 | 1257.304 | 27.47 | 27.768 | 40.08 | 20.001 | 2.7 | 5.6 | 0.6 | 0.5 | 0.3
5369 | 30/07/2025 12:15:51.005 | 96.024 | 83 | 100 | 70 | 53 | 32.445 | 8.988 | 7.185 | 133.303 | 31.335 | 28.672 | 29.289 | 598.089 | 26.745 | 27.839 | 1262.53 | 27.482 | 27.742 | 40.234 | 20.001 | 2.7 | 5.6 | 0.6 | 0.5 | 0.3
5370 | 30/07/2025 12:15:52.639 | 95.784 | 83 | 100 | 70 | 52 | 28.785 | 8.993 | 7.134 | 134.294 | 31.315 | 28.709 | 29.297 | 597.982 | 26.737 | 27.858 | 1259.518 | 27.517 | 27.754 | 38.413 | 20.001 | 2.7 | 4 | 0.6 | 0.1 | 0.3
5371 | 30/07/2025 12:15:54.276 | 96.312 | 83 | 100 | 71 | 52 | 31.188 | 9.13 | 7.137 | 134.696 | 31.334 | 28.692 | 29.289 | 597.894 | 26.742 | 27.864 | 1262.217 | 27.496 | 27.731 | 38.317 | 27.001 | 3.6 | 4.7 | 0.1 | 0.5 | 0.2
5372 | 30/07/2025 12:15:55.911 | 95.856 | 84 | 100 | 70 | 51 | 29.584 | 9.131 | 7.15 | 134.659 | 31.33 | 28.703 | 29.275 | 598.144 | 26.743 | 27.857 | 1262.622 | 27.491 | 27.76 | 40.056 | 27.001 | 3.6 | 4.4 | 0.1 | 0.6 | 0.2
5373 | 30/07/2025 12:15:57.545 | 96.456 | 83 | 99 | 70 | 52 | 29.963 | 9.132 | 7.144 | 134.682 | 31.361 | 28.675 | 29.254 | 597.902 | 26.765 | 27.853 | 1269.168 | 27.459 | 27.744 | 40.147 | 23.001 | 2.7 | 4.8 | 0.6 | 0.6 | 0.2
5374 | 30/07/2025 12:15:59.181 | 96.432 | 82 | 100 | 70 | 52 | 32.725 | 9.417 | 7.134 | 134.605 | 31.359 | 28.681 | 29.301 | 598.041 | 26.733 | 27.839 | 1267.403 | 27.498 | 27.76 | 40.202 | 23.001 | 2.7 | 4.8 | 0.6 | 0.6 | 0.2
5375 | 30/07/2025 12:16:00.816 | 96.456 | 84 | 100 | 71 | 52 | 31.838 | 9.021 | 7.135 | 134.538 | 31.348 | 28.694 | 29.287 | 597.818 | 26.728 | 27.855 | 1262.054 | 27.496 | 27.742 | 40.183 | 23.001 | 2.7 | 5.3 | 0.6 | 0 | 0.2
5376 | 30/07/2025 12:16:02.450 | 96.648 | 84 | 100 | 71 | 52 | 28.573 | 9.211 | 7.135 | 134.825 | 31.373 | 28.698 | 29.284 | 598.136 | 26.752 | 27.84 | 1261.216 | 27.486 | 27.735 | 39.845 | 26.001 | 2.3 | 3.6 | 0.6 | 0.5 | 0.2
5377 | 30/07/2025 12:16:04.085 | 96.6 | 84 | 100 | 70 | 53 | 32.737 | 9.134 | 7.135 | 134.753 | 31.362 | 28.685 | 29.262 | 598.053 | 26.729 | 27.847 | 1261.295 | 27.466 | 27.738 | 40.092 | 26.001 | 2.3 | 6.1 | 0.6 | 0.6 | 0.2
5378 | 30/07/2025 12:16:05.721 | 96.456 | 84 | 100 | 72 | 53 | 29.025 | 9.133 | 7.132 | 134.637 | 31.355 | 28.676 | 29.29 | 598.075 | 26.742 | 27.844 | 1266.952 | 27.454 | 27.753 | 40.201 | 28.001 | 3.4 | 3.7 | 0.7 | 0 | 0.2
5379 | 30/07/2025 12:16:07.355 | 96.168 | 84 | 100 | 71 | 52 | 30.716 | 9.441 | 7.134 | 133.037 | 31.356 | 28.699 | 29.291 | 597.915 | 26.735 | 27.854 | 1274.446 | 27.51 | 27.756 | 40.222 | 28.001 | 3.4 | 3.7 | 0.7 | 0 | 0.2
5380 | 30/07/2025 12:16:08.990 | 96.144 | 84 | 100 | 69 | 52 | 32.851 | 9.141 | 7.137 | 134.545 | 31.354 | 28.694 | 29.281 | 597.969 | 26.749 | 27.835 | 1276.829 | 27.49 | 27.734 | 39.171 | 28.001 | 3.4 | 5.6 | 0.7 | 0 | 0.2
5381 | 30/07/2025 12:16:10.626 | 95.544 | 84 | 100 | 70 | 53 | 31.328 | 9.046 | 7.133 | 134.551 | 31.354 | 28.699 | 29.279 | 598.227 | 26.721 | 27.838 | 1287.029 | 27.49 | 27.758 | 38.178 | 26.001 | 3.1 | 5.2 | 0.6 | 0.5 | 0.1
5382 | 30/07/2025 12:16:12.260 | 94.872 | 83 | 100 | 71 | 52 | 32.617 | 8.984 | 7.134 | 134.711 | 31.368 | 28.685 | 29.264 | 598.004 | 26.746 | 27.846 | 1282.696 | 27.465 | 27.75 | 38.375 | 26.001 | 3.1 | 7 | 0.6 | 0.5 | 0.1
5383 | 30/07/2025 12:16:13.897 | 94.632 | 84 | 100 | 70 | 52 | 32.448 | 9.136 | 7.132 | 134.678 | 31.337 | 28.678 | 29.264 | 597.904 | 26.728 | 27.814 | 1274.93 | 27.483 | 27.749 | 38.453 | 28.001 | 3.1 | 2.3 | 0.1 | 0.8 | 0.1
5384 | 30/07/2025 12:16:15.535 | 94.584 | 84 | 99 | 71 | 52 | 28.803 | 8.985 | 7.137 | 134.468 | 31.346 | 28.698 | 29.295 | 597.907 | 26.73 | 27.83 | 1267.16 | 27.495 | 27.744 | 38.393 | 28.001 | 3.1 | 7.1 | 0.1 | 0.5 | 0.1
5385 | 30/07/2025 12:16:17.171 | 94.56 | 82 | 99 | 70 | 52 | 31.195 | 9.219 | 7.133 | 134.717 | 31.355 | 28.696 | 29.282 | 597.907 | 26.742 | 27.823 | 1267.143 | 27.492 | 27.733 | 38.262 | 28.001 | 3.1 | 7.1 | 0.1 | 0.5 | 0.1
5386 | 30/07/2025 12:16:18.806 | 94.56 | 82 | 100 | 71 | 52 | 32.912 | 9.129 | 7.135 | 134.739 | 31.333 | 28.701 | 29.278 | 598.099 | 26.745 | 27.837 | 1276.717 | 27.495 | 27.771 | 38.519 | 24.001 | 2.4 | 4.6 | 1.1 | 0.5 | 0.2
5387 | 30/07/2025 12:16:20.441 | 94.944 | 83 | 100 | 71 | 52 | 30.812 | 9.214 | 7.135 | 133.957 | 31.33 | 28.66 | 29.26 | 597.935 | 26.751 | 27.846 | 1274.869 | 27.462 | 27.742 | 38.427 | 24.001 | 2.4 | 4.4 | 1.1 | 1.6 | 0.2
5388 | 30/07/2025 12:16:22.077 | 95.472 | 83 | 100 | 70 | 54 | 32.722 | 9.283 | 7.135 | 133.013 | 31.337 | 28.68 | 29.274 | 598.116 | 26.743 | 27.854 | 1276.611 | 27.487 | 27.749 | 38.435 | 23.001 | 3 | 3.8 | 0 | 1.3 | 0.2
5389 | 30/07/2025 12:16:23.711 | 95.808 | 84 | 100 | 70 | 53 | 31.992 | 9.303 | 7.136 | 133.191 | 31.328 | 28.694 | 29.292 | 597.985 | 26.766 | 27.85 | 1272.568 | 27.497 | 27.735 | 38.44 | 23.001 | 3 | 4.1 | 0 | 1.1 | 0.2
5390 | 30/07/2025 12:16:25.347 | 96.384 | 84 | 100 | 71 | 52 | 28.741 | 8.986 | 7.118 | 133.398 | 31.335 | 28.693 | 29.281 | 598.087 | 26.745 | 27.851 | 1277.307 | 27.499 | 27.747 | 38.199 | 23.001 | 3 | 4.1 | 0 | 1.1 | 0.2
5391 | 30/07/2025 12:16:26.981 | 96.456 | 83 | 100 | 70 | 52 | 31.861 | 9.289 | 7.121 | 133.079 | 31.321 | 28.682 | 29.249 | 597.966 | 26.74 | 27.863 | 1277.156 | 27.464 | 27.757 | 38.472 | 22.001 | 2.9 | 4.5 | 0.9 | 0.6 | 0.1
5392 | 30/07/2025 12:16:28.617 | 96.36 | 84 | 100 | 70 | 53 | 32.913 | 8.987 | 7.132 | 133.018 | 31.347 | 28.675 | 29.297 | 598.006 | 26.736 | 27.848 | 1274.675 | 27.475 | 27.745 | 38.51 | 22.001 | 2.9 | 3.3 | 0.9 | 0.7 | 0.1
5393 | 30/07/2025 12:16:30.253 | 96.624 | 84 | 100 | 70 | 52 | 30.653 | 8.983 | 7.136 | 133.069 | 31.346 | 28.691 | 29.306 | 598 | 26.75 | 27.846 | 1276.972 | 27.501 | 27.735 | 38.579 | 28.001 | 1.6 | 2.1 | 0 | 0.3 | 0.2
5394 | 30/07/2025 12:16:31.889 | 96.864 | 84 | 100 | 70 | 53 | 32.825 | 9.136 | 7.151 | 133.03 | 31.352 | 28.702 | 29.297 | 599.285 | 26.744 | 27.851 | 1276.054 | 27.498 | 27.736 | 38.295 | 28.001 | 1.6 | 5.5 | 0 | 0 | 0.2
5395 | 30/07/2025 12:16:33.526 | 96.816 | 84 | 100 | 69 | 52 | 31.325 | 9.178 | 7.135 | 133.246 | 31.344 | 28.699 | 29.269 | 600.601 | 26.747 | 27.854 | 1277.203 | 27.494 | 27.741 | 38.131 | 23.001 | 2.9 | 4.2 | 0.9 | 0 | 0.3
5396 | 30/07/2025 12:16:35.161 | 96.696 | 84 | 100 | 70 | 53 | 28.787 | 9.23 | 7.134 | 133.345 | 31.367 | 28.683 | 29.272 | 600.581 | 26.748 | 27.842 | 1279.397 | 27.455 | 27.742 | 38.395 | 23.001 | 2.9 | 4.2 | 0.9 | 0 | 0.3
5397 | 30/07/2025 12:16:36.795 | 97.008 | 84 | 100 | 69 | 53 | 32.167 | 9.131 | 7.151 | 133.22 | 31.358 | 28.676 | 29.287 | 600.57 | 26.742 | 27.849 | 1277.167 | 27.505 | 27.76 | 38.454 | 23.001 | 2.9 | 5.1 | 0.9 | 0.5 | 0.3
5398 | 30/07/2025 12:16:38.434 | 97.416 | 85 | 100 | 70 | 53 | 32.888 | 9.138 | 7.152 | 132.937 | 31.355 | 28.696 | 29.268 | 600.403 | 26.741 | 27.855 | 1269.32 | 27.488 | 27.736 | 38.239 | 23.001 | 3.4 | 6.6 | 0.9 | 0.2 | 0.3
5399 | 30/07/2025 12:16:40.073 | 97.416 | 85 | 100 | 71 | 52 | 31.229 | 9.137 | 7.15 | 133.176 | 31.341 | 28.692 | 29.288 | 600.295 | 26.734 | 27.837 | 1267.355 | 27.508 | 27.741 | 38.332 | 23.001 | 3.4 | 4.6 | 0.9 | 1.3 | 0.3
5400 | 30/07/2025 12:16:41.708 | 97.176 | 84 | 100 | 70 | 53 | 32.899 | 8.987 | 7.153 | 133.439 | 31.346 | 28.691 | 29.267 | 600.519 | 26.736 | 27.853 | 1271.997 | 27.477 | 27.754 | 38.247 | 24.001 | 5 | 4.8 | 0.4 | 0.5 | 0.2
5401 | 30/07/2025 12:16:43.343 | 96.096 | 84 | 100 | 69 | 53 | 30.644 | 9.03 | 7.149 | 133.325 | 31.361 | 28.674 | 29.282 | 600.62 | 26.727 | 27.836 | 1272.261 | 27.461 | 27.754 | 38.355 | 24.001 | 5 | 4.8 | 0.4 | 0.5 | 0.2
5402 | 30/07/2025 12:16:44.979 | 96.312 | 85 | 100 | 70 | 52 | 29.083 | 9.225 | 7.15 | 132.892 | 31.348 | 28.694 | 29.288 | 600.49 | 26.732 | 27.845 | 1267.468 | 27.502 | 27.749 | 38.492 | 24.001 | 5 | 3.5 | 0.4 | 0.2 | 0.2
5403 | 30/07/2025 12:16:46.613 | 96.12 | 84 | 100 | 70 | 52 | 32.458 | 9.293 | 7.136 | 133.534 | 31.353 | 28.699 | 29.293 | 601.294 | 26.756 | 27.841 | 1269.522 | 27.488 | 27.726 | 40.145 | 24.001 | 3.3 | 4.3 | 0.6 | 0.8 | 0.3
5404 | 30/07/2025 12:16:48.248 | 96.528 | 83 | 100 | 71 | 53 | 32.712 | 9.291 | 7.133 | 134.72 | 31.343 | 28.692 | 29.278 | 600.544 | 26.731 | 27.81 | 1260.417 | 27.501 | 27.764 | 39.849 | 24.001 | 3.3 | 3.3 | 0.6 | 0.6 | 0.3
5405 | 30/07/2025 12:16:49.883 | 96.48 | 85 | 100 | 70 | 53 | 31.696 | 9.236 | 7.098 | 134.748 | 31.366 | 28.692 | 29.277 | 601.991 | 26.74 | 27.813 | 1255.693 | 27.484 | 27.75 | 40.145 | 25.001 | 2.6 | 4.6 | 0.6 | 0.5 | 0.4
5406 | 30/07/2025 12:16:51.519 | 96.696 | 84 | 100 | 71 | 52 | 32.921 | 9.134 | 7.085 | 133.998 | 31.341 | 28.67 | 29.287 | 601.99 | 26.728 | 27.829 | 1260.708 | 27.489 | 27.75 | 40.366 | 25.001 | 2.6 | 4.7 | 0.6 | 0.9 | 0.4
5407 | 30/07/2025 12:16:53.152 | 96.84 | 85 | 100 | 70 | 52 | 30.165 | 9.143 | 7.136 | 132.939 | 31.349 | 28.694 | 29.29 | 600.526 | 26.747 | 27.84 | 1273.873 | 27.497 | 27.748 | 40.286 | 25.001 | 2.6 | 4.7 | 0.6 | 0.9 | 0.4
5408 | 30/07/2025 12:16:54.786 | 97.344 | 85 | 100 | 71 | 52 | 29.604 | 9.134 | 7.122 | 133.241 | 31.338 | 28.697 | 29.292 | 600.413 | 26.741 | 27.842 | 1276.336 | 27.491 | 27.727 | 40.18 | 27.001 | 2.8 | 4.2 | 1.2 | 0.4 | 0.3
5409 | 30/07/2025 12:16:56.420 | 97.248 | 86 | 100 | 70 | 53 | 32.649 | 9.133 | 7.122 | 133.008 | 31.33 | 28.7 | 29.272 | 602.081 | 26.747 | 27.871 | 1280.776 | 27.501 | 27.766 | 38.454 | 27.001 | 2.8 | 4.5 | 1.2 | 0 | 0.3
5410 | 30/07/2025 12:16:58.053 | 96.912 | 84 | 100 | 70 | 52 | 28.895 | 9.19 | 7.119 | 133.123 | 31.334 | 28.679 | 29.27 | 602.108 | 26.756 | 27.856 | 1279.174 | 27.476 | 27.763 | 38.364 | 28.001 | 3.2 | 3.2 | 0.9 | 0.5 | 0.3
5411 | 30/07/2025 12:16:59.688 | 96.696 | 84 | 100 | 70 | 52 | 32.235 | 9.132 | 7.119 | 133.102 | 31.314 | 28.675 | 29.284 | 600.53 | 26.747 | 27.855 | 1279.335 | 27.481 | 27.741 | 38.42 | 28.001 | 3.2 | 4.3 | 0.9 | 0 | 0.3
5412 | 30/07/2025 12:17:01.322 | 97.2 | 86 | 100 | 70 | 52 | 32.893 | 8.993 | 7.135 | 132.967 | 31.347 | 28.697 | 29.286 | 600.4 | 26.741 | 27.851 | 1279.511 | 27.493 | 27.735 | 38.409 | 28.001 | 3.2 | 4.3 | 0.9 | 0 | 0.3
5413 | 30/07/2025 12:17:02.957 | 96.6 | 84 | 100 | 70 | 53 | 29.686 | 8.981 | 7.133 | 133.273 | 31.345 | 28.692 | 29.291 | 600.478 | 26.748 | 27.86 | 1277.235 | 27.506 | 27.752 | 38.361 | 24.001 | 2.4 | 3.3 | 0.6 | 1 | 0.3
5414 | 30/07/2025 12:17:04.593 | 96.72 | 85 | 100 | 70 | 53 | 30.04 | 9.008 | 7.135 | 133.298 | 31.36 | 28.681 | 29.25 | 600.6 | 26.745 | 27.858 | 1289.43 | 27.481 | 27.757 | 38.395 | 24.001 | 2.4 | 3.8 | 0.6 | 0.5 | 0.3
5415 | 30/07/2025 12:17:06.229 | 97.008 | 84 | 100 | 70 | 53 | 30.788 | 8.989 | 7.122 | 133.106 | 31.331 | 28.68 | 29.271 | 601.942 | 26.743 | 27.86 | 1283.361 | 27.484 | 27.761 | 38.614 | 27.001 | 3.5 | 3.8 | 0.6 | 0.9 | 0.2
5416 | 30/07/2025 12:17:07.863 | 97.272 | 86 | 100 | 70 | 52 | 29.045 | 8.987 | 7.123 | 133.191 | 31.356 | 28.684 | 29.303 | 601.927 | 26.769 | 27.86 | 1271.91 | 27.488 | 27.748 | 38.485 | 27.001 | 3.5 | 3.2 | 0.6 | 0.7 | 0.2
5417 | 30/07/2025 12:17:09.497 | 96.864 | 84 | 100 | 70 | 52 | 32.472 | 8.988 | 7.122 | 133.056 | 31.367 | 28.698 | 29.303 | 601.903 | 26.743 | 27.843 | 1279.032 | 27.494 | 27.749 | 38.334 | 28.001 | 2.4 | 4.9 | 0.9 | 0 | 0.2
5418 | 30/07/2025 12:17:11.131 | 96.504 | 83 | 100 | 71 | 53 | 32.741 | 9.131 | 7.122 | 133.241 | 31.362 | 28.704 | 29.273 | 601.959 | 26.746 | 27.852 | 1277.351 | 27.497 | 27.741 | 38.402 | 28.001 | 2.4 | 4.9 | 0.9 | 0 | 0.2
5419 | 30/07/2025 12:17:12.764 | 96.216 | 84 | 100 | 70 | 52 | 29.13 | 9.223 | 7.121 | 133.281 | 31.367 | 28.683 | 29.256 | 602.152 | 26.735 | 27.832 | 1287.705 | 27.46 | 27.746 | 38.601 | 28.001 | 2.4 | 6.2 | 0.9 | 1 | 0.2
5420 | 30/07/2025 12:17:14.398 | 96.288 | 84 | 100 | 71 | 52 | 30.663 | 9.293 | 7.122 | 133.186 | 31.347 | 28.674 | 29.288 | 602.113 | 26.729 | 27.83 | 1285.601 | 27.508 | 27.761 | 38.354 | 25.001 | 2.9 | 3.8 | 0 | 0.5 | 0.2
5421 | 30/07/2025 12:17:16.033 | 96 | 83 | 100 | 70 | 51 | 30.126 | 9.223 | 7.122 | 132.935 | 31.369 | 28.699 | 29.299 | 601.881 | 26.743 | 27.83 | 1281.911 | 27.499 | 27.756 | 38.315 | 25.001 | 2.9 | 3.3 | 0 | 0.6 | 0.2
5422 | 30/07/2025 12:17:17.669 | 96.192 | 83 | 100 | 69 | 53 | 29.54 | 9.14 | 7.134 | 133.057 | 31.352 | 28.701 | 29.291 | 601.85 | 26.737 | 27.837 | 1282.099 | 27.515 | 27.741 | 38.345 | 23.001 | 1.9 | 5.4 | 1.2 | 0.5 | 0.2
5423 | 30/07/2025 12:17:19.304 | 97.248 | 85 | 100 | 70 | 53 | 32.605 | 8.846 | 7.136 | 133.262 | 31.358 | 28.689 | 29.277 | 601.979 | 26.739 | 27.829 | 1267.496 | 27.487 | 27.752 | 38.113 | 23.001 | 1.9 | 5.4 | 1.2 | 0.5 | 0.2
5424 | 30/07/2025 12:17:20.940 | 97.776 | 85 | 100 | 70 | 53 | 32.365 | 8.99 | 7.131 | 133.127 | 31.359 | 28.679 | 29.275 | 603.329 | 26.723 | 27.812 | 1268.412 | 27.464 | 27.753 | 38.503 | 23.001 | 1.9 | 5.2 | 1.2 | 0.8 | 0.2
5425 | 30/07/2025 12:17:22.574 | 98.4 | 88 | 100 | 70 | 53 | 28.831 | 9.136 | 7.134 | 132.962 | 31.343 | 28.687 | 29.302 | 603.255 | 26.731 | 27.835 | 1267.119 | 27.503 | 27.754 | 38.507 | 30.001 | 2.8 | 3.2 | 0.2 | 0 | 0.2
5426 | 30/07/2025 12:17:24.209 | 98.544 | 84 | 100 | 70 | 54 | 31.105 | 9.131 | 7.135 | 133.175 | 31.363 | 28.696 | 29.281 | 603.117 | 26.75 | 27.816 | 1267.064 | 27.484 | 27.738 | 38.419 | 30.001 | 2.8 | 4.6 | 0.2 | 1 | 0.2
5427 | 30/07/2025 12:17:25.844 | 98.592 | 86 | 100 | 71 | 53 | 29.5 | 9.045 | 7.135 | 131.657 | 31.339 | 28.69 | 29.275 | 603.015 | 26.737 | 27.84 | 1268.173 | 27.492 | 27.736 | 38.426 | 22.001 | 2 | 3.9 | 0.1 | 0.8 | 0.4
5428 | 30/07/2025 12:17:27.479 | 99.048 | 88 | 100 | 70 | 52 | 30.065 | 9.034 | 7.134 | 131.848 | 31.364 | 28.692 | 29.278 | 602.098 | 26.745 | 27.836 | 1272.657 | 27.481 | 27.752 | 38.467 | 22.001 | 2 | 4.2 | 0.1 | 0.9 | 0.4
5429 | 30/07/2025 12:17:29.114 | 98.952 | 87 | 100 | 70 | 52 | 32.787 | 9.003 | 7.133 | 131.817 | 31.326 | 28.662 | 29.282 | 602.106 | 26.754 | 27.858 | 1276.895 | 27.479 | 27.791 | 38.448 | 22.001 | 2 | 4.2 | 0.1 | 0.9 | 0.4
5430 | 30/07/2025 12:17:30.748 | 98.904 | 88 | 100 | 70 | 52 | 31.956 | 8.986 | 7.153 | 133.041 | 31.33 | 28.692 | 29.283 | 601.814 | 26.752 | 27.858 | 1284.582 | 27.501 | 27.759 | 38.491 | 29.001 | 2.7 | 5.2 | 0.9 | 0.5 | 0.5
5431 | 30/07/2025 12:17:32.381 | 99.072 | 86 | 100 | 70 | 52 | 28.703 | 9.086 | 7.151 | 133.155 | 31.341 | 28.689 | 29.283 | 601.904 | 26.727 | 27.855 | 1290.414 | 27.499 | 27.725 | 38.332 | 29.001 | 2.7 | 5.6 | 0.9 | 0.8 | 0.5
5432 | 30/07/2025 12:17:34.017 | 99.096 | 86 | 100 | 70 | 52 | 32.757 | 9.01 | 7.153 | 133.274 | 31.333 | 28.689 | 29.276 | 601.829 | 26.762 | 27.873 | 1289.917 | 27.489 | 27.738 | 38.274 | 26.001 | 2.5 | 6.7 | 1.2 | 0.1 | 0.5
5433 | 30/07/2025 12:17:35.652 | 99 | 89 | 100 | 72 | 52 | 29.138 | 9.134 | 7.15 | 133.079 | 31.332 | 28.69 | 29.273 | 602.15 | 26.751 | 27.848 | 1278.169 | 27.478 | 27.759 | 38.585 | 26.001 | 2.5 | 4 | 1.2 | 0 | 0.5
5434 | 30/07/2025 12:17:37.286 | 99.144 | 88 | 100 | 71 | 54 | 30.645 | 8.986 | 7.151 | 132.862 | 31.344 | 28.672 | 29.283 | 601.884 | 26.745 | 27.852 | 1274.778 | 27.482 | 27.75 | 38.593 | 26.001 | 2.5 | 4 | 1.2 | 0 | 0.5
5435 | 30/07/2025 12:17:38.918 | 98.976 | 86 | 100 | 69 | 53 | 32.803 | 9.289 | 7.134 | 133.218 | 31.361 | 28.699 | 29.297 | 601.833 | 26.744 | 27.844 | 1272.514 | 27.496 | 27.745 | 38.255 | 27.001 | 2.8 | 2.6 | 1.2 | 0 | 0.3
5436 | 30/07/2025 12:17:40.551 | 98.448 | 88 | 100 | 70 | 53 | 31.439 | 8.949 | 7.134 | 133.199 | 31.342 | 28.7 | 29.29 | 601.951 | 26.748 | 27.853 | 1267.21 | 27.502 | 27.741 | 38.282 | 27.001 | 2.8 | 4.8 | 1.2 | 0.8 | 0.3
5437 | 30/07/2025 12:17:42.185 | 98.136 | 86 | 100 | 70 | 53 | 32.642 | 8.906 | 7.134 | 133.213 | 31.358 | 28.689 | 29.289 | 602.012 | 26.738 | 27.839 | 1262.819 | 27.49 | 27.917 | 38.061 | 29.001 | 2 | 2.7 | 0.6 | 0.2 | 0.3
5438 | 30/07/2025 12:17:43.821 | 97.656 | 85 | 100 | 70 | 53 | 32.503 | 9.208 | 7.119 | 133.113 | 31.353 | 28.682 | 29.263 | 601.972 | 26.738 | 27.851 | 1267.601 | 27.466 | 27.805 | 38.457 | 29.001 | 2 | 5.8 | 0.6 | 0.5 | 0.3
5439 | 30/07/2025 12:17:45.457 | 97.632 | 84 | 100 | 71 | 52 | 28.831 | 8.984 | 7.07 | 134.435 | 31.375 | 28.681 | 29.299 | 601.842 | 26.755 | 27.845 | 1249.483 | 27.484 | 27.759 | 38.402 | 27.001 | 1.7 | 4.3 | 1.5 | 0.2 | 0.4
5440 | 30/07/2025 12:17:47.091 | 97.584 | 85 | 100 | 68 | 53 | 31.29 | 9.135 | 7.068 | 134.464 | 31.36 | 28.699 | 29.298 | 602.1 | 26.738 | 27.844 | 1254.279 | 27.504 | 27.756 | 38.404 | 27.001 | 1.7 | 4.3 | 1.5 | 0.2 | 0.4
5441 | 30/07/2025 12:17:48.727 | 97.416 | 85 | 100 | 70 | 53 | 32.909 | 9.133 | 7.069 | 134.756 | 31.346 | 28.689 | 29.276 | 601.908 | 26.744 | 27.856 | 1259.808 | 27.481 | 27.738 | 38.04 | 27.001 | 1.7 | 3 | 1.5 | 0 | 0.4
5442 | 30/07/2025 12:17:50.362 | 97.032 | 84 | 100 | 71 | 52 | 30.781 | 8.911 | 7.068 | 134.688 | 31.35 | 28.686 | 29.268 | 600.818 | 26.722 | 27.84 | 1259.967 | 27.474 | 27.758 | 38.178 | 31.001 | 1.9 | 2.3 | 0.7 | 0.6 | 0.4
5443 | 30/07/2025 12:17:51.997 | 97.368 | 85 | 100 | 71 | 53 | 32.749 | 8.984 | 7.071 | 134.711 | 31.343 | 28.661 | 29.269 | 600.429 | 26.733 | 27.844 | 1267.027 | 27.456 | 27.744 | 38.555 | 31.001 | 1.9 | 4 | 0.7 | 0.6 | 0.4
5444 | 30/07/2025 12:17:53.637 | 97.176 | 87 | 100 | 70 | 52 | 31.977 | 8.988 | 7.069 | 134.474 | 31.369 | 28.69 | 29.304 | 600.612 | 26.734 | 27.835 | 1264.658 | 27.499 | 27.754 | 38.342 | 27.001 | 3.1 | 4.2 | 0.2 | 0.5 | 0.3
5445 | 30/07/2025 12:17:55.270 | 97.152 | 85 | 100 | 71 | 53 | 28.741 | 9.141 | 7.071 | 134.262 | 31.345 | 28.703 | 29.282 | 601.869 | 26.714 | 27.833 | 1263.103 | 27.501 | 27.742 | 38.347 | 27.001 | 3.1 | 4.2 | 0.2 | 0.5 | 0.3
5446 | 30/07/2025 12:17:56.905 | 97.152 | 84 | 100 | 69 | 52 | 33.219 | 8.986 | 7.069 | 134.821 | 31.355 | 28.685 | 29.271 | 601.949 | 26.738 | 27.826 | 1262.825 | 27.487 | 27.733 | 38.313 | 27.001 | 3.1 | 3.1 | 0.2 | 0.9 | 0.3
5447 | 30/07/2025 12:17:58.540 | 97.32 | 84 | 100 | 71 | 53 | 32.952 | 9.188 | 7.068 | 134.572 | 31.358 | 28.679 | 29.272 | 602.183 | 26.739 | 27.814 | 1257.752 | 27.46 | 27.77 | 38.605 | 29.001 | 1.8 | 4.5 | 0 | 1.2 | 0.3
5448 | 30/07/2025 12:18:00.176 | 97.176 | 84 | 100 | 70 | 52 | 30.567 | 9.226 | 7.069 | 134.708 | 31.36 | 28.673 | 29.286 | 601.908 | 26.756 | 27.844 | 1257.57 | 27.471 | 27.748 | 38.469 | 29.001 | 1.8 | 2.5 | 0 | 0.3 | 0.3
5449 | 30/07/2025 12:18:01.810 | 97.032 | 84 | 100 | 71 | 53 | 32.841 | 8.99 | 7.135 | 134.49 | 31.333 | 28.699 | 29.274 | 601.994 | 26.745 | 27.83 | 1257.443 | 27.51 | 27.746 | 38.598 | 26.001 | 2.2 | 2.3 | 0.9 | 0 | 0.4
5450 | 30/07/2025 12:18:03.446 | 97.104 | 84 | 100 | 70 | 52 | 31.261 | 9.21 | 7.136 | 134.594 | 31.332 | 28.692 | 29.288 | 601.731 | 26.756 | 27.867 | 1254.705 | 27.491 | 27.741 | 38.237 | 26.001 | 2.2 | 3.2 | 0.9 | 0 | 0.4
5451 | 30/07/2025 12:18:05.085 | 96.84 | 85 | 100 | 70 | 52 | 28.803 | 9.276 | 7.134 | 134.888 | 31.341 | 28.694 | 29.279 | 602.077 | 26.753 | 27.841 | 1263.74 | 27.483 | 27.817 | 38.22 | 26.001 | 2.2 | 3.2 | 0.9 | 0 | 0.4
5452 | 30/07/2025 12:18:06.720 | 97.032 | 84 | 100 | 71 | 53 | 32.189 | 9.133 | 7.133 | 134.601 | 31.323 | 28.68 | 29.275 | 602.032 | 26.735 | 27.861 | 1258.693 | 27.483 | 27.762 | 38.533 | 24.001 | 2.5 | 4.1 | 0 | 0 | 0.4
5453 | 30/07/2025 12:18:08.354 | 96.504 | 84 | 100 | 71 | 51 | 28.707 | 9.128 | 7.132 | 134.649 | 31.337 | 28.68 | 29.293 | 602.049 | 26.735 | 27.839 | 1258.075 | 27.483 | 27.751 | 38.341 | 24.001 | 2.5 | 4.3 | 0 | 0.8 | 0.4
5454 | 30/07/2025 12:18:09.990 | 97.272 | 84 | 100 | 71 | 53 | 31.167 | 9.131 | 7.134 | 132.915 | 31.318 | 28.707 | 29.283 | 601.92 | 26.747 | 27.863 | 1247.189 | 27.501 | 27.743 | 38.404 | 34.001 | 1.1 | 3.6 | 0 | 0.4 | 0.4
5455 | 30/07/2025 12:18:11.625 | 96.696 | 84 | 100 | 70 | 53 | 32.864 | 8.91 | 7.172 | 133.358 | 31.359 | 28.692 | 29.289 | 601.894 | 26.753 | 27.856 | 1256.497 | 27.486 | 27.752 | 38.188 | 34.001 | 1.1 | 4.5 | 0 | 0.8 | 0.4
5456 | 30/07/2025 12:18:13.260 | 97.728 | 85 | 100 | 70 | 52 | 30.752 | 9.094 | 7.185 | 133.162 | 31.333 | 28.685 | 29.271 | 603.207 | 26.745 | 27.843 | 1264.154 | 27.484 | 27.951 | 38.458 | 34.001 | 1.1 | 4.5 | 0 | 0.8 | 0.4
5457 | 30/07/2025 12:18:14.895 | 97.224 | 84 | 100 | 72 | 52 | 29.074 | 9.253 | 7.186 | 133.062 | 31.352 | 28.667 | 29.285 | 603.116 | 26.739 | 27.847 | 1265.466 | 27.467 | 27.921 | 38.59 | 29.001 | 3.5 | 3.7 | 0 | 0.8 | 0.5
5458 | 30/07/2025 12:18:16.529 | 97.272 | 84 | 100 | 71 | 51 | 32.495 | 9.129 | 7.136 | 132.919 | 31.362 | 28.693 | 29.306 | 603.138 | 26.75 | 27.844 | 1279.311 | 27.496 | 27.752 | 38.31 | 29.001 | 3.5 | 5.5 | 0 | 0.4 | 0.5
5459 | 30/07/2025 12:18:18.164 | 97.008 | 86 | 100 | 70 | 53 | 28.727 | 9.135 | 7.137 | 132.839 | 31.362 | 28.696 | 29.287 | 601.717 | 26.749 | 27.846 | 1279.095 | 27.506 | 27.898 | 38.467 | 27.001 | 2.8 | 4.6 | 1 | 0 | 0.3
5460 | 30/07/2025 12:18:19.799 | 97.08 | 85 | 100 | 71 | 53 | 31.882 | 8.984 | 7.135 | 133.289 | 31.368 | 28.695 | 29.296 | 602.39 | 26.73 | 27.83 | 1289.54 | 27.495 | 27.75 | 38.177 | 27.001 | 2.8 | 4.9 | 1 | 0.8 | 0.3
5461 | 30/07/2025 12:18:21.434 | 96.984 | 84 | 100 | 69 | 54 | 32.911 | 8.841 | 7.134 | 132.999 | 31.345 | 28.681 | 29.268 | 603.103 | 26.732 | 27.843 | 1285.904 | 27.48 | 27.937 | 38.608 | 30.001 | 2.6 | 3.8 | 0.6 | 0.3 | 0.3
5462 | 30/07/2025 12:18:23.068 | 97.824 | 87 | 100 | 71 | 52 | 30.209 | 9.145 | 7.136 | 133.157 | 31.363 | 28.673 | 29.3 | 603.086 | 26.751 | 27.836 | 1279.462 | 27.476 | 27.915 | 38.479 | 30.001 | 2.6 | 3.8 | 0.6 | 0.3 | 0.3
5463 | 30/07/2025 12:18:24.704 | 97.968 | 86 | 100 | 71 | 54 | 29.573 | 8.993 | 7.089 | 132.99 | 31.354 | 28.706 | 29.289 | 602.403 | 26.732 | 27.823 | 1274.718 | 27.509 | 27.929 | 38.577 | 30.001 | 2.6 | 2.8 | 0.6 | 0 | 0.3
5464 | 30/07/2025 12:18:26.340 | 98.448 | 87 | 100 | 71 | 53 | 31.478 | 8.917 | 7.086 | 133.305 | 31.371 | 28.692 | 29.286 | 601.634 | 26.733 | 27.831 | 1269.718 | 27.497 | 27.897 | 38.339 | 29.001 | 2.8 | 4.2 | 0.6 | 0 | 0.3
5465 | 30/07/2025 12:18:27.977 | 98.568 | 88 | 100 | 71 | 52 | 28.822 | 9.127 | 7.128 | 133.122 | 31.348 | 28.695 | 29.264 | 601.97 | 26.725 | 27.83 | 1265.063 | 27.502 | 27.915 | 38.282 | 29.001 | 2.8 | 5.4 | 0.6 | 0 | 0.3
5466 | 30/07/2025 12:18:29.612 | 98.616 | 86 | 99 | 70 | 52 | 32.214 | 8.985 | 7.133 | 133.162 | 31.346 | 28.669 | 29.271 | 601.852 | 26.733 | 27.825 | 1266.629 | 27.46 | 27.927 | 38.533 | 26.001 | 2.3 | 4.9 | 0.9 | 0 | 0.2
5467 | 30/07/2025 12:18:31.248 | 99.048 | 89 | 100 | 70 | 52 | 32.913 | 9.135 | 7.134 | 133.094 | 31.351 | 28.689 | 29.305 | 602.036 | 26.727 | 27.805 | 1263.558 | 27.495 | 27.926 | 38.574 | 26.001 | 2.3 | 4.9 | 0.9 | 0 | 0.2
5468 | 30/07/2025 12:18:32.883 | 98.928 | 88 | 100 | 70 | 53 | 29.709 | 8.995 | 7.09 | 132.956 | 31.347 | 28.707 | 29.286 | 601.855 | 26.749 | 27.848 | 1256.354 | 27.504 | 27.928 | 38.381 | 26.001 | 2.3 | 3.3 | 0.9 | 0 | 0.2
5469 | 30/07/2025 12:18:34.518 | 99.6 | 88 | 100 | 70 | 53 | 30.325 | 8.929 | 7.086 | 133.213 | 31.355 | 28.695 | 29.288 | 602.036 | 26.756 | 27.845 | 1271.839 | 27.486 | 27.921 | 38.076 | 26.001 | 3.6 | 5.2 | 0.6 | 0.5 | 0.2
5470 | 30/07/2025 12:18:36.153 | 99.36 | 89 | 100 | 71 | 52 | 30.764 | 8.983 | 7.069 | 133.117 | 31.339 | 28.684 | 29.247 | 601.951 | 26.75 | 27.831 | 1277.233 | 27.48 | 27.936 | 38.353 | 26.001 | 3.6 | 4.6 | 0.6 | 0.8 | 0.2
5471 | 30/07/2025 12:18:37.788 | 99.648 | 89 | 100 | 70 | 51 | 29.109 | 8.982 | 7.069 | 133.209 | 31.359 | 28.669 | 29.279 | 601.955 | 26.736 | 27.834 | 1276.844 | 27.463 | 27.933 | 38.401 | 27.001 | 3.3 | 4.2 | 0.6 | 0.9 | 0.3
5472 | 30/07/2025 12:18:39.422 | 99.936 | 89 | 100 | 71 | 53 | 32.462 | 8.981 | 7.07 | 133.079 | 31.332 | 28.704 | 29.291 | 601.965 | 26.742 | 27.852 | 1279.939 | 27.511 | 27.939 | 38.365 | 27.001 | 3.3 | 2.4 | 0.6 | 0.3 | 0.3
5473 | 30/07/2025 12:18:41.056 | 99.792 | 88 | 100 | 71 | 52 | 32.723 | 9.211 | 7.072 | 132.978 | 31.316 | 28.687 | 29.284 | 601.722 | 26.751 | 27.858 | 1281.354 | 27.49 | 27.901 | 38.499 | 27.001 | 3.3 | 2.4 | 0.6 | 0.3 | 0.3
5474 | 30/07/2025 12:18:42.692 | 99.84 | 89 | 100 | 70 | 53 | 29.093 | 9.129 | 7.085 | 133.214 | 31.345 | 28.689 | 29.293 | 602.076 | 26.738 | 27.842 | 1282.045 | 27.485 | 27.93 | 38.271 | 25.001 | 1.2 | 4 | 0.6 | 1.1 | 0.3
5475 | 30/07/2025 12:18:44.327 | 100.128 | 88 | 100 | 70 | 52 | 32.896 | 9.131 | 7.07 | 133.16 | 31.347 | 28.681 | 29.252 | 601.998 | 26.752 | 27.855 | 1277.273 | 27.473 | 27.94 | 38.748 | 25.001 | 1.2 | 3.5 | 0.6 | 0.8 | 0.3
5476 | 30/07/2025 12:18:45.961 | 100.104 | 89 | 100 | 70 | 52 | 30.03 | 9.139 | 7.066 | 133.175 | 31.353 | 28.673 | 29.296 | 601.962 | 26.737 | 27.852 | 1271.823 | 27.488 | 27.936 | 38.481 | 27.001 | 3.4 | 4.6 | 0.6 | 0.5 | 0.2
5477 | 30/07/2025 12:18:47.595 | 100.08 | 86 | 100 | 70 | 53 | 29.507 | 9.133 | 7.069 | 132.836 | 31.343 | 28.706 | 29.286 | 601.824 | 26.746 | 27.855 | 1279.28 | 27.491 | 27.921 | 38.578 | 27.001 | 3.4 | 4.8 | 0.6 | 0.1 | 0.2
5478 | 30/07/2025 12:18:49.230 | 100.008 | 88 | 100 | 70 | 53 | 32.618 | 9.276 | 7.069 | 133.184 | 31.37 | 28.687 | 29.289 | 601.925 | 26.763 | 27.843 | 1283.411 | 27.487 | 27.903 | 38.199 | 27.001 | 3.4 | 4.8 | 0.6 | 0.1 | 0.2
5479 | 30/07/2025 12:18:50.862 | 99.504 | 88 | 100 | 70 | 53 | 32.507 | 9.138 | 7.085 | 133.191 | 31.362 | 28.691 | 29.277 | 602.079 | 26.747 | 27.842 | 1279.978 | 27.497 | 27.945 | 38.472 | 27.001 | 2.1 | 3.1 | 1.3 | 0.5 | 0.2
5480 | 30/07/2025 12:18:52.496 | 99.696 | 90 | 100 | 70 | 53 | 28.736 | 9.26 | 7.086 | 134.155 | 31.364 | 28.671 | 29.29 | 602.994 | 26.746 | 27.854 | 1279.791 | 27.464 | 27.931 | 38.465 | 27.001 | 2.1 | 4.5 | 1.3 | 0.8 | 0.2
5481 | 30/07/2025 12:18:54.132 | 99.6 | 89 | 100 | 70 | 52 | 32.875 | 8.99 | 7.087 | 134.41 | 31.343 | 28.676 | 29.298 | 603.122 | 26.73 | 27.847 | 1279.288 | 27.505 | 27.94 | 38.317 | 28.001 | 3.9 | 5.4 | 0.6 | 0.6 | 0.2
5482 | 30/07/2025 12:18:55.766 | 99.384 | 84 | 100 | 71 | 52 | 29.528 | 8.847 | 7.123 | 134.575 | 31.35 | 28.694 | 29.271 | 603.059 | 26.743 | 27.852 | 1286.707 | 27.498 | 27.898 | 38.383 | 28.001 | 3.9 | 3.5 | 0.6 | 0.7 | 0.2
5483 | 30/07/2025 12:18:57.402 | 99.336 | 88 | 100 | 70 | 52 | 30.18 | 9.207 | 7.121 | 134.844 | 31.369 | 28.694 | 29.3 | 603.254 | 26.73 | 27.842 | 1294.517 | 27.488 | 27.923 | 38.178 | 22.001 | 2 | 2.9 | 1 | 0.8 | 0.1
5484 | 30/07/2025 12:18:59.036 | 99.264 | 89 | 100 | 72 | 53 | 32.794 | 8.995 | 7.12 | 134.456 | 31.34 | 28.672 | 29.255 | 603.066 | 26.743 | 27.84 | 1277.36 | 27.469 | 27.93 | 38.636 | 22.001 | 2 | 2.9 | 1 | 0.8 | 0.1
5485 | 30/07/2025 12:19:00.670 | 98.856 | 86 | 100 | 72 | 52 | 32.027 | 8.909 | 7.06 | 134.525 | 31.371 | 28.682 | 29.304 | 603.221 | 26.735 | 27.82 | 1271.94 | 27.474 | 27.92 | 38.391 | 22.001 | 2 | 4.1 | 1 | 0.7 | 0.1
5486 | 30/07/2025 12:19:02.303 | 98.856 | 88 | 100 | 71 | 53 | 28.778 | 9.262 | 7.058 | 134.428 | 31.334 | 28.701 | 29.289 | 603.214 | 26.711 | 27.813 | 1274.449 | 27.51 | 27.931 | 38.43 | 29.001 | 2.3 | 5.7 | 1.3 | 0 | 0.2
5487 | 30/07/2025 12:19:03.936 | 98.688 | 86 | 100 | 70 | 53 | 32.781 | 9.212 | 7.069 | 134.47 | 31.358 | 28.694 | 29.285 | 603.022 | 26.735 | 27.832 | 1264.471 | 27.488 | 27.898 | 38.37 | 29.001 | 2.3 | 4 | 1.3 | 0.6 | 0.2
5488 | 30/07/2025 12:19:05.568 | 98.856 | 87 | 100 | 70 | 52 | 29.21 | 9.224 | 7.069 | 134.582 | 31.337 | 28.694 | 29.331 | 603.299 | 26.741 | 27.823 | 1259.582 | 27.498 | 27.934 | 38.394 | 30.001 | 0.6 | 3.1 | 0.7 | 0.1 | 0.2
5489 | 30/07/2025 12:19:07.204 | 98.256 | 86 | 100 | 71 | 52 | 30.627 | 9.011 | 7.071 | 134.647 | 31.349 | 28.67 | 29.272 | 603.031 | 26.744 | 27.841 | 1262.968 | 27.452 | 27.928 | 38.375 | 30.001 | 0.6 | 3.1 | 0.7 | 0.1 | 0.2
5490 | 30/07/2025 12:19:08.839 | 97.848 | 86 | 100 | 70 | 51 | 32.871 | 9.136 | 7.134 | 134.648 | 31.349 | 28.688 | 29.471 | 603.355 | 26.737 | 27.83 | 1260.966 | 27.504 | 27.942 | 38.397 | 30.001 | 0.6 | 3.7 | 0.7 | 0.5 | 0.2
5491 | 30/07/2025 12:19:10.473 | 97.488 | 84 | 100 | 70 | 52 | 31.45 | 9.135 | 7.134 | 134.41 | 31.336 | 28.695 | 29.474 | 603.095 | 26.749 | 27.863 | 1257.407 | 27.5 | 27.927 | 38.331 | 24.001 | 4.4 | 3.9 | 0 | 0.5 | 0.2
5492 | 30/07/2025 12:19:12.114 | 97.152 | 84 | 100 | 71 | 52 | 32.661 | 9.139 | 7.133 | 134.634 | 31.328 | 28.697 | 29.285 | 603.165 | 26.76 | 27.846 | 1257.346 | 27.499 | 27.905 | 38.28 | 24.001 | 4.4 | 6 | 0 | 0.7 | 0.2
5493 | 30/07/2025 12:19:13.748 | 96.84 | 84 | 100 | 70 | 53 | 32.411 | 9.133 | 7.103 | 134.702 | 31.327 | 28.693 | 29.252 | 603.168 | 26.748 | 27.864 | 1267.456 | 27.477 | 27.932 | 38.486 | 32.001 | 4 | 2.7 | 1.2 | 0.7 | 0.2
5494 | 30/07/2025 12:19:15.383 | 96 | 83 | 100 | 71 | 52 | 28.857 | 9.131 | 7.085 | 134.611 | 31.334 | 28.672 | 29.275 | 603.12 | 26.737 | 27.857 | 1259.88 | 27.466 | 27.927 | 38.393 | 32.001 | 4 | 5.6 | 1.2 | 1 | 0.2
5495 | 30/07/2025 12:19:17.016 | 96.624 | 83 | 100 | 70 | 51 | 31.061 | 9.138 | 7.088 | 134.491 | 31.334 | 28.704 | 29.3 | 603.226 | 26.747 | 27.863 | 1262.088 | 27.509 | 27.932 | 38.467 | 32.001 | 4 | 5.6 | 1.2 | 1 | 0.2
5496 | 30/07/2025 12:19:18.654 | 96.696 | 83 | 100 | 70 | 53 | 32.863 | 9.286 | 7.073 | 134.548 | 31.351 | 28.695 | 29.293 | 603.011 | 26.755 | 27.854 | 1260.861 | 27.488 | 27.912 | 38.262 | 27.001 | 3.2 | 4 | 0.7 | 0.5 | 0.2
5497 | 30/07/2025 12:19:20.289 | 96.648 | 83 | 100 | 70 | 52 | 29.972 | 9.291 | 7.069 | 134.626 | 31.333 | 28.703 | 29.281 | 603.146 | 26.739 | 27.87 | 1265.492 | 27.502 | 27.931 | 38.258 | 27.001 | 3.2 | 2.7 | 0.7 | 0.5 | 0.2
5498 | 30/07/2025 12:19:21.924 | 96.912 | 85 | 100 | 70 | 52 | 32.736 | 9.131 | 7.071 | 134.839 | 31.357 | 28.682 | 29.264 | 603.223 | 26.758 | 27.848 | 1264.919 | 27.476 | 27.934 | 38.452 | 26.001 | 1.6 | 5.3 | 0.9 | 0.8 | 0.3
5499 | 30/07/2025 12:19:23.557 | 97.104 | 84 | 100 | 71 | 52 | 32.019 | 8.917 | 7.068 | 134.673 | 31.363 | 28.675 | 29.291 | 603.277 | 26.731 | 27.835 | 1267.176 | 27.475 | 27.941 | 38.331 | 26.001 | 1.6 | 3.9 | 0.9 | 0.4 | 0.3
5500 | 30/07/2025 12:19:25.198 | 97.488 | 87 | 100 | 70 | 52 | 28.691 | 8.99 | 7.069 | 134.117 | 31.355 | 28.698 | 29.286 | 603.138 | 26.75 | 27.855 | 1267.33 | 27.487 | 27.922 | 38.509 | 26.001 | 1.6 | 3.9 | 0.9 | 0.4 | 0.3
5501 | 30/07/2025 12:19:26.832 | 98.208 | 86 | 100 | 70 | 52 | 31.791 | 9.215 | 7.071 | 134.613 | 31.379 | 28.69 | 29.296 | 602.131 | 26.749 | 27.838 | 1277.341 | 27.495 | 27.901 | 38.45 | 25.001 | 2.1 | 6.6 | 0.7 | 0.5 | 0.2
5502 | 30/07/2025 12:19:28.468 | 98.088 | 86 | 100 | 71 | 53 | 29.057 | 9.225 | 7.087 | 134.71 | 31.364 | 28.688 | 29.291 | 601.85 | 26.742 | 27.857 | 1277.277 | 27.484 | 27.917 | 38.37 | 25.001 | 2.1 | 2.7 | 0.7 | 0.2 | 0.2
5503 | 30/07/2025 12:19:30.103 | 98.328 | 86 | 100 | 70 | 52 | 30.65 | 8.983 | 7.085 | 133.207 | 31.355 | 28.677 | 29.436 | 602.1 | 26.733 | 27.842 | 1277.69 | 27.462 | 27.935 | 38.382 | 24.001 | 3.7 | 4.2 | 0.6 | 0 | 0.3
5504 | 30/07/2025 12:19:31.737 | 98.28 | 84 | 100 | 71 | 53 | 32.865 | 9.137 | 7.087 | 133.026 | 31.34 | 28.679 | 29.282 | 602.016 | 26.724 | 27.839 | 1287.512 | 27.491 | 27.933 | 38.595 | 24.001 | 3.7 | 4.1 | 0.6 | 0.5 | 0.3
5505 | 30/07/2025 12:19:33.371 | 98.184 | 86 | 100 | 70 | 53 | 31.513 | 8.985 | 7.089 | 133.178 | 31.358 | 28.692 | 29.439 | 601.852 | 26.738 | 27.843 | 1279.739 | 27.497 | 27.901 | 38.437 | 25.001 | 3.2 | 3.3 | 0.5 | 1.3 | 0.3
5506 | 30/07/2025 12:19:35.019 | 98.568 | 86 | 100 | 70 | 52 | 28.83 | 9.129 | 7.087 | 133.157 | 31.352 | 28.704 | 29.466 | 602.005 | 26.74 | 27.836 | 1265.597 | 27.501 | 27.938 | 38.172 | 25.001 | 3.2 | 3.3 | 0.5 | 1.3 | 0.3
5507 | 30/07/2025 12:19:36.658 | 99.312 | 88 | 100 | 70 | 53 | 32.191 | 8.986 | 7.12 | 132.967 | 31.343 | 28.683 | 29.42 | 602.032 | 26.733 | 27.835 | 1267.449 | 27.467 | 27.937 | 38.476 | 25.001 | 3.2 | 3.7 | 0.5 | 0 | 0.3
5508 | 30/07/2025 12:19:38.293 | 99.816 | 88 | 100 | 70 | 53 | 28.892 | 8.921 | 7.096 | 133.047 | 31.337 | 28.668 | 29.289 | 601.978 | 26.72 | 27.808 | 1265.342 | 27.466 | 27.942 | 38.797 | 29.001 | 2.4 | 3.1 | 0 | 0 | 0.3
5509 | 30/07/2025 12:19:39.927 | 100.296 | 88 | 100 | 70 | 53 | 31.259 | 9.214 | 7.07 | 132.899 | 31.341 | 28.691 | 29.457 | 601.987 | 26.743 | 27.838 | 1256.376 | 27.497 | 27.919 | 38.509 | 29.001 | 2.4 | 6.5 | 0 | 0.5 | 0.3
5510 | 30/07/2025 12:19:41.562 | 100.272 | 89 | 100 | 71 | 52 | 32.907 | 9.137 | 7.085 | 133.164 | 31.348 | 28.701 | 29.434 | 602 | 26.737 | 27.805 | 1263.806 | 27.497 | 27.895 | 38.43 | 26.001 | 3.7 | 5.7 | 1.5 | 0.1 | 0.2
5511 | 30/07/2025 12:19:43.200 | 99.768 | 89 | 100 | 71 | 53 | 30.854 | 9.136 | 7.084 | 132.946 | 31.321 | 28.695 | 29.449 | 602.013 | 26.748 | 27.853 | 1270.388 | 27.511 | 27.94 | 38.406 | 26.001 | 3.7 | 5.7 | 1.5 | 0.1 | 0.2
5512 | 30/07/2025 12:19:44.835 | 99.6 | 90 | 100 | 70 | 52 | 29.106 | 9.133 | 7.086 | 133.158 | 31.34 | 28.671 | 29.403 | 601.943 | 26.765 | 27.852 | 1264.901 | 27.451 | 27.913 | 39.666 | 26.001 | 3.7 | 4.1 | 1.5 | 0.5 | 0.2
5513 | 30/07/2025 12:19:46.471 | 99.432 | 86 | 100 | 70 | 52 | 32.467 | 9.019 | 7.07 | 133.039 | 31.33 | 28.684 | 29.472 | 602.106 | 26.757 | 27.838 | 1256.289 | 27.499 | 27.941 | 38.394 | 27.001 | 4.2 | 3.8 | 0.9 | 0.1 | 0.2
5514 | 30/07/2025 12:19:48.107 | 99.456 | 88 | 100 | 70 | 52 | 28.715 | 8.848 | 7.069 | 133.01 | 31.338 | 28.703 | 29.444 | 601.897 | 26.746 | 27.848 | 1256.136 | 27.494 | 27.922 | 38.489 | 27.001 | 4.2 | 3.3 | 0.9 | 0.5 | 0.2
5515 | 30/07/2025 12:19:49.740 | 99.696 | 87 | 100 | 70 | 53 | 31.616 | 9.136 | 7.067 | 133.353 | 31.318 | 28.7 | 29.43 | 601.869 | 26.732 | 27.848 | 1257.666 | 27.507 | 27.913 | 38.417 | 24.001 | 5.5 | 3.4 | 0.6 | 0.5 | 0.3
5516 | 30/07/2025 12:19:51.375 | 99.072 | 86 | 100 | 71 | 53 | 32.936 | 8.99 | 7.069 | 134.648 | 31.315 | 28.689 | 29.431 | 603.113 | 26.742 | 27.851 | 1247.377 | 27.489 | 27.925 | 38.316 | 24.001 | 5.5 | 2.2 | 0.6 | 0.2 | 0.3
5517 | 30/07/2025 12:19:53.010 | 99.144 | 88 | 100 | 71 | 54 | 30.119 | 9.21 | 7.066 | 134.602 | 31.346 | 28.665 | 29.414 | 603.127 | 26.737 | 27.829 | 1244.574 | 27.461 | 27.931 | 38.516 | 24.001 | 5.5 | 2.2 | 0.6 | 0.2 | 0.3
5518 | 30/07/2025 12:19:54.649 | 99.216 | 88 | 100 | 71 | 52 | 29.457 | 8.988 | 7.085 | 134.541 | 31.34 | 28.71 | 29.465 | 603.102 | 26.742 | 27.852 | 1241.006 | 27.499 | 27.927 | 38.512 | 25.001 | 5.1 | 5.7 | 1.2 | 0.5 | 0.3
5519 | 30/07/2025 12:19:56.284 | 98.808 | 85 | 100 | 70 | 53 | 31.37 | 9.255 | 7.087 | 134.454 | 31.36 | 28.698 | 29.46 | 603.173 | 26.734 | 27.841 | 1241.776 | 27.494 | 27.93 | 38.385 | 25.001 | 5.1 | 4.7 | 1.2 | 0.5 | 0.3
5520 | 30/07/2025 12:19:57.918 | 98.64 | 87 | 100 | 70 | 52 | 28.797 | 9.29 | 7.087 | 134.737 | 31.362 | 28.702 | 29.445 | 602.094 | 26.744 | 27.846 | 1242.401 | 27.512 | 27.927 | 38.361 | 31.001 | 1.3 | 2.5 | 0.7 | 0.1 | 0.3
5521 | 30/07/2025 12:19:59.553 | 98.04 | 86 | 100 | 70 | 53 | 32.157 | 9.211 | 7.088 | 134.618 | 31.372 | 28.687 | 29.444 | 603.128 | 26.747 | 27.846 | 1237.448 | 27.48 | 27.94 | 38.576 | 31.001 | 1.3 | 3.3 | 0.7 | 0 | 0.3
5522 | 30/07/2025 12:20:01.187 | 98.328 | 88 | 100 | 70 | 52 | 32.864 | 9.289 | 7.133 | 134.594 | 31.353 | 28.669 | 29.436 | 603.302 | 26.735 | 27.845 | 1236.176 | 27.483 | 27.94 | 38.534 | 31.001 | 1.3 | 3.3 | 0.7 | 0 | 0.3
5523 | 30/07/2025 12:20:02.823 | 98.256 | 86 | 100 | 71 | 52 | 29.509 | 9.218 | 7.135 | 134.321 | 31.346 | 28.691 | 29.443 | 602.964 | 26.738 | 27.838 | 1230.796 | 27.494 | 27.909 | 38.529 | 22.001 | 2.7 | 4.5 | 0.6 | 0.8 | 0.3
5524 | 30/07/2025 12:20:04.457 | 97.584 | 84 | 100 | 70 | 50 | 32.917 | 9.14 | 7.134 | 134.35 | 31.35 | 28.703 | 29.445 | 603.111 | 26.73 | 27.84 | 1227.683 | 27.516 | 27.923 | 38.397 | 22.001 | 2.7 | 3.5 | 0.6 | 0.1 | 0.3
5525 | 30/07/2025 12:20:06.090 | 97.704 | 84 | 100 | 71 | 52 | 30.774 | 9.132 | 7.136 | 134.75 | 31.352 | 28.699 | 29.422 | 602.906 | 26.732 | 27.835 | 1227.592 | 27.488 | 27.897 | 38.198 | 28.001 | 3.3 | 3.5 | 0.6 | 0.5 | 0.3
5526 | 30/07/2025 12:20:07.725 | 97.704 | 86 | 99 | 70 | 52 | 29.065 | 9.135 | 7.132 | 134.561 | 31.362 | 28.687 | 29.447 | 603.225 | 26.72 | 27.823 | 1232.346 | 27.452 | 27.939 | 38.409 | 28.001 | 3.3 | 3 | 0.6 | 0.8 | 0.3
5527 | 30/07/2025 12:20:09.360 | 97.872 | 85 | 100 | 71 | 52 | 32.488 | 9.197 | 7.134 | 134.445 | 31.337 | 28.677 | 29.425 | 603.08 | 26.721 | 27.837 | 1235.648 | 27.489 | 27.928 | 38.732 | 28.001 | 3.3 | 3 | 0.6 | 0.8 | 0.3
5528 | 30/07/2025 12:20:10.996 | 97.392 | 85 | 100 | 69 | 53 | 32.757 | 9.138 | 7.135 | 134.55 | 31.366 | 28.695 | 29.46 | 603.161 | 26.738 | 27.824 | 1237.21 | 27.49 | 27.91 | 38.414 | 27.001 | 2.3 | 2.3 | 0.6 | 0.2 | 0.3
5529 | 30/07/2025 12:20:12.631 | 97.968 | 86 | 100 | 71 | 52 | 29.282 | 9.312 | 7.133 | 134.656 | 31.353 | 28.701 | 29.465 | 603.154 | 26.735 | 27.812 | 1244.598 | 27.501 | 27.931 | 38.357 | 27.001 | 2.3 | 5.5 | 0.6 | 0.5 | 0.3
5530 | 30/07/2025 12:20:14.267 | 98.04 | 86 | 100 | 69 | 52 | 32.944 | 9.134 | 7.134 | 134.828 | 31.362 | 28.695 | 29.451 | 603.122 | 26.744 | 27.839 | 1243.906 | 27.484 | 27.933 | 38.199 | 21.001 | 3.1 | 4.6 | 0.3 | 0.1 | 0.3
5531 | 30/07/2025 12:20:15.901 | 97.896 | 84 | 100 | 70 | 53 | 30.289 | 9.133 | 7.132 | 134.575 | 31.336 | 28.673 | 29.44 | 603.2 | 26.738 | 27.831 | 1249.928 | 27.467 | 27.937 | 38.6 | 21.001 | 3.1 | 3.3 | 0.3 | 0 | 0.3
5532 | 30/07/2025 12:20:17.536 | 98.256 | 84 | 100 | 71 | 52 | 29.599 | 9.211 | 7.136 | 134.5 | 31.343 | 28.687 | 29.449 | 603.061 | 26.741 | 27.84 | 1250.12 | 27.493 | 27.916 | 38.631 | 26.001 | 3.4 | 4.3 | 1.5 | 0 | 0.3
5533 | 30/07/2025 12:20:19.170 | 98.28 | 85 | 100 | 71 | 52 | 32.7 | 9.252 | 7.123 | 134.348 | 31.329 | 28.706 | 29.474 | 603.213 | 26.74 | 27.836 | 1247.185 | 27.488 | 27.901 | 38.442 | 26.001 | 3.4 | 4.3 | 1.5 | 0 | 0.3
5534 | 30/07/2025 12:20:20.805 | 97.944 | 86 | 100 | 71 | 53 | 32.53 | 9.137 | 7.122 | 134.624 | 31.326 | 28.701 | 29.449 | 603.108 | 26.741 | 27.869 | 1249.404 | 27.505 | 27.936 | 38.322 | 26.001 | 3.4 | 4 | 1.5 | 1 | 0.3
5535 | 30/07/2025 12:20:22.439 | 97.92 | 84 | 100 | 70 | 53 | 32.2 | 9.258 | 7.121 | 134.637 | 31.334 | 28.691 | 29.425 | 603.277 | 26.754 | 27.841 | 1247.318 | 27.479 | 27.943 | 38.586 | 30.001 | 2.1 | 4 | 2 | 0.8 | 0.3
5536 | 30/07/2025 12:20:24.075 | 98.184 | 86 | 100 | 70 | 52 | 32.926 | 9.479 | 7.121 | 134.41 | 31.315 | 28.668 | 29.452 | 601.884 | 26.734 | 27.862 | 1246.687 | 27.462 | 27.927 | 38.601 | 30.001 | 2.1 | 3.2 | 2 | 0.6 | 0.3
5537 | 30/07/2025 12:20:25.710 | 98.232 | 85 | 100 | 70 | 52 | 29.626 | 9.213 | 7.12 | 134.617 | 31.345 | 28.693 | 29.432 | 601.784 | 26.747 | 27.846 | 1254.623 | 27.494 | 27.919 | 38.393 | 31.001 | 3.6 | 4 | 0.6 | 0 | 0.2
5538 | 30/07/2025 12:20:27.346 | 98.256 | 88 | 100 | 71 | 52 | 30.013 | 9.138 | 7.086 | 134.723 | 31.328 | 28.698 | 29.455 | 601.928 | 26.739 | 27.858 | 1259.016 | 27.511 | 27.919 | 38.469 | 31.001 | 3.6 | 4 | 0.6 | 0 | 0.2
5539 | 30/07/2025 12:20:28.983 | 97.896 | 89 | 100 | 70 | 52 | 32.78 | 9.138 | 7.085 | 134.624 | 31.338 | 28.689 | 29.41 | 601.829 | 26.742 | 27.857 | 1250.673 | 27.48 | 27.928 | 38.38 | 31.001 | 3.6 | 4.4 | 0.6 | 0.6 | 0.2
5540 | 30/07/2025 12:20:30.619 | 98.208 | 86 | 100 | 71 | 52 | 32.078 | 8.993 | 7.133 | 134.797 | 31.356 | 28.673 | 29.443 | 602.056 | 26.755 | 27.835 | 1240.02 | 27.458 | 27.938 | 38.547 | 29.001 | 2.3 | 3.4 | 0.9 | 0.8 | 0.2
5541 | 30/07/2025 12:20:32.256 | 98.376 | 86 | 100 | 70 | 53 | 32.475 | 9.003 | 7.135 | 134.767 | 31.364 | 28.666 | 29.429 | 601.878 | 26.746 | 27.842 | 1239.73 | 27.485 | 27.9 | 38.523 | 29.001 | 2.3 | 4.2 | 0.9 | 0.4 | 0.2
5542 | 30/07/2025 12:20:33.891 | 98.376 | 87 | 100 | 70 | 52 | 32.779 | 8.999 | 7.135 | 134.448 | 31.362 | 28.695 | 29.446 | 603.218 | 26.728 | 27.826 | 1246.431 | 27.501 | 27.932 | 40.279 | 26.001 | 3 | 4.2 | 0 | 0.5 | 0.2
5543 | 30/07/2025 12:20:35.526 | 98.064 | 84 | 100 | 70 | 52 | 29.1 | 9.205 | 7.135 | 134.538 | 31.338 | 28.691 | 29.419 | 602.986 | 26.745 | 27.865 | 1235.435 | 27.49 | 27.906 | 38.34 | 26.001 | 3 | 3.3 | 0 | 0.2 | 0.2
5544 | 30/07/2025 12:20:37.160 | 98.064 | 86 | 100 | 70 | 52 | 30.604 | 9.127 | 7.151 | 134.627 | 31.38 | 28.694 | 29.425 | 603.022 | 26.759 | 27.841 | 1239.763 | 27.474 | 27.93 | 38.287 | 26.001 | 3 | 3.3 | 0 | 0.2 | 0.2
5545 | 30/07/2025 12:20:38.795 | 98.376 | 84 | 100 | 70 | 52 | 32.856 | 9.287 | 7.15 | 134.59 | 31.335 | 28.68 | 29.433 | 603.153 | 26.733 | 27.841 | 1244.358 | 27.488 | 27.941 | 38.437 | 26.001 | 4 | 5.5 | 1.2 | 0 | 0.2
5546 | 30/07/2025 12:20:40.430 | 97.896 | 87 | 100 | 70 | 54 | 31.436 | 9.134 | 7.154 | 134.435 | 31.356 | 28.695 | 29.46 | 603.103 | 26.731 | 27.843 | 1237.045 | 27.5 | 27.914 | 38.388 | 26.001 | 4 | 2.4 | 1.2 | 0.5 | 0.2
5547 | 30/07/2025 12:20:42.064 | 98.088 | 86 | 100 | 71 | 51 | 32.689 | 9.138 | 7.15 | 134.208 | 31.341 | 28.704 | 29.462 | 603.106 | 26.736 | 27.834 | 1232.255 | 27.497 | 27.923 | 38.364 | 31.001 | 2.8 | 3.6 | 0.6 | 0.8 | 0.3
5548 | 30/07/2025 12:20:43.698 | 98.136 | 87 | 100 | 71 | 52 | 32.459 | 9.134 | 7.152 | 134.901 | 31.35 | 28.687 | 29.46 | 603.065 | 26.739 | 27.843 | 1230.068 | 27.488 | 27.907 | 38.134 | 31.001 | 2.8 | 2.9 | 0.6 | 0.7 | 0.3
5549 | 30/07/2025 12:20:45.333 | 98.856 | 88 | 100 | 70 | 52 | 28.8 | 9.284 | 7.15 | 134.681 | 31.367 | 28.688 | 29.458 | 602.233 | 26.728 | 27.836 | 1234.865 | 27.462 | 27.942 | 38.405 | 31.001 | 2.8 | 2.9 | 0.6 | 0.7 | 0.3
5550 | 30/07/2025 12:20:46.968 | 98.568 | 86 | 100 | 71 | 55 | 31.165 | 9.198 | 7.151 | 134.51 | 31.342 | 28.671 | 29.443 | 601.876 | 26.743 | 27.844 | 1237.416 | 27.473 | 27.932 | 38.505 | 27.001 | 2.6 | 2.7 | 0 | 0.1 | 0.2
5551 | 30/07/2025 12:20:48.602 | 98.616 | 85 | 100 | 71 | 52 | 32.908 | 9.128 | 7.152 | 134.686 | 31.359 | 28.698 | 29.461 | 602.997 | 26.749 | 27.83 | 1246.868 | 27.496 | 27.915 | 38.353 | 27.001 | 2.6 | 3.2 | 0 | 0.5 | 0.2
5552 | 30/07/2025 12:20:50.237 | 98.208 | 85 | 100 | 70 | 54 | 30.07 | 9.278 | 7.151 | 134.469 | 31.342 | 28.692 | 29.438 | 603.01 | 26.737 | 27.835 | 1246.835 | 27.492 | 27.908 | 38.442 | 26.001 | 2.3 | 3.1 | 0.6 | 0.1 | 0.3
5553 | 30/07/2025 12:20:51.872 | 98.376 | 87 | 100 | 70 | 52 | 32.786 | 9.291 | 7.194 | 134.806 | 31.355 | 28.691 | 29.436 | 603.16 | 26.76 | 27.838 | 1252.021 | 27.484 | 27.932 | 38.222 | 26.001 | 2.3 | 4.8 | 0.6 | 0.5 | 0.3
5554 | 30/07/2025 12:20:53.505 | 98.256 | 87 | 100 | 71 | 53 | 32.037 | 9.366 | 7.218 | 134.685 | 31.313 | 28.674 | 29.435 | 602.05 | 26.738 | 27.852 | 1252.578 | 27.466 | 27.937 | 38.574 | 27.001 | 2.2 | 5 | 1.1 | 0.6 | 0.3
5555 | 30/07/2025 12:20:55.138 | 97.92 | 86 | 100 | 70 | 52 | 28.77 | 9.232 | 7.221 | 134.684 | 31.329 | 28.686 | 29.469 | 603.112 | 26.759 | 27.862 | 1264.698 | 27.496 | 27.914 | 38.503 | 27.001 | 2.2 | 5 | 1.1 | 0.6 | 0.3
5556 | 30/07/2025 12:20:56.781 | 97.968 | 85 | 100 | 70 | 51 | 31.753 | 9.137 | 7.203 | 134.621 | 31.333 | 28.695 | 29.45 | 603.24 | 26.741 | 27.844 | 1262.163 | 27.498 | 27.916 | 38.738 | 27.001 | 2.2 | 4.4 | 1.1 | 0.6 | 0.3
5557 | 30/07/2025 12:20:58.414 | 97.968 | 85 | 100 | 72 | 53 | 29.188 | 9.213 | 7.204 | 134.719 | 31.325 | 28.691 | 29.449 | 602.899 | 26.76 | 27.851 | 1264.655 | 27.485 | 27.897 | 38.432 | 26.001 | 3.2 | 3.3 | 0.6 | 0.6 | 0.3
5558 | 30/07/2025 12:21:00.050 | 98.448 | 86 | 100 | 70 | 52 | 30.588 | 8.992 | 7.164 | 134.694 | 31.331 | 28.695 | 29.439 | 603.116 | 26.742 | 27.861 | 1273.834 | 27.487 | 27.944 | 38.254 | 26.001 | 3.2 | 6.6 | 0.6 | 0.1 | 0.3
5559 | 30/07/2025 12:21:01.684 | 98.592 | 86 | 100 | 71 | 52 | 32.834 | 9.215 | 7.135 | 134.572 | 31.348 | 28.667 | 29.423 | 603.109 | 26.751 | 27.862 | 1277.043 | 27.459 | 27.937 | 38.618 | 24.001 | 3 | 5.2 | 0.6 | 0.5 | 0.3
5560 | 30/07/2025 12:21:03.319 | 98.568 | 86 | 100 | 70 | 53 | 31.529 | 9.198 | 7.123 | 134.488 | 31.376 | 28.704 | 29.474 | 601.97 | 26.737 | 27.84 | 1276.565 | 27.497 | 27.928 | 39.999 | 24.001 | 3 | 5.2 | 0.6 | 0.5 | 0.3
5561 | 30/07/2025 12:21:04.953 | 98.352 | 85 | 100 | 70 | 53 | 28.858 | 9.14 | 7.122 | 134.44 | 31.356 | 28.697 | 29.451 | 601.902 | 26.734 | 27.847 | 1273.331 | 27.51 | 27.904 | 38.463 | 24.001 | 3 | 4.5 | 0.6 | 0.6 | 0.3
5562 | 30/07/2025 12:21:06.588 | 98.28 | 87 | 100 | 70 | 53 | 32.163 | 9.131 | 7.122 | 134.731 | 31.364 | 28.694 | 29.436 | 601.809 | 26.743 | 27.852 | 1264.579 | 27.485 | 27.914 | 38.355 | 28.001 | 2 | 4.3 | 0.1 | 0.6 | 0.3
5563 | 30/07/2025 12:21:08.222 | 98.232 | 86 | 100 | 70 | 52 | 28.822 | 9.211 | 7.119 | 134.541 | 31.348 | 28.698 | 29.417 | 602.033 | 26.74 | 27.852 | 1258.07 | 27.476 | 27.938 | 38.506 | 28.001 | 2 | 5.8 | 0.1 | 0 | 0.3
5564 | 30/07/2025 12:21:09.856 | 98.304 | 87 | 100 | 70 | 52 | 31.152 | 9.286 | 7.121 | 134.683 | 31.367 | 28.663 | 29.449 | 601.923 | 26.745 | 27.854 | 1254.592 | 27.463 | 27.917 | 38.385 | 28.001 | 3.2 | 3.6 | 0.6 | 0.5 | 0.2
5565 | 30/07/2025 12:21:11.490 | 98.088 | 85 | 100 | 71 | 53 | 32.908 | 9.14 | 7.123 | 134.41 | 31.358 | 28.694 | 29.443 | 601.977 | 26.732 | 27.835 | 1254.394 | 27.511 | 27.93 | 38.525 | 28.001 | 3.2 | 2.9 | 0.6 | 0.5 | 0.2
5566 | 30/07/2025 12:21:13.123 | 98.136 | 86 | 100 | 71 | 52 | 30.876 | 9.198 | 7.124 | 134.616 | 31.353 | 28.693 | 29.434 | 601.852 | 26.737 | 27.851 | 1246.634 | 27.484 | 27.894 | 38.428 | 28.001 | 3.2 | 2.9 | 0.6 | 0.5 | 0.2
5567 | 30/07/2025 12:21:14.755 | 98.064 | 85 | 100 | 70 | 52 | 28.972 | 8.982 | 7.134 | 134.842 | 31.362 | 28.688 | 29.443 | 601.957 | 26.733 | 27.832 | 1239.714 | 27.478 | 27.916 | 38.071 | 23.001 | 2 | 1.9 | 0.6 | 0.2 | 0.3
5568 | 30/07/2025 12:21:16.389 | 98.184 | 84 | 100 | 70 | 53 | 32.471 | 8.99 | 7.132 | 134.676 | 31.344 | 28.656 | 29.424 | 603.173 | 26.714 | 27.828 | 1242.317 | 27.477 | 27.932 | 38.422 | 23.001 | 2 | 2.6 | 0.6 | 0 | 0.3
5569 | 30/07/2025 12:21:18.025 | 97.488 | 85 | 100 | 71 | 53 | 28.714 | 8.985 | 7.134 | 134.464 | 31.358 | 28.682 | 29.454 | 603.11 | 26.726 | 27.819 | 1242 | 27.477 | 27.927 | 38.389 | 23.001 | 1.6 | 4.8 | 0.6 | 0.5 | 0.3
5570 | 30/07/2025 12:21:19.660 | 97.632 | 86 | 100 | 70 | 52 | 31.64 | 9.098 | 7.184 | 134.391 | 31.339 | 28.705 | 29.433 | 601.781 | 26.734 | 27.828 | 1241.574 | 27.513 | 27.919 | 38.392 | 23.001 | 1.6 | 3.7 | 0.6 | 1.1 | 0.3
5571 | 30/07/2025 12:21:21.291 | 97.848 | 87 | 100 | 70 | 53 | 32.936 | 9.195 | 7.188 | 134.929 | 31.358 | 28.696 | 29.435 | 601.703 | 26.731 | 27.824 | 1255.013 | 27.488 | 27.895 | 38.263 | 23.001 | 1.6 | 3.7 | 0.6 | 1.1 | 0.3
5572 | 30/07/2025 12:21:22.927 | 98.232 | 87 | 100 | 70 | 53 | 30.249 | 9.133 | 7.185 | 134.61 | 31.35 | 28.681 | 29.448 | 602.037 | 26.732 | 27.82 | 1257.789 | 27.483 | 27.946 | 38.218 | 24.001 | 3 | 5.4 | 0.6 | 0.8 | 0.3
5573 | 30/07/2025 12:21:24.563 | 98.928 | 87 | 100 | 70 | 53 | 32.833 | 9.187 | 7.185 | 134.713 | 31.354 | 28.669 | 29.437 | 602.05 | 26.753 | 27.828 | 1257.021 | 27.451 | 27.917 | 38.46 | 24.001 | 3 | 4.8 | 0.6 | 1.5 | 0.3
5574 | 30/07/2025 12:21:26.196 | 98.808 | 88 | 100 | 70 | 52 | 31.516 | 9.134 | 7.186 | 134.514 | 31.342 | 28.698 | 29.444 | 602.113 | 26.748 | 27.838 | 1267.012 | 27.513 | 27.941 | 38.424 | 24.001 | 1.4 | 3.1 | 1.7 | 0 | 0.3
5575 | 30/07/2025 12:21:27.832 | 98.856 | 86 | 100 | 69 | 52 | 28.86 | 9.216 | 7.122 | 134.33 | 31.321 | 28.699 | 29.446 | 601.802 | 26.756 | 27.851 | 1271.914 | 27.494 | 27.905 | 38.521 | 24.001 | 1.4 | 3.6 | 1.7 | 0 | 0.3
5576 | 30/07/2025 12:21:29.467 | 98.28 | 85 | 100 | 70 | 51 | 32.161 | 9.144 | 7.1 | 134.709 | 31.336 | 28.688 | 29.436 | 601.882 | 26.738 | 27.843 | 1280.609 | 27.486 | 27.924 | 38.338 | 25.001 | 1.7 | 5.6 | 0 | 0 | 0.3
5577 | 30/07/2025 12:21:31.103 | 97.92 | 84 | 100 | 69 | 52 | 32.937 | 8.98 | 7.087 | 134.621 | 31.318 | 28.68 | 29.434 | 602.151 | 26.741 | 27.863 | 1283.003 | 27.471 | 27.937 | 38.69 | 25.001 | 1.7 | 5.6 | 0 | 0 | 0.3
5578 | 30/07/2025 12:21:32.737 | 98.184 | 84 | 100 | 70 | 52 | 29.751 | 9.043 | 7.086 | 134.594 | 31.337 | 28.68 | 29.452 | 600.608 | 26.737 | 27.853 | 1282.835 | 27.489 | 27.909 | 38.613 | 25.001 | 1.7 | 2.8 | 0 | 1.3 | 0.3
5579 | 30/07/2025 12:21:34.373 | 98.616 | 86 | 100 | 70 | 53 | 32.898 | 9.134 | 7.087 | 134.352 | 31.338 | 28.702 | 29.434 | 600.522 | 26.739 | 27.86 | 1283.238 | 27.497 | 27.926 | 38.623 | 31.001 | 1.6 | 4.3 | 0 | 0.8 | 0.4
5580 | 30/07/2025 12:21:36.007 | 98.976 | 86 | 100 | 70 | 53 | 31.02 | 9.012 | 7.071 | 134.443 | 31.362 | 28.689 | 29.467 | 601.798 | 26.754 | 27.843 | 1279.582 | 27.48 | 27.895 | 38.308 | 31.001 | 1.6 | 5.7 | 0 | 0.5 | 0.4
5581 | 30/07/2025 12:21:37.642 | 99.648 | 89 | 100 | 71 | 54 | 29.155 | 9.136 | 7.067 | 134.604 | 31.356 | 28.695 | 29.454 | 601.739 | 26.737 | 27.847 | 1286.498 | 27.501 | 27.933 | 38.293 | 26.001 | 2.1 | 3.7 | 0.7 | 0.1 | 0.3
5582 | 30/07/2025 12:21:39.276 | 99.36 | 87 | 100 | 70 | 52 | 32.515 | 9.113 | 7.068 | 133.196 | 31.36 | 28.667 | 29.42 | 602.008 | 26.741 | 27.851 | 1282.273 | 27.455 | 27.915 | 38.804 | 26.001 | 2.1 | 3.7 | 0.7 | 0.1 | 0.3
5583 | 30/07/2025 12:21:40.909 | 100.032 | 90 | 100 | 70 | 52 | 32.817 | 9.204 | 7.118 | 133.132 | 31.359 | 28.695 | 29.471 | 601.985 | 26.739 | 27.842 | 1267.021 | 27.51 | 27.915 | 38.478 | 26.001 | 2.1 | 5 | 0.7 | 0.5 | 0.3
5584 | 30/07/2025 12:21:42.544 | 99.648 | 88 | 100 | 70 | 52 | 29.234 | 9.138 | 7.12 | 133.181 | 31.357 | 28.695 | 29.463 | 600.41 | 26.739 | 27.862 | 1267.157 | 27.495 | 27.92 | 38.421 | 29.001 | 3.1 | 5.5 | 0.6 | 0.6 | 0.3
5585 | 30/07/2025 12:21:44.180 | 99.264 | 89 | 100 | 71 | 51 | 32.906 | 9.16 | 7.12 | 133.219 | 31.365 | 28.694 | 29.481 | 600.351 | 26.74 | 27.853 | 1268.055 | 27.493 | 27.93 | 38.177 | 29.001 | 3.1 | 3.3 | 0.6 | 1.4 | 0.3
5586 | 30/07/2025 12:21:45.811 | 99.552 | 87 | 100 | 70 | 52 | 30.322 | 9.152 | 7.12 | 134.525 | 31.342 | 28.691 | 29.429 | 600.6 | 26.725 | 27.853 | 1274.389 | 27.477 | 27.935 | 38.439 | 27.001 | 2.1 | 1.6 | 0.3 | 0.5 | 0.4
5587 | 30/07/2025 12:21:47.445 | 99.48 | 87 | 99 | 70 | 52 | 29.455 | 8.98 | 7.134 | 134.556 | 31.359 | 28.666 | 29.46 | 600.538 | 26.736 | 27.846 | 1262.349 | 27.465 | 27.922 | 38.533 | 27.001 | 2.1 | 2.2 | 0.3 | 0.8 | 0.4
5588 | 30/07/2025 12:21:49.078 | 99.552 | 88 | 100 | 70 | 53 | 32.674 | 9.173 | 7.134 | 134.217 | 31.354 | 28.697 | 29.443 | 600.49 | 26.718 | 27.831 | 1254.137 | 27.507 | 27.932 | 38.679 | 27.001 | 2.1 | 2.2 | 0.3 | 0.8 | 0.4
5589 | 30/07/2025 12:21:50.712 | 99.816 | 87 | 100 | 71 | 52 | 32.465 | 9.247 | 7.123 | 134.755 | 31.342 | 28.688 | 29.447 | 600.386 | 26.732 | 27.84 | 1259.533 | 27.497 | 27.896 | 38.283 | 28.001 | 2.5 | 4 | 1 | 0.5 | 0.4
5590 | 30/07/2025 12:21:52.347 | 99.168 | 88 | 100 | 72 | 52 | 32.121 | 9.134 | 7.088 | 134.593 | 31.34 | 28.697 | 29.435 | 600.457 | 26.727 | 27.825 | 1257.594 | 27.51 | 27.935 | 38.233 | 28.001 | 2.5 | 6.7 | 1 | 0.2 | 0.4
5591 | 30/07/2025 12:21:53.983 | 99 | 88 | 100 | 70 | 52 | 32.942 | 9.277 | 7.089 | 134.53 | 31.35 | 28.673 | 29.42 | 600.524 | 26.733 | 27.831 | 1259.378 | 27.463 | 27.932 | 38.387 | 32.001 | 2.4 | 3.9 | 0.4 | 0.6 | 0.3
5592 | 30/07/2025 12:21:55.618 | 99.336 | 88 | 100 | 71 | 53 | 29.63 | 9.197 | 7.133 | 134.672 | 31.352 | 28.672 | 29.471 | 600.583 | 26.723 | 27.817 | 1261.58 | 27.47 | 27.922 | 38.377 | 32.001 | 2.4 | 2.5 | 0.4 | 0.5 | 0.3
5593 | 30/07/2025 12:21:57.250 | 99.408 | 87 | 100 | 71 | 53 | 30 | 9.218 | 7.134 | 134.259 | 31.338 | 28.711 | 29.452 | 600.41 | 26.743 | 27.847 | 1262.208 | 27.495 | 27.932 | 38.488 | 32.001 | 2.4 | 2.5 | 0.4 | 0.5 | 0.3
5594 | 30/07/2025 12:21:58.884 | 99.744 | 88 | 100 | 70 | 52 | 32.768 | 9.236 | 7.135 | 134.85 | 31.347 | 28.683 | 29.426 | 600.476 | 26.747 | 27.845 | 1267.399 | 27.488 | 27.895 | 38.183 | 31.001 | 2.4 | 5.1 | 1.6 | 0.1 | 0.3
5595 | 30/07/2025 12:22:00.518 | 99.504 | 89 | 100 | 70 | 52 | 29.103 | 9.134 | 7.135 | 134.473 | 31.334 | 28.69 | 29.427 | 600.289 | 26.743 | 27.855 | 1267.321 | 27.484 | 27.924 | 38.318 | 31.001 | 2.4 | 4.1 | 1.6 | 0.5 | 0.3
5596 | 30/07/2025 12:22:02.153 | 99.864 | 90 | 100 | 70 | 53 | 32.429 | 9.127 | 7.133 | 134.792 | 31.348 | 28.678 | 29.415 | 600.539 | 26.763 | 27.851 | 1274.768 | 27.462 | 27.936 | 38.561 | 30.001 | 1.2 | 3.6 | 0.9 | 0.2 | 0.3
5597 | 30/07/2025 12:22:03.788 | 99.144 | 85 | 100 | 70 | 52 | 32.771 | 9.276 | 7.122 | 134.43 | 31.319 | 28.684 | 29.446 | 600.542 | 26.751 | 27.855 | 1267.06 | 27.517 | 27.932 | 38.451 | 30.001 | 1.2 | 4.3 | 0.9 | 0 | 0.3
5598 | 30/07/2025 12:22:05.422 | 99.408 | 86 | 100 | 71 | 52 | 29.088 | 9.141 | 7.088 | 134.387 | 31.324 | 28.691 | 29.43 | 600.419 | 26.75 | 27.854 | 1268.985 | 27.498 | 27.903 | 38.543 | 27.001 | 2.6 | 3.6 | 0.6 | 0.5 | 0.3
5599 | 30/07/2025 12:22:07.056 | 98.784 | 86 | 100 | 72 | 53 | 30.569 | 9.208 | 7.086 | 134.701 | 31.338 | 28.696 | 29.436 | 600.396 | 26.736 | 27.856 | 1267.298 | 27.495 | 27.928 | 38.153 | 27.001 | 2.6 | 3.6 | 0.6 | 0.5 | 0.3
5600 | 30/07/2025 12:22:08.691 | 98.4 | 88 | 100 | 70 | 53 | 32.818 | 9.225 | 7.133 | 134.449 | 31.335 | 28.676 | 29.409 | 600.491 | 26.733 | 27.864 | 1274.505 | 27.47 | 27.931 | 38.587 | 27.001 | 2.6 | 4.6 | 0.6 | 0 | 0.3
5601 | 30/07/2025 12:22:10.325 | 98.256 | 88 | 100 | 70 | 52 | 29.555 | 9.195 | 7.131 | 134.697 | 31.354 | 28.674 | 29.461 | 600.663 | 26.74 | 27.84 | 1274.558 | 27.463 | 27.945 | 38.508 | 28.001 | 3.5 | 3.9 | 0 | 0.8 | 0.2
5602 | 30/07/2025 12:22:11.959 | 98.616 | 88 | 100 | 70 | 52 | 32.646 | 9.291 | 7.135 | 134.435 | 31.35 | 28.689 | 29.458 | 600.476 | 26.747 | 27.862 | 1276.944 | 27.495 | 27.934 | 38.488 | 28.001 | 3.5 | 6.1 | 0 | 1.7 | 0.2
5603 | 30/07/2025 12:22:13.590 | 98.4 | 86 | 100 | 71 | 52 | 32.554 | 9.296 | 7.136 | 134.677 | 31.373 | 28.693 | 29.472 | 600.453 | 26.746 | 27.852 | 1286.939 | 27.489 | 27.909 | 38.311 | 24.001 | 2.1 | 5.3 | 0.7 | 0.5 | 0.2
5604 | 30/07/2025 12:22:15.226 | 98.664 | 86 | 100 | 70 | 53 | 28.954 | 9.257 | 7.133 | 134.691 | 31.346 | 28.694 | 29.436 | 600.384 | 26.74 | 27.847 | 1286.725 | 27.504 | 27.94 | 38.241 | 24.001 | 2.1 | 5.3 | 0.7 | 0.5 | 0.2
5605 | 30/07/2025 12:22:16.870 | 98.448 | 84 | 100 | 70 | 53 | 31.264 | 9.129 | 7.135 | 134.505 | 31.358 | 28.674 | 29.442 | 600.589 | 26.739 | 27.842 | 1284.575 | 27.459 | 27.919 | 38.551 | 24.001 | 2.1 | 3.9 | 0.7 | 0.1 | 0.2
5606 | 30/07/2025 12:22:18.505 | 98.16 | 85 | 100 | 72 | 53 | 29.816 | 9.133 | 7.133 | 134.555 | 31.36 | 28.67 | 29.471 | 600.569 | 26.732 | 27.842 | 1287.315 | 27.481 | 27.94 | 38.293 | 33.001 | 1.5 | 3.5 | 0 | 0.8 | 0.3
5607 | 30/07/2025 12:22:20.141 | 98.016 | 84 | 100 | 70 | 52 | 29.986 | 9.244 | 7.135 | 134.412 | 31.355 | 28.7 | 29.453 | 600.622 | 26.743 | 27.85 | 1292.686 | 27.496 | 27.908 | 38.424 | 33.001 | 1.5 | 5.6 | 0 | 0.2 | 0.3
5608 | 30/07/2025 12:22:21.776 | 98.448 | 86 | 100 | 71 | 52 | 32.81 | 9.14 | 7.143 | 134.632 | 31.357 | 28.695 | 29.438 | 600.377 | 26.723 | 27.837 | 1297.095 | 27.492 | 27.918 | 38.198 | 24.001 | 3.7 | 5.3 | 0.9 | 0 | 0.3
5609 | 30/07/2025 12:22:23.412 | 97.848 | 84 | 100 | 71 | 52 | 32.124 | 9.135 | 7.152 | 134.48 | 31.339 | 28.688 | 29.421 | 600.487 | 26.715 | 27.837 | 1295.109 | 27.474 | 27.918 | 38.486 | 24.001 | 3.7 | 4 | 0.9 | 1 | 0.3
5610 | 30/07/2025 12:22:25.047 | 97.368 | 86 | 100 | 70 | 52 | 28.775 | 9.128 | 7.15 | 134.689 | 31.365 | 28.673 | 29.464 | 600.588 | 26.745 | 27.828 | 1293.57 | 27.466 | 27.927 | 38.494 | 24.001 | 3.7 | 4 | 0.9 | 1 | 0.3
5611 | 30/07/2025 12:22:26.683 | 98.04 | 86 | 100 | 71 | 52 | 31.673 | 9.13 | 7.152 | 134.583 | 31.346 | 28.702 | 29.472 | 600.507 | 26.734 | 27.826 | 1284.892 | 27.514 | 27.935 | 38.314 | 28.001 | 3.1 | 4.3 | 0 | 0.8 | 0.3
5612 | 30/07/2025 12:22:28.319 | 97.92 | 85 | 100 | 71 | 54 | 29.217 | 9.293 | 7.152 | 134.433 | 31.356 | 28.687 | 29.47 | 600.491 | 26.728 | 27.812 | 1287.005 | 27.501 | 27.906 | 38.415 | 28.001 | 3.1 | 4.9 | 0 | 0.5 | 0.3
5613 | 30/07/2025 12:22:29.954 | 97.632 | 84 | 100 | 70 | 52 | 30.586 | 9.134 | 7.168 | 134.518 | 31.331 | 28.701 | 29.437 | 600.405 | 26.733 | 27.813 | 1292.36 | 27.506 | 27.916 | 38.469 | 26.001 | 2.2 | 4 | 2 | 1.3 | 0.2
5614 | 30/07/2025 12:22:31.589 | 97.992 | 87 | 100 | 70 | 51 | 32.859 | 9.24 | 7.185 | 134.539 | 31.354 | 28.685 | 29.425 | 600.667 | 26.749 | 27.838 | 1286.733 | 27.467 | 27.925 | 38.475 | 26.001 | 2.2 | 4.5 | 2 | 0.3 | 0.2
5615 | 30/07/2025 12:22:33.223 | 98.472 | 85 | 100 | 71 | 52 | 31.443 | 9.179 | 7.122 | 134.488 | 31.347 | 28.674 | 29.457 | 600.626 | 26.747 | 27.842 | 1282.119 | 27.475 | 27.935 | 38.572 | 26.001 | 2.2 | 4.5 | 2 | 0.3 | 0.2
5616 | 30/07/2025 12:22:34.857 | 97.92 | 85 | 99 | 70 | 52 | 28.82 | 9.291 | 7.088 | 134.343 | 31.33 | 28.707 | 29.438 | 600.397 | 26.761 | 27.858 | 1266.986 | 27.497 | 27.923 | 38.619 | 25.001 | 1.1 | 4.1 | 0.9 | 0.5 | 0.2
5617 | 30/07/2025 12:22:36.492 | 98.328 | 87 | 100 | 70 | 52 | 32.466 | 9.217 | 7.085 | 134.636 | 31.327 | 28.7 | 29.445 | 600.302 | 26.744 | 27.858 | 1261.699 | 27.502 | 27.915 | 38.274 | 25.001 | 1.1 | 3.5 | 0.9 | 0.6 | 0.2
5618 | 30/07/2025 12:22:38.129 | 98.136 | 85 | 100 | 71 | 52 | 28.818 | 9.132 | 7.132 | 134.403 | 31.316 | 28.693 | 29.429 | 600.288 | 26.746 | 27.86 | 1267.189 | 27.483 | 27.92 | 38.286 | 31.001 | 3.9 | 5.9 | 0.9 | 0.8 | 0.2
5619 | 30/07/2025 12:22:39.765 | 98.376 | 87 | 100 | 71 | 53 | 31.055 | 9.027 | 7.15 | 134.656 | 31.356 | 28.675 | 29.433 | 600.72 | 26.745 | 27.836 | 1267.554 | 27.463 | 27.922 | 38.576 | 31.001 | 3.9 | 5.4 | 0.9 | 0.4 | 0.2
5620 | 30/07/2025 12:22:41.401 | 98.472 | 85 | 100 | 71 | 53 | 32.895 | 9.131 | 7.186 | 134.543 | 31.33 | 28.686 | 29.487 | 600.543 | 26.744 | 27.872 | 1277.807 | 27.507 | 27.941 | 38.462 | 28.001 | 3 | 4.3 | 1.2 | 0.6 | 0.2
5621 | 30/07/2025 12:22:43.037 | 98.304 | 85 | 100 | 71 | 53 | 30.908 | 9.134 | 7.188 | 134.473 | 31.353 | 28.695 | 29.437 | 600.409 | 26.75 | 27.862 | 1276.904 | 27.496 | 27.906 | 38.357 | 28.001 | 3 | 4.3 | 1.2 | 0.6 | 0.2
5622 | 30/07/2025 12:22:44.671 | 98.736 | 87 | 100 | 70 | 52 | 29.113 | 9.242 | 7.185 | 134.911 | 31.358 | 28.699 | 29.427 | 600.464 | 26.73 | 27.835 | 1277.314 | 27.495 | 27.916 | 38.218 | 28.001 | 3 | 3.5 | 1.2 | 0.1 | 0.2
5623 | 30/07/2025 12:22:46.306 | 98.616 | 86 | 100 | 71 | 52 | 32.114 | 9.13 | 7.139 | 134.552 | 31.368 | 28.696 | 29.423 | 600.341 | 26.756 | 27.866 | 1280.828 | 27.481 | 27.93 | 38.128 | 23.001 | 4.1 | 4.2 | 0.9 | 0 | 0.2
5624 | 30/07/2025 12:22:47.943 | 98.664 | 88 | 100 | 71 | 53 | 28.803 | 9.135 | 7.132 | 134.682 | 31.358 | 28.671 | 29.425 | 600.444 | 26.744 | 27.845 | 1267.019 | 27.469 | 27.937 | 38.577 | 23.001 | 4.1 | 2.6 | 0.9 | 0 | 0.2
5625 | 30/07/2025 12:22:49.579 | 97.92 | 85 | 100 | 70 | 54 | 31.72 | 9.135 | 7.136 | 134.268 | 31.36 | 28.689 | 29.443 | 601.906 | 26.74 | 27.851 | 1275.328 | 27.504 | 27.924 | 38.369 | 22.001 | 2.5 | 3.8 | 0.7 | 0.5 | 0.2
5626 | 30/07/2025 12:22:51.215 | 98.04 | 86 | 100 | 70 | 52 | 32.897 | 9.133 | 7.134 | 134.659 | 31.367 | 28.698 | 29.445 | 601.769 | 26.742 | 27.839 | 1263.164 | 27.488 | 27.911 | 38.345 | 22.001 | 2.5 | 3.8 | 0.7 | 0.5 | 0.2
5627 | 30/07/2025 12:22:52.853 | 98.232 | 87 | 100 | 71 | 53 | 30.345 | 9.045 | 7.134 | 134.589 | 31.347 | 28.691 | 29.43 | 600.451 | 26.74 | 27.85 | 1260.422 | 27.504 | 27.931 | 38.379 | 22.001 | 2.5 | 8.2 | 0.7 | 0 | 0.2
5628 | 30/07/2025 12:22:54.490 | 98.496 | 87 | 100 | 70 | 52 | 32.873 | 8.983 | 7.133 | 134.639 | 31.363 | 28.69 | 29.441 | 600.54 | 26.723 | 27.831 | 1257.354 | 27.481 | 27.933 | 38.3 | 24.001 | 2 | 5.5 | 0.3 | 0.5 | 0.3
5629 | 30/07/2025 12:22:56.128 | 98.664 | 84 | 100 | 70 | 52 | 31.559 | 9.134 | 7.133 | 134.636 | 31.352 | 28.666 | 29.434 | 600.503 | 26.724 | 27.849 | 1255.334 | 27.48 | 27.932 | 38.469 | 24.001 | 2 | 5.4 | 0.3 | 0.8 | 0.3
5630 | 30/07/2025 12:22:57.762 | 98.664 | 86 | 100 | 71 | 52 | 28.832 | 9.136 | 7.137 | 134.429 | 31.347 | 28.685 | 29.449 | 600.501 | 26.733 | 27.827 | 1260.126 | 27.492 | 27.901 | 38.454 | 28.001 | 1.5 | 4.6 | 0.3 | 0.2 | 0.3
5631 | 30/07/2025 12:22:59.396 | 98.592 | 85 | 100 | 70 | 53 | 32.239 | 9.132 | 7.148 | 134.54 | 31.345 | 28.702 | 29.454 | 600.418 | 26.728 | 27.829 | 1264.679 | 27.498 | 27.923 | 38.322 | 28.001 | 1.5 | 3.3 | 0.3 | 0 | 0.3
5632 | 30/07/2025 12:23:01.030 | 98.232 | 86 | 100 | 70 | 52 | 32.973 | 9.129 | 7.187 | 134.552 | 31.343 | 28.691 | 29.421 | 600.366 | 26.714 | 27.824 | 1271.105 | 27.483 | 27.923 | 38.233 | 28.001 | 1.5 | 3.3 | 0.3 | 0 | 0.3
5633 | 30/07/2025 12:23:02.747 | 98.04 | 85 | 100 | 70 | 52 | 29.855 | 9.123 | 7.184 | 134.643 | 31.367 | 28.663 | 29.448 | 600.499 | 26.738 | 27.823 | 1280.876 | 27.458 | 27.91 | 38.518 | 25.001 | 3.3 | 4.3 | 0.3 | 0 | 0.2
5634 | 30/07/2025 12:23:04.387 | 98.04 | 86 | 100 | 70 | 52 | 32.937 | 9.143 | 7.187 | 134.344 | 31.352 | 28.676 | 29.465 | 600.458 | 26.735 | 27.824 | 1277.154 | 27.479 | 27.916 | 38.532 | 25.001 | 3.3 | 4.5 | 0.3 | 0.5 | 0.2
5635 | 30/07/2025 12:23:06.022 | 98.352 | 85 | 99 | 70 | 52 | 30.958 | 9.213 | 7.122 | 134.515 | 31.35 | 28.696 | 29.471 | 600.521 | 26.729 | 27.834 | 1271.563 | 27.499 | 27.917 | 38.414 | 31.001 | 1.6 | 3 | 0 | 0.5 | 0.2
5636 | 30/07/2025 12:23:07.658 | 97.8 | 87 | 100 | 70 | 52 | 29.035 | 9.434 | 7.091 | 134.601 | 31.322 | 28.695 | 29.436 | 600.361 | 26.751 | 27.851 | 1276.91 | 27.5 | 27.92 | 38.205 | 31.001 | 1.6 | 2.3 | 0 | 0.2 | 0.2
5637 | 30/07/2025 12:23:09.293 | 97.392 | 84 | 100 | 70 | 53 | 32.431 | 9.131 | 7.071 | 134.623 | 31.337 | 28.683 | 29.435 | 600.533 | 26.759 | 27.856 | 1271.974 | 27.47 | 27.928 | 38.327 | 31.001 | 1.6 | 2.3 | 0 | 0.2 | 0.2
5638 | 30/07/2025 12:23:10.930 | 96.888 | 85 | 100 | 70 | 52 | 32.795 | 9.188 | 7.084 | 134.597 | 31.314 | 28.675 | 29.468 | 600.63 | 26.745 | 27.846 | 1277.065 | 27.483 | 27.935 | 38.454 | 25.001 | 1.5 | 2.4 | 0.9 | 0.5 | 0.2
5639 | 30/07/2025 12:23:12.564 | 97.248 | 86 | 100 | 70 | 52 | 29.209 | 9.301 | 7.092 | 134.172 | 31.313 | 28.697 | 29.433 | 600.427 | 26.738 | 27.856 | 1279.184 | 27.495 | 27.916 | 38.472 | 25.001 | 1.5 | 5 | 0.9 | 0.8 | 0.2
5640 | 30/07/2025 12:23:14.197 | 96.744 | 84 | 100 | 71 | 52 | 32.957 | 9.194 | 7.122 | 134.393 | 31.312 | 28.714 | 29.45 | 600.543 | 26.744 | 27.859 | 1278.943 | 27.501 | 27.926 | 38.535 | 25.001 | 3 | 2.8 | 0.6 | 0.6 | 0.2
5641 | 30/07/2025 12:23:15.833 | 96.96 | 84 | 100 | 70 | 51 | 30.239 | 9.129 | 7.125 | 134.75 | 31.35 | 28.69 | 29.439 | 600.277 | 26.747 | 27.849 | 1277.573 | 27.487 | 27.915 | 38.374 | 25.001 | 3 | 3.6 | 0.6 | 0.5 | 0.2
5642 | 30/07/2025 12:23:17.468 | 96.336 | 84 | 100 | 70 | 52 | 29.49 | 8.991 | 7.132 | 134.665 | 31.351 | 28.686 | 29.444 | 600.586 | 26.736 | 27.841 | 1267.252 | 27.463 | 27.934 | 38.437 | 23.001 | 2.9 | 4.4 | 1.8 | 0 | 0.2
5643 | 30/07/2025 12:23:19.102 | 96.408 | 84 | 100 | 71 | 52 | 32.709 | 8.99 | 7.134 | 134.523 | 31.35 | 28.687 | 29.456 | 600.475 | 26.731 | 27.85 | 1273.974 | 27.496 | 27.937 | 38.455 | 23.001 | 2.9 | 4.4 | 1.8 | 0 | 0.2
5644 | 30/07/2025 12:23:20.736 | 96.624 | 85 | 100 | 70 | 52 | 32.478 | 9.139 | 7.135 | 134.624 | 31.365 | 28.701 | 29.433 | 600.539 | 26.757 | 27.844 | 1274.123 | 27.489 | 27.902 | 38.437 | 23.001 | 2.9 | 3.9 | 1.8 | 0 | 0.2
5645 | 30/07/2025 12:23:22.371 | 85.68 | 72 | 98 | 68 | 50 | 32.086 | 9.13 | 7.134 | 134.555 | 31.353 | 28.699 | 29.44 | 600.379 | 26.739 | 27.864 | 1270.103 | 27.493 | 27.909 | 38.306 | 24.001 | 1.1 | 2 | 0.6 | 0 | 0.2
5646 | 30/07/2025 12:23:24.004 | 70.344 | 57 | 95 | 65 | 48 | 32.878 | 9.243 | 7.132 | 134.781 | 31.37 | 28.687 | 29.419 | 600.426 | 26.751 | 27.854 | 1269.518 | 27.487 | 27.93 | 38.257 | 24.001 | 1.1 | 1.9 | 0.6 | 0 | 0.2
5647 | 30/07/2025 12:23:25.640 | 56.304 | 43 | 92 | 62 | 44 | 29.747 | 9.138 | 7.119 | 134.572 | 31.349 | 28.675 | 29.428 | 600.567 | 26.737 | 27.843 | 1266.183 | 27.476 | 27.946 | 38.583 | 19 | 2.2 | 4.2 | 0.5 | 0 | 0.4
5648 | 30/07/2025 12:23:27.283 | 45.216 | 34 | 90 | 59 | 41 | 30.035 | 9.025 | 7.136 | 132.866 | 31.347 | 28.693 | 29.459 | 600.423 | 26.731 | 27.847 | 1257.273 | 27.491 | 27.917 | 38.338 | 19 | 2.2 | 4.2 | 0.5 | 0 | 0.4
5649 | 30/07/2025 12:23:28.927 | 35.4 | 27 | 87 | 56 | 38 | 32.795 | 9.22 | 7.133 | 131.728 | 31.36 | 28.698 | 29.45 | 600.398 | 26.727 | 27.827 | 1259.568 | 27.49 | 27.908 | 38.267 | 19 | 2.2 | 4.6 | 0.5 | 0.6 | 0.4
5650 | 30/07/2025 12:23:30.563 | 27.984 | 20 | 84 | 53 | 36 | 32.206 | 9.184 | 7.134 | 128.958 | 31.346 | 28.703 | 29.437 | 600.32 | 26.724 | 27.841 | 1259.676 | 27.493 | 27.932 | 38.244 | 14 | 1.3 | 5.3 | 0.6 | 0.3 | 0.3
5651 | 30/07/2025 12:23:32.199 | 22.44 | 16 | 81 | 51 | 33 | 32.53 | 8.984 | 7.133 | 128.894 | 31.347 | 28.687 | 29.441 | 600.552 | 26.719 | 27.821 | 1252.762 | 27.479 | 27.939 | 38.308 | 14 | 1.3 | 4.3 | 0.6 | 1.2 | 0.3
5652 | 30/07/2025 12:23:33.878 | 17.736 | 12 | 77 | 49 | 30 | 32.879 | 8.986 | 7.149 | 126.21 | 31.333 | 28.661 | 29.434 | 600.498 | 26.703 | 27.836 | 1257.413 | 27.476 | 27.941 | 38.457 | 8 | 1.6 | 4.1 | 1 | 0.6 | 0.3
5653 | 30/07/2025 12:23:35.512 | 14.424 | 9.8 | 74 | 44 | 26 | 29.342 | 8.987 | 7.152 | 122.68 | 31.372 | 28.701 | 29.459 | 601.953 | 26.751 | 27.811 | 1266.752 | 27.487 | 27.91 | 38.349 | 8 | 1.6 | 6.1 | 1 | 0.5 | 0.3
5654 | 30/07/2025 12:23:37.148 | 11.736 | 7.7 | 72 | 42 | 23 | 30.7 | 8.99 | 7.136 | 121.051 | 31.349 | 28.702 | 29.466 | 601.97 | 26.732 | 27.817 | 1277.482 | 27.503 | 27.913 | 38.514 | 8 | 1.6 | 6.1 | 1 | 0.5 | 0.3
5655 | 30/07/2025 12:23:38.783 | 9.744 | 6.3 | 69 | 39 | 20 | 32.874 | 9.193 | 7.134 | 117.225 | 31.339 | 28.691 | 29.414 | 601.798 | 26.738 | 27.835 | 1284.343 | 27.487 | 27.923 | 38.402 | 6 | 0.6 | 4.6 | 0 | 0.7 | 0.3
5656 | 30/07/2025 12:23:40.420 | 8.016 | 5.2 | 66 | 36 | 17 | 29.541 | 8.986 | 7.133 | 116.714 | 31.334 | 28.686 | 29.426 | 603.202 | 26.754 | 27.845 | 1282.343 | 27.485 | 27.951 | 38.453 | 6 | 0.6 | 3.2 | 0 | 0.1 | 0.3
5657 | 30/07/2025 12:23:42.054 | 6.648 | 4.3 | 64 | 32 | 14 | 32.708 | 9.13 | 7.136 | 113.345 | 31.331 | 28.678 | 29.426 | 601.858 | 26.75 | 27.845 | 1265.393 | 27.473 | 27.908 | 38.321 | 4 | 1.1 | 3.2 | 0.6 | 0 | 0.3
5658 | 30/07/2025 12:23:43.689 | 5.592 | 3.7 | 60 | 29 | 12 | 32.568 | 9.18 | 7.133 | 110.722 | 31.345 | 28.691 | 29.473 | 602.017 | 26.728 | 27.842 | 1252.666 | 27.501 | 27.919 | 38.406 | 4 | 1.1 | 3.1 | 0.6 | 0 | 0.3
5659 | 30/07/2025 12:23:45.331 | 4.752 | 3.1 | 57 | 26 | 9 | 28.953 | 8.988 | 7.134 | 107.768 | 31.323 | 28.701 | 29.437 | 601.818 | 26.746 | 27.85 | 1249.532 | 27.502 | 27.913 | 38.192 | 4 | 1.1 | 3.1 | 0.6 | 0 | 0.3
5660 | 30/07/2025 12:23:46.971 | 4.128 | 2.6 | 54 | 24 | 6 | 31.072 | 9.245 | 7.133 | 104.676 | 31.334 | 28.682 | 29.409 | 601.928 | 26.763 | 27.839 | 1258.183 | 27.474 | 27.931 | 38.347 | 3 | 0.1 | 3.4 | 0.9 | 0.5 | 0.3
5661 | 30/07/2025 12:23:48.606 | 3.504 | 2.2 | 50 | 21 | 2 | 32.944 | 9.134 | 7.148 | 101.696 | 31.334 | 28.671 | 29.444 | 601.967 | 26.739 | 27.853 | 1269.679 | 27.475 | 27.948 | 38.475 | 3 | 0.1 | 4.1 | 0.9 | 0.1 | 0.3
5662 | 30/07/2025 12:23:50.242 | 3.048 | 1.9 | 48 | 18 | 1 | 29.961 | 9.214 | 7.15 | 100.283 | 31.352 | 28.69 | 29.467 | 601.986 | 26.739 | 27.847 | 1271.785 | 27.488 | 27.921 | 38.458 | 3 | 0 | 4.1 | 0.6 | 0.5 | 0.3
5663 | 30/07/2025 12:23:51.875 | 2.76 | 1.8 | 45 | 15 | 1 | 32.824 | 9.299 | 7.179 | 98.643 | 31.328 | 28.704 | 29.462 | 602.089 | 26.732 | 27.853 | 1277.129 | 27.513 | 27.919 | 38.571 | 3 | 0 | 3.9 | 0.6 | 0 | 0.3
5664 | 30/07/2025 12:23:53.508 | 2.424 | 1.5 | 42 | 11 | 1 | 32.05 | 9.132 | 7.173 | 95.732 | 31.349 | 28.699 | 29.42 | 600.287 | 26.75 | 27.86 | 1272.319 | 27.486 | 27.913 | 38.272 | 3 | 0 | 3.9 | 0.6 | 0 | 0.2
5665 | 30/07/2025 12:23:55.141 | 2.16 | 1.4 | 39 | 9 | 1 | 28.751 | 8.942 | 7.15 | 92.848 | 31.361 | 28.683 | 29.407 | 600.68 | 26.744 | 27.843 | 1268.499 | 27.469 | 27.941 | 38.287 | 3 | 0 | 3.9 | 0.6 | 0 | 0.2
5666 | 30/07/2025 12:23:56.777 | 1.968 | 1.2 | 36 | 5 | 1 | 31.638 | 8.985 | 7.152 | 91.091 | 31.354 | 28.685 | 29.466 | 600.484 | 26.735 | 27.861 | 1264.868 | 27.481 | 27.932 | 38.52 | 3 | 0 | 2.8 | 0.6 | 1 | 0.2
5667 | 30/07/2025 12:23:58.411 | 1.776 | 1.1 | 33 | 4 | 0 | 29.17 | 8.989 | 7.151 | 89.956 | 31.356 | 28.693 | 29.463 | 600.551 | 26.726 | 27.843 | 1268.489 | 27.504 | 27.93 | 38.509 | 2 | 0.6 | 3.5 | 0.6 | 0.3 | 0.2
5668 | 30/07/2025 12:24:00.043 | 1.584 | 1 | 31 | 0 | 0 | 30.489 | 8.991 | 7.134 | 86.77 | 31.359 | 28.697 | 29.425 | 600.359 | 26.718 | 27.856 | 1267.561 | 27.488 | 27.898 | 38.453 | 2 | 0.6 | 4.8 | 0.6 | 0.5 | 0.2
5669 | 30/07/2025 12:24:01.680 | 1.416 | 0.96 | 27 | 0 | 1 | 32.855 | 9.132 | 7.134 | 85.229 | 31.354 | 28.695 | 29.435 | 600.519 | 26.745 | 27.835 | 1265.13 | 27.493 | 27.918 | 38.191 | 2 | 1.2 | 4.8 | 1.3 | 0.1 | 0.2
5670 | 30/07/2025 12:24:03.314 | 1.344 | 0.87 | 23 | 0 | 1 | 31.562 | 9.215 | 7.132 | 83.833 | 31.349 | 28.67 | 29.426 | 600.668 | 26.733 | 27.834 | 1260.842 | 27.487 | 27.929 | 38.588 | 2 | 1.2 | 4.8 | 1.3 | 0.1 | 0.2
5671 | 30/07/2025 12:24:04.950 | 1.224 | 0.81 | 21 | 0 | 1 | 28.788 | 8.988 | 7.137 | 80.784 | 31.356 | 28.69 | 29.477 | 600.359 | 26.728 | 27.844 | 1254.948 | 27.49 | 27.924 | 38.522 | 2 | 1.2 | 4.3 | 1.3 | 0.6 | 0.2
5672 | 30/07/2025 12:24:06.585 | 1.128 | 0.74 | 17 | 0 | 1 | 33.518 | 9.138 | 7.133 | 79.296 | 31.364 | 28.695 | 29.471 | 600.556 | 26.724 | 27.823 | 1247.244 | 27.491 | 27.918 | 38.275 | 1 | 0.3 | 4.4 | 1 | 0.8 | 0.2
5673 | 30/07/2025 12:24:08.220 | 1.056 | 0.7 | 15 | 0 | 1 | 28.866 | 9.213 | 7.137 | 78.269 | 31.36 | 28.695 | 29.429 | 600.401 | 26.74 | 27.831 | 1246.98 | 27.489 | 27.886 | 38.279 | 1 | 0.3 | 4.1 | 1 | 0.9 | 0.2
5674 | 30/07/2025 12:24:09.853 | 0.936 | 0.65 | 12 | 0 | 1 | 31.258 | 9.016 | 7.134 | 76.522 | 31.348 | 28.697 | 29.448 | 600.497 | 26.72 | 27.81 | 1249.819 | 27.483 | 27.942 | 38.413 | 1 | 0.6 | 3.4 | 0 | 0.1 | 0.2
5675 | 30/07/2025 12:24:11.487 | 0.888 | 0.62 | 9 | 0 | 1 | 32.934 | 8.968 | 7.15 | 74.847 | 31.325 | 28.664 | 29.427 | 600.601 | 26.727 | 27.829 | 1247.472 | 27.461 | 27.916 | 38.798 | 1 | 0.6 | 4 | 0 | 0 | 0.2
5676 | 30/07/2025 12:24:13.121 | 0.84 | 0.58 | 5 | 1 | 1 | 30.984 | 9.181 | 7.171 | 73.507 | 31.36 | 28.696 | 29.463 | 601.8 | 26.741 | 27.845 | 1235.265 | 27.498 | 27.925 | 38.483 | 1 | 0.6 | 4 | 0 | 0 | 0.2
5677 | 30/07/2025 12:24:14.753 | 0.816 | 0.54 | 3 | 0 | 1 | 29.094 | 9.141 | 7.178 | 71.975 | 31.327 | 28.697 | 29.435 | 601.885 | 26.752 | 27.841 | 1234.772 | 27.51 | 27.916 | 38.09 | 1 | 0.1 | 3.5 | 1.3 | 0 | 0.2
5678 | 30/07/2025 12:24:16.388 | 0.744 | 0.5 | 0 | 0 | 1 | 32.13 | 9.199 | 7.152 | 70.804 | 31.34 | 28.699 | 29.466 | 601.901 | 26.746 | 27.843 | 1237.026 | 27.492 | 27.906 | 38.198 | 1 | 0.1 | 4.8 | 1.3 | 0.5 | 0.2
5679 | 30/07/2025 12:24:18.025 | 0.672 | 0.48 | 0 | 1 | 2 | 28.812 | 9.137 | 7.146 | 69.007 | 31.309 | 28.691 | 29.401 | 601.892 | 26.726 | 27.847 | 1245.611 | 27.481 | 27.934 | 38.429 | 1 | 0.9 | 4.4 | 1.3 | 0.5 | 0.2
5680 | 30/07/2025 12:24:19.661 | 0.648 | 0.46 | 0 | 0 | 1 | 31.638 | 9.285 | 7.135 | 69.303 | 31.336 | 28.672 | 29.443 | 600.6 | 26.759 | 27.866 | 1243.087 | 27.472 | 27.918 | 40.364 | 1 | 0.9 | 5.2 | 1.3 | 0.9 | 0.2
5681 | 30/07/2025 12:24:21.296 | 0.624 | 0.44 | 0 | 0 | 1 | 32.972 | 9.221 | 7.135 | 67.243 | 31.329 | 28.698 | 29.468 | 600.53 | 26.744 | 27.841 | 1249.703 | 27.504 | 27.92 | 38.349 | 1 | 0.9 | 5.2 | 1.3 | 0.9 | 0.2
5682 | 30/07/2025 12:24:22.931 | 0.552 | 0.42 | 0 | 0 | 1 | 30.425 | 9.132 | 7.135 | 65.703 | 31.319 | 28.688 | 29.434 | 600.322 | 26.742 | 27.869 | 1252.097 | 27.494 | 27.911 | 38.19 | 1 | 0 | 4.4 | 0.9 | 0.2 | 0.2
5683 | 30/07/2025 12:24:24.571 | 0.552 | 0.4 | 1 | 1 | 1 | 29.461 | 8.982 | 7.121 | 64.196 | 31.359 | 28.689 | 29.433 | 600.484 | 26.741 | 27.849 | 1261.931 | 27.48 | 27.927 | 38.401 | 1 | 0 | 4.4 | 0.9 | 0 | 0.2